## Slide 1
PSV-7132-7134-7136-7137
Blocked Outlet Scenario

## Slide 2
Determine relief load
The rated capacity of FT-2001 is 28130kg/h , so the relief load is 28130 kg/h.

## Slide 3
2.Calculate orifice area
Determine if it is in critical flow:
If so, then :

## Slide 6
Results
Note that the relieving temperature is obtained from TOPSOE EXCEL
T | 464 K | W | 28138 kg/h
Z | 0.93 | A | 60.6 cm2
M | 18.02 | A | 9.39 in2
C | 0.0256 | Accumulation | 10%

## Slide 7
5.Use API-526 to determine the designation and the inlet and outlet sizing
Since it is more than 6.38 inch, then Q is selected. Also, by checking its rating and temperature limitation, 6Q8 is selected.

## Slide 9
Select proper PSV type by checking backpressure
According to licensor data, superimposed and build-up backpressure are max 10 barg. Since the backpressure is constant and it is discharged to atmosphere then a conventional type could be selected even though the percentage is high
superimposed | Build-up | Total
0 barg | 10 barg | 10 barg
0% | 100% | 100%

## Slide 10
Material Selection
Since it is Steam , A216 WCB could be used for its body

## Slide 11
Discussion