PSV-1015

Fire Scenario

Unwetted Surface

PSV SIZING PROCEDURE FOR UNWETTED FIRE SCENARIO

1.Determine the scenario, using API-521

2.Calculate the relief load, using API-520 Part1

3.Calculate the orifice area, using API-520 Part1

4.Select proper PSV type by checking backpressure

5.Use API-526 to determine the designation and the inlet and outlet sizing

6.Use API-520 Part2 to detail its construction

1.Determine the scenario, using API-521

Since it is K.N Drum and exposed to fire then a fire scenario is defined.

| Parameters | Value | Parameters | Value |
| --- | --- | --- | --- |
| Diameter | 1.55 m | M | 16.74 |
| Height | 2.55 m | Set Pressure | 60 barg |
| Fluid | Natural Gas | Relieving Pressure | 73.6 bara |
| Z | 0.95 | Accumulation | 0.21 |
| Cp/Cv | 1.26 | Material | CS |

2.Calculate the relief load, using API-520 Part1

Calculation

| Parameters | Value | Parameters | Value |
| --- | --- | --- | --- |
| Aw | 15 m2 | KD | 0.975 |
| C9 | 0.2772 | F’ | 128 |
| C10 | 0.0395 | Relief Load | 964 kg/hr |
| C | 0.026 |  |  |

Note that since F’ is less than 182 the corresponding equation has been used in which F’ is set

to 182. Remember that in F’ calculation T1 is set to max 400 C .

3.Calculate the orifice area, using API-520 Part1

Use the following formula to calculate orifice area:

By setting F’, Aw, p1 to 128, 15 and 73600 kpa, we obtain 0.034 inch^2

5.Use API-526 to determine the designation and the inlet and outlet sizing

Since it is less than 0.11 inch then D is selected. Also, by checking its rating and temperature

limitation, 1D2 is selected.

Select proper PSV type by checking backpressure

According to licensor data, superimposed and build-up backpressure are max 1.5 and 18.5

barg. Even though selecting Conventional type is not fully recommended, Conventional type has

been selected by LESER.

| superimposed | Build-up | Total |
| --- | --- | --- |
| 1.5 barg | 18.5 barg | 20 barg |
| 2.5% | 30% | 33.3% |

Material Selection

Since it is Natural Gas then A-216 WCB is selected for its body

Discussion

The selected PSV in site is 1E2 but calculation shows that it should be 1D2, then what is the

cause?

TCC has selected T1 equal to 87C or 360K which is the design temperature of knockout Drum,

thanks to which the calculated F’ becomes 590 and if you set Aw equal to 16 m2 it becomes

560.

The resultant relief load and effective area become 3600 kg/h and 0.17 inch respectively, which

means that type 1E2 is selected