## Slide 2
Chapter 1
Definitions and Terms
Maximum allowable working pressure (MAWP)
The maximum gauge pressure permissible at the top of a completed vessel in its normal operating
position at the designated coincident temperature specified for that pressure. The pressure is the least of
the values for the internal or external pressure as determined by the vessel design rules for each element
of the vessel using actual nominal thickness, exclusive of additional metal thickness allowed for corrosion
and loadings other than pressure. The MAWP is the basis for the pressure setting of the pressure-relief
devices that protect the vessel. The MAWP is normally greater than the design pressure but can be equal
to the design pressure when the design rules are used only to calculate the minimum thickness for each
element and calculations are not made to determine the value of the MAWP.

## Slide 3
Design pressure
Pressure, together with the design temperature, used to determine the minimum permissible thickness or
physical characteristic of each vessel component as determined by the vessel design rules. The design
pressure is selected by the user to provide a suitable margin above the most severe pressure expected
during normal operation at a coincident temperature. It is the pressure specified on the purchase order.
This pressure may be used in place of the MAWP in all cases where the MAWP has not been
established. The design pressure is equal to or less than the MAWP. In most of the cases, however, the pressure
relieving device is set at the design pressure and not at the M.A.W.P. because the latter is only known late in the
design, when the detailed mechanical design of the vessel is completed.
Accumulation
The pressure increase over the MAWP of the vessel, expressed in pressure units or as a percentage of
MAWP or design pressure. Maximum allowable accumulations are established by applicable codes for
emergency operating and fire contingencies.
Blow-down :
for gas 5-7% and for 2-phase and liquid is 20%

## Slide 4
Overpressure:
is the pressure increase over the set pressure of the primary relieving device during discharge. Overpressure is
the same as accumulation only when the relieving device is set to open at the maximum allowable working pressure of
the vessel
Backpressure
The pressure that exists at the outlet of a pressure-relief device as a result of the pressure in the
discharge system. Backpressure is the sum of the superimposed and built-up backpressures.
Built-up backpressure
The increase in pressure at the outlet of a pressure-relief device that develops as a result of flow after the
pressure-relief device opens.
Superimposed backpressure
The static pressure that exists at the outlet of a pressure-relief device at the time the device is required to
operate. Superimposed backpressure is the result of pressure in the discharge system coming from other
sources and may be constant or variable.

## Slide 5
Relieving conditions
Relieving pressure, shown as P1 in the various sizing equations, is the inlet pressure of the
PRD at relieving conditions. The relieving pressure is the total of set pressure plus overpressure. The
examples cited in this section for the determination of relieving pressure refer to PRVs; however, they are
also applicable to non-reclosing PRDs (see Figure 15 and Figure 19 for pressure level relationships for
these types of devices). The effects of inlet pressure drop on specification of relieving pressure for PRV
sizing can be neglected if the inlet pressure drop does not exceed 3 % of set pressure.

## Slide 7
Notes
1.In general, restrictions, either a specially designed spool piece or a restriction orifice, should not be used as a
means of limiting the capacity of a pressurization path.
2. When the increased operating condition will not exceed 10 hours at any one time or 100 hours per year, it is
permissible to increase the pressure rating at the temperature existing during the increased operating condition,
by a maximum of 33 %.
3. When the increased operating condition will not exceed 50 hours at any one time or 500 hours per year, it is
permissible to increase the pressure rating at the temperature existing during the increased operating condition,
by a maximum of 20 %.

## Slide 8
Overall PSV Sizing Procedure
1.Determine the scenario, using API-521
2.Calculate the relief load, using API-520 Part1
3.Calculate the orifice area, using API-520 Part1
4.Select proper PSV type by checking backpressure
5.Use API-526 to determine the designation and the inlet and outlet sizing
6.Use API-521 Part2 to detail its construction

## Slide 9
Chapter 2
Individual Overpressure Causes and Their Relieving Rates
Fire Scenario
Fire exposure on equipment can result in overpressure due to vapor generation (boiling of liquid contents or
decomposition reaction) and/or fluid expansion. Fire exposure can also cause overheating of the vessel walls
resulting in a reduction in material strength. Either the vapor thermal-expansion-relief load or the boiling-liquid
vaporization-relief load, but not both, should be used. It is a practice that has been used for many years. There
are no known experimental studies where separate contributions of vapor thermal expansion versus boiling-
liquid vaporization have been determined. When sizing the PRD for fire exposure, the contribution of vaporizing
liquid compared with vapor expansion is generally governing unless, for example, the wetted surface has external
insulation in accordance with 4.4.13.2.7 and the unwetted surfaces are not insulated.

## Slide 10
Effect of Fire on the Wetted Surface of a Vessel
To determine vapor generation, it is necessary to recognize only that portion of the vessel that is wetted by its
internal liquid and is equal to or less than 7.6 m (25 ft) above the source of flame. Wetted surfaces higher than
7.6 m (25 ft) are normally excluded because pool fire flames are not likely to impinge for long durations above
this height.

## Slide 11
Effect of Fire on the Unwetted Surface of a Vessel
Unwetted wall vessels are those that have no liquid in contact with the internal vessel walls (e.g. internal walls
are exposed only to a gas, vapor, or supercritical fluid or they are internally insulated regardless of the contained
fluids). These include vessels that contain separate liquid and vapor phases under normal conditions but become
single phase (above the critical) at relieving conditions. Vessels can be designed to have internal insulation (e.g.
refractory) and such areas may be considered unwetted. A characteristic of a vessel with an unwetted internal
wall is that heat flow from the wall to the contained fluid is low as a result of the heat transfer resistance of the
contained fluid or any internal insulating material. Heat input from a fire to the bare outside surface of an
unwetted or internally insulated vessel can, in time, be sufficient to heat the vessel wall to a temperature high
enough to rupture the vessel.

## Slide 12
Heat Absorption Equations for Vessels Containing Liquids
The amount of heat absorbed by a vessel exposed to an open fire is markedly affected by the type of fuel feeding
the fire, the degree to which the vessel is enveloped by the flames (a function of vessel size and shape), the
environment factor, firefighting, and drainage. Equation (7) is used to evaluate these conditions if there are
Prompt firefighting efforts and drainage of flammable materials away from the vessels:

## Slide 14
Where adequate drainage and firefighting equipment do not exist, Equation (8) should be used
Credit for thermal insulation is typically not taken because it usually does not meet the fire-protection insulation requirements. Thermal insulation not equal to fire proof insulation.
The designer should be certain that any system of insulating materials permits the basic insulating material to function effectively at temperatures up to 900 °C during a fire for up to 2 hr.
The value of thermal conductivity used in calculating the environmental factor credit for insulation should be the thermal conductivity of the insulation at the mean temperature between 904°C and the process temperature expected at relieving conditions. (Use of a conservative mean temperature of 1000°F (540°C) is suggested.)
For insulated vessels, the environment factor is given by:

## Slide 15
Horizontal Drum
Up to 25 ft (7.6 m) above grade - Use total wetted vessel surface up to
high liquid level.
Greater than 25 ft (7.6 m) above grade - Use the wetted area of the
vessel surface to high liquid level or up to the vessel center line whichever is
less.
Vertical Drums
The wetted vessel surface within 25 ft (7.6 m) of grade, based on high liquid
level, is used. If the entire vessel is more than 25 ft (7.6 m) above grade,
then only the surface of the bottom head need be included. For vessels
supported on skirts that do not require fireproofing of their inside surface the
surface of the bottom head need not be included in the wetted area
regardless of elevation.
Vertical Vessels
A wetted = 1.089 D 2 + π D h
Use this equation when the liquid surface elevation SE < 7.6 m. If the
surface elevation of liquid level is above 7.6 m, replace h by h - (SE – 7.6)

## Slide 16
Fire Case Calculation by Software
Relief load calculation for single component:
Calculate Aw then calculate Q-fire then calculate landa then divide Q-fire to landa.
In order to calculate landa put Vf=0 and relieving pressure = 1.21pset + patm.
Relief load calculation for multi-component:
For multi-component systems, the latent heat of the residual liquid will change as the lighter components are vaporized and removed from the system. In general, such systems require a time-dependent analysis to determine the required relief area and the corresponding relief rate. The following approach is suggested.
Using the composition of the residual liquid inventory in the vessel, perform a bubble point flash at the accumulated pressure. In doing this flash, the flow rate of the feed stream to the flash can be set at initial mass on the equipment. m=ρ.V
m: initial liquid mass in the equipment
V: liquid volume in the equipment up to HLL
ρ: liquid mass density at normal operation.

## Slide 17
For each flash, sufficient heat is applied to vaporize a nominal 10 wt% of liquid, the remaining liquid passing to the next flash.
An estimate of the time for each flash should be made.
time=required heat for each flash/calculated heat of fire.
A flash temperature of 400°C is obtained. The total vaporization time riches 2 hours. For each stage, a latent heat of vaporization should be calculated and data for the flashed vapor used to compute the value of a factor A’ which is indicative of the pressure relief valve orifice area required based on that stage of the vaporization of the original fluid.
A =1/Y sqr(ZT/M)
pressure relief valve orifice area parameter (not the orifice area)
λ latent heat of vaporization (kJ/kg)
z vapor compressibility
T vapor temperature (K)
M vapor molecular weigh
Two-phase relief-device sizing is not normally required for the fire case, except for unusually foamy materials or reactive chemicals.
If no accurate latent heat value is available for these hydrocarbons near the critical point, a minimum value of 115 kJ/kg (50 Btu/lb) is sometimes acceptable as an approximation

## Slide 18
Horizontal Vessels:
Liquid level below centerline
S=D Cos – 1 ((r- h) / r)
Liquid level above centerline
S=D {π-Cos – 1 ((h- r) / r)}
A wetted=(2.178D2+ πDL)(S/ πD)
As with vertical vessels, these equations are directly useful when the liquid surface elevation S E < 7.6 m. If the surface elevation of liquid level is above 7.6 m, replace h by h - ( S E – 7.6).
Trayed column
High liquid level in bottom plus liquid holdup from all trays. Level in reboiler is to be included if the reboiler is an integral part of the column. Total wetted surface up to the height of 7.6m. Vessel heads protected by support skirts with limited ventilation are not normally included as wetted surface area. Liquid hold-up on each tray shall be equal to the weir height plus 50mm.
Air-Coolers
It is not necessary to consider the bare area for air-cooled condensers, whetherpartial or total condensing, as long as both of the following conditions are satisfied:
1. The tubes are sloped so that they are self-draining.
2. There is no control valve or pump connected directly to the condenser
liquid outlet.

## Slide 19
Heat Absorption Equations for Vessels Containing Only Gases, Vapors, or Supercritical Fluids
The discharge areas for PRDs on vessels containing supercritical fluids, gases or vapors exposed to open fires can
be estimated using Equation (9). In certain cases, the normal operating pressure can be below the
thermodynamic critical conditions but the relieving pressure is supercritical. In such cases, the guidance below
can be used to size the relief device. In the use of Equation (9), no credit has been taken for insulation:
The derivations of Equations (9), (10), (13), and (14) [53] are based on the physical properties of air and the
perfect gas laws. The derivations assume that the vessel is uninsulated and has no mass, that the vessel wall
temperature does not reach rupture stress temperature, and that there is no change in fluid temperature. These
assumptions should be reviewed to ensure that they are appropriate for any particular situation. Insulation that
meets the external insulation criteria outlined in 4.4.13.2.7 offers a mitigating benefit when gas-filled vessels are
exposed to a fire by decreasing the rate at which the metal wall temperature rises.
The surface area potentially exposed to a fire should be used when determining the fire-relief requirements of
gas-filled vessels.

## Slide 24
Failure of Automatic Controls Scenario
Inadvertent Valve Opening
The inadvertent opening of any valve from a source of higher pressure, such as high-pressure steam or process
fluids, should be considered. Administrative controls can be used to prevent inadvertent valve opening, subject to
4.2.1 and 4.2.2. The relief load should be determined using the maximum operating pressure upstream of the
valve and the relieving pressure on equipment downstream of the valve. If the pressure source is a pipeline or a
production well, the pressure upstream of the valve may reach the maximum shut-in pressure of the source after
a shutdown. The user should determine whether inadvertent valve opening combined with maximum shut-in
pressure in upstream system is a credible relief case. There can be single or multiple inlet lines fitted with control devices. The
scenario to consider is that one inlet valve is in a fully opened position regardless of the control valve failure position. Opening
of this control valve can be caused by instrument failure or misoperation. If the system has multiple inlets, the position of any
control device in those remaining lines shall be assumed to remain in its normal operating position. Therefore, the required
relieving rate is the difference between the maximum expected inlet flow and the normal outlet flow, adjusted for relieving
conditions and considering unit turndown, assuming that the other valves in the system are still in operating position
at normal flow (i.e. normally open, normally closed, or throttling

## Slide 25
The following applies when a manual or actuated valve is inadvertently opened, causing pressure buildup in a
vessel. The vessel should have a PRD large enough to pass a rate equal to the flow through the open valve; credit
may be taken for the flow capacity of vessel outlets that can reasonably be expected to remain open. The manual
or actuated valve should be considered as passing its capacity at a full-open position with the pressure in the
vessel at relieving conditions. Volumetric or heat-content equivalents may be used if the manual or actuated
valve admits a liquid that flashes or a fluid that causes vaporizing of the vessel contents.

## Slide 26
An important consideration is the effect of having a manual bypass on the inlet control valve(s) at least partially
open. If, during operation, the bypass valve is opened to provide additional flow, then this total flow (control valve
wide open and bypass valve normal position) shall be considered in the relieving scenario.
The potential for the bypass valve to be inadvertently opened (e.g. during normal operations, control valve
maintenance, start-up, shutdown, or special operations) while the control valve is operating (both bypass and
control valve wide open) should also be considered. Administrative controls can be used to prevent inadvertent
opening of the bypass valve. The user is cautioned that some systems can have unacceptable risk due to failure of
administrative controls and resulting consequences due to loss of containment. In these cases, limiting the
overpressure to the normally allowable overpressure can be more appropriate. Note that the entire system,
including all of the auxiliary devices (e.g. gasketed joints, instrumentation), should be considered for the
overpressure during the failure of administrative controls.

## Slide 27
Other situations can arise where problems involved in evaluating relief requirements after the failure of an inlet
control device are more complex and of special concern (e.g. a pressure vessel operating at a high pressure where
liquid bottoms are on level control and discharge into a lower-pressure system). Usually, when the liquid is let
down from the high-pressure vessel into the low-pressure system, only the flashing effect is of concern in the
event that the low-pressure system has a closed outlet. However, the designer should also consider that vapors
flow into the low-pressure system if loss of liquid level occurs in the vessel at higher pressure. In this case, if the
volume of the source of incoming vapors is large compared with the volume of the low-pressure system or if the
source of vapor is unlimited, serious overpressure can rapidly develop. When this occurs, it can be necessary to
size relief devices on the low-pressure system to handle the full vapor flow through the liquid control valve. The
loss of liquid level followed by high-pressure vapor flow is commonly referred to as “vapor breakthrough” or “gas
blowby.

## Slide 28
Closed Outlets
The inadvertent closure of a valve on the outlet of pressure equipment while the equipment is on stream can
expose the equipment to a pressure that exceeds the MAWP. Every valve (i.e. manual, control, or remotely
operated) should be considered as being subject to inadvertent operation. If closure of an outlet valve can result
in pressure in excess of that allowed by the design code, a PRD is required. If the equipment is designed to the
maximum source pressure, then closure of an outlet valve will not result in overpressure, so a PRD is not
required for the closed outlet scenario.
Additional Considerations Involving Pumps:
The system does not require relief protection for the closed outlet (i.e. shut-in) scenario if the pump, piping, and
other equipment downstream of a centrifugal pump (which can be exposed to the shut-in pressure of the pump,
e.g. closed block valve in the discharge system) are designed to withstand the maximum shut-in pressure of the
pump or other pressure source such as a start-up or warm-up line.
For positive displacement pumps, pressure-relief protection is usually required to protect the pump itself and
downstream equipment against shut-in conditions.

## Slide 29
In the case of a manual valve, administrative controls can be used to prevent the closed outlet scenario unless
the resulting pressure exceeds the maximum allowed by the pressure design code [usually the corrected
hydrotest pressure is exceeded.
Liquid Overfill
Liquid overfill of a vessel results in a closed outlet case. As an alternative to providing an adequacy sized
pressure relief valve, the following alternative options are available for preventing overpressure:
1) Increase the system design pressure and/or pressure relief valve set pressure within code allowances.
2) Provide a safety instrument system (HIPS) to isolate the inflow on increasing vessel inventory.
3) Rely on operator intervention to prevent overfill from occurring. Where liquid overfill is eliminated on the
basis of operator intervention, at least one additional and independent alarm shall be provided to indicate that
the situation has not yet been brought under control. This alarm may monitor a parameter other than level
(e.g.differential pressure)

## Slide 30
Sizing Procedure for Gases
Determine if it is in critical flow:
If so, then :

## Slide 33
If it is subcritical flow, then use the following equation for conventional or pilot type

## Slide 35
Hydraulic Expansion
Hydraulic expansion is the increase in liquid volume caused by an increase in temperature (see Table 2). It can
result from several causes, the most common of which are the following.
a) Piping or vessels are blocked in while they are filled with cold liquid and are subsequently heated by heat
tracing, coils, ambient heat gain, or fire.
b) A heat exchanger is blocked in on the cold side with flow in the hot side.
Caution—Block valves have the potential to leak, thereby admitting either cold or hot fluid into a heat
exchanger that is intended to be blocked in, resulting in a potential overpressure.
c) Piping or vessels are blocked in while they are filled with liquid at near-ambient temperatures and are heated by direct solar radiation.

## Slide 36
Where the system under consideration for thermal relief consists of piping only (does not contain pressure
vessels or heat exchangers), a PRD might not be required to protect piping from thermal expansion if any of the
following:
a) the piping always contains a pocket of noncondensing vapor, such that it can never become liquid-full; or
Caution—Small vapor or gas pockets can disappear upon heating due to compression and/or
solubilization. In contrast, multicomponent mixtures with a wide boiling range can always have
sufficient vapor present to preclude becoming completely liquid-full. The liquid-volume change upon
solar heating, heat tracing, heating to ambient temperature, or heat from another source should be
estimated to determine if the volume of the vapor pocket is sufficient for liquid expansion.
b) the piping is in continuous use (i.e. not batch or semicontinuous use) and drained after being blocked in using
well supervised procedures or permits; or
c) the fluid temperature is greater than the maximum temperature expected from solar heating [usually
approximately 60 °C to 70 °C (approximately 140 °F to 160 °F)] and there are no other heat sources such as
heat tracing (note that fire is generally not considered when evaluating pressure-relief requirements for piping);
d) the estimated pressure rise from thermal expansion is within the design limits of the equipment or piping.

## Slide 37
Sizing and Set Pressure
Since every application is for a relieving liquid, the required relieving rate is small; specifying an oversized device
is, therefore, reasonable. A nominal diameter (DN) 20 × DN 25 (NPS 3/4 × NPS 1) relief valve is commonly used.
If there is reason to believe that this size is not adequate, the procedure in 4.4.12.3 can be applied.
The thermal-relief pressure setting should never be above the maximum
pressure permitted by the weakest component in the system being protected. However, the PRD should be set
high enough to open only under hydraulic expansion conditions. If thermal-relief valves discharge into a closed
system, the effects of backpressure should be considered.
Two general applications for which thermal-relieving devices larger than a DN 20 × DN 25 (NPS 3/4 × NPS 1) valve
can be required are long pipelines of large diameter in uninsulated, aboveground installations and large vessels or
heat exchangers operating liquid-full. Long pipelines can be blocked in at or below ambient temperature; the effect
of solar radiation raises the temperature at a calculable rate. If the total heat transfer rate and thermal expansion
coefficient for the fluid are known, a required relieving rate can be calculated. See Parry [135] for additional
information on thermal relief

## Slide 39
Sizing and Set Pressure
Since every application is for a relieving liquid, the required relieving rate is small; specifying an oversized device
is, therefore, reasonable. A nominal diameter (DN) 20 × DN 25 (NPS 3/4 × NPS 1) relief valve is commonly used.
If there is reason to believe that this size is not adequate, the procedure in 4.4.12.3 can be applied.
The thermal-relief pressure setting should never be above the maximum
pressure permitted by the weakest component in the system being protected. However, the PRD should be set
high enough to open only under hydraulic expansion conditions. If thermal-relief valves discharge into a closed
system, the effects of backpressure should be considered.
Two general applications for which thermal-relieving devices larger than a DN 20 × DN 25 (NPS 3/4 × NPS 1) valve
can be required are long pipelines of large diameter in uninsulated, aboveground installations and large vessels or
heat exchangers operating liquid-full. Long pipelines can be blocked in at or below ambient temperature; the effect
of solar radiation raises the temperature at a calculable rate. If the total heat transfer rate and thermal expansion
coefficient for the fluid are known, a required relieving rate can be calculated. See Parry [135] for additional
information on thermal relief

## Slide 40
In order to calculate the orifice area use the following equation:

## Slide 41
Notes:
When a PRV is sized for viscous liquid service, it should first be sized as if it were for a
non-viscous type application (i.e. Kv = 1.0) so that a preliminary required discharge area, AR, can be
obtained from Equation (32) or Equation (33). The user is cautioned that the equations presented here
may not be applicable for non-Newtonian applications (see 5.10). From the list of API 526 standard orifice
sizes or the manufacturer’s listing, the next orifice size, Aselected, larger than AR should be chosen to
calculate the Reynolds number, Re, from either of the following relationships

## Slide 42
After the Reynolds number, Re, is determined, the factor Kv is obtained and applied in Equation (32)
or Equation (33) to correct the preliminary required discharge area, AR. If the corrected area exceeds the
chosen standard orifice area, Aselected, the Reynolds number should be recalculated using the next larger
standard orifice size and the value of Kv updated accordingly.

## Slide 44
Selecting PSV Type based on Backpressure
Regardless of whether the valve is vented directly to atmosphere or the discharge is piped to a collection system,
the backpressure may affect the operation of the PRV. Effects due to backpressure may include variations in
opening pressure, reduction in flow capacity, instability, or a combination of all three.
backpressure can be constant if the valve outlet is connected to a process vessel or system that is held at a
constant pressure. In most cases, however, the superimposed backpressure will be variable as a result of
changing conditions existing in the discharge system.
Effects of Superimposed Backpressure on Pressure-relief Valve Opening

## Slide 45
Effects of Superimposed Backpressure on Pressure-relief Valve Opening

## Slide 51
A pilot-operated PRV consists of the main valve, which normally encloses a floating
unbalanced piston assembly, and an external pilot (see Figure 10 through Figure 14). The piston is
designed to have a larger area on the top than on the bottom. Up to the set pressure, the top and bottom
areas are exposed to the same inlet operating pressure. Because of the larger area on the top of the
piston, the net force holds the piston tightly against the main valve nozzle. As the operating pressure
increases, the net seating force increases and tends to make the valve tighter. This feature allows most
pilot-operated valves to be used where the maximum expected operating pressure is higher than the
percentage shown in Figure 15. At the set pressure, the pilot vents the pressure from the top of the
piston; the resulting net force is now upward causing the piston to lift, and process flow is established
through the main valve. After the overpressure incident, the pilot will close the vent from the top of the
piston, thereby re-establishing pressure, and the net force will cause the piston to reseat.
The pilots may be either a flowing or nonflowing type. The flowing type allows process fluid to
continuously flow through the pilot when the main valve is open; the nonflowing type does not. The
nonflowing pilot type is generally recommended for most services to reduce the possibility of hydrate
formation (icing) or solids in the lading fluid affecting the pilot’s performance

## Slide 54
The modulating pilot, as shown in Figure 17, opens the main valve only enough to satisfy the
required relieving capacity and can be used in gas, liquid, or two-phase flow applications. A modulating
pilot-operated valve, in contrast to a pop-action valve, limits the amount of relieving fluid to only the
amount required to prevent the pressure from exceeding the allowable accumulation. Since a modulating
pilot only releases the required relieving rate, the calculation of built-up backpressure may be based on
the required relieving rate instead of the rated capacity of the valve corrected for the actual overpressure.
The modulating pilot valve also can reduce interaction with other pressure control equipment in the
system during an upset condition, reduce unwanted atmospheric emissions, and reduce the noise level
associated with discharge to the atmosphere.

## Slide 55
PRV Instability
PRV Cycling
PRV Flutter
PRV Chatter
Chattering is where the PRV opens and closes at a very high frequency (on the order of the natural
frequency of the valve’s spring/mass system). Spring-loaded PRVs are spring/mass devices and
consequently are susceptible to dynamic interaction with the system. The primary concern is loss of
containment (loosening of flange bolts or failure of piping components due to fatigue) caused by pressure
pulsation or impact loading from rapid hammering of the valve disk onto the valve seat. Chattering may lead
to significantly reduced PRV flow capacity. As a secondary effect, the chattering can cause valve seat
damage and mechanical failure of valve internals (galling and bellows failure). Spring-loaded PRVs and
popactionpilot valves can experience chatter.
Modulating pilot-operated or remote sensing pop-action pilot PRVs are less likely to chatter).
The damaging forces on piping associated with fluid pressure and velocity changes associated with chatter
are much more severe in liquid service as compared to vapor service due to the higher densities associated
with liquids. This is supported by analysis that shows that the pressure change as a result of fluid
acceleration is typically small in inlet piping applications in vapor service.

## Slide 56
Potential Causes of PRV Instability
1.Excessive PRV Inlet Pressure Loss
2. Excessive Built-up Backpressure
3. Acoustic Interaction
4. Retrograde Condensation
5. Improper Valve Selection
6. Oversized PRVs

## Slide 57
PRD Location
If other factors permit, the PRD should normally be placed close to the protected equipment or system of
equipment so that the pressure in the protected equipment stays within code allowable limits and to avoid
PRV instability. The PRD should not be located where there are pressure fluctuations large enough to result in
relief valve simmering/activation or rupture disk fatigue. On installations that have pressure fluctuations that
peak close to the set pressure of the PRV or burst pressure of a rupture disk, the PRD should be located farther
from the source and in a more stable pressure region.
— locations close to control valves, other valves, and other appurtenances;
— locations close to orifice plates and flow nozzles;
— locations close to other fittings, such as short radius elbows;
— locations close to the discharge of positive displacement pumps or compressors.
The potential effect of pressure fluctuations on the relief device may be reduced by the following
— locating the PRD 10 or more pipe diameters from any areas as described above;
— providing a well-rounded, smooth branch connection where the relief device inlet piping joins the main piping
run.
— providing a larger branch connection (relative to the size of the PRV inlet).

## Slide 58
The PRD inlet and outlet piping should be free-draining (no pockets) away from the PRD.
The nominal size of the inlet piping and fittings shall be the same as or larger than the nominal size of the
pressure-relief valve inlet connection.
Horizontal lines are generally regarded as self-draining. However, avoid the installation of a PRV at the end
of a long horizontal inlet pipe through which there is normally no flow. Solids, such as rust or scale, may
accumulate, or liquid may be trapped, creating interference with the valve’s operation or requiring more
frequent valve maintenance.
Auto-refrigeration during discharge can cool the outlet of the PRD and the discharge piping to the point that
brittle fracture can occur. Piping design, including material selection, shall consider the expected discharge
temperature.
Note that the rated capacity corrected for the actual overpressure can vary depending on the overpressure
scenario common relief header piping in closed discharge systems can be sized using the protected system’s
required relieving capacity.
For a modulating pilot-operated PRV, the discharge piping can be sized using the required relieving capacity
of the system that the valve is protecting.

## Slide 59
Whenever the atmospheric vent, discharge piping, or common relief header piping is sized using the
system’s required relieving capacity instead of the rated capacity of the valve corrected for the actual
overpressure, the backpressure should be re-checked whenever changes are made to the process that
affect the required relieving capacity of the system the valve is protecting.
The discharge piping from thermal relief valves designed solely to protect against liquid hydraulic expansion
due to ambient heating (including solar radiation) typically does not need to be sized to meet the built-up
backpressure limits provided in API 520, Part I and as discussed in 6.3.1. The reason for this is that the
capacity of these PRVs is typically larger by an order of magnitude (>10 times) than the required relief rate
and the flow in the discharge line never reaches a steady state flow at the capacity.
Superimposed backpressure that exceeds the inlet pressure of a pilot-operated PRV can cause the main
valve to open, allowing reverse flow through the main valve.

## Slide 60
PRV Inlet Pressure Drop Limitations
1.Confirm the inlet pressure losses do not significantly affect the capacity of the PRV.
2.Confirm the PRV is set to open at or below the maximum allowable working pressure for all equipment
being protected.
3.Limit the pressure to the maximum allowable accumulation for all equipment being protected
4.Provide reasonable assurance that the inlet pressure losses are unlikely to result in destructive
instability of the PRV.
PRV Inlet Pressure Loss Criteria
The total nonrecoverable pressure loss between the protected equipment and the pressure-relief valve
should not exceed 3 % of the PRV set pressure, except as noted below:
— thermal relief valves
— remotely sensed pilot-operated relief valves
— an engineering analysis is performed for the specific installation.
Note that keeping the pressure loss below 3 % becomes progressively more difficult at low pressures and/or
as the orifice size of a PRV increases. In certain applications, it is difficult to meet the 3 % criterion for the
largest API 526 [2] orifice size for a given inlet flange diameter (e.g. 2J3, 4P6, 6R8, etc.). There are some
non-API 526 valves that also exhibit this behavior.

## Slide 61
When a pressure-relief valve is installed on a normally flowing process line, the 3 % limit should be applied to
the sum of the loss in the normally nonflowing PRV inlet pipe and the incremental pressure loss in the
process line caused by the flow through the PRV.

## Slide 63
Isolation Valve Requirements
Isolation (stop) valves are allowed upstream and/or downstream of the pressure-relieving device for the
purpose of inspection, testing, and repair of the pressure-relieving device or discharge header isolation.
For outlet isolation valves, to help minimize the built-up backpressure, the flow area in the outlet isolation
valve should be equal to or greater than the outlet area of the PRV.
Typically, the inlet isolation valves for spare relief devices are closed and the outlet isolation valves are open.
The outlet isolation valve for spare relief devices can be closed during operation if exposure to the fluid is a
concern; however, the pressure temperature rating of the PRD outlet, the outlet isolation valve, and
intervening piping should be suitable for the conditions upstream of the relief device in case of leakage.
Protection of the PRD from discharge system fluids without closing the outlet isolation valve can also be
achieved either by providing a purge or by installing a discharge rupture disk.

## Slide 66
Rupture Disk
Rupture disk devices are non-reclosing PRDs used to protect vessels, piping, and other
pressure-containing components from excessive pressure and/or vacuum. Rupture disks are used in
single and multiple relief device installations. They are also used as redundant PRDs.
With no moving parts, rupture disks are simple, reliable, and faster acting than other PRDs.
Rupture disks react quickly enough to relieve some types of pressure spikes. Because of their light
weight, rupture disks can be made from high alloy and corrosion resistant materials that are not practical
in PRVs.
Rupture disks can be specified for systems with vapor (gas) or liquid pressure-relief
requirements. Also, rupture disk designs are available for highly viscous fluids. The use of rupture disk
devices in liquid service should be carefully evaluated to ensure that the design of the disk is suitable for
liquid service. The user should consult the manufacturer for information regarding liquid service
applications.

## Slide 67
Rupture disk devices often have different opening characteristics as a function of the fluid state
against the disk at the time of bursting. To account for the resulting differences in the resistance to flow,
certified Kr values are stated in terms of Krg (gas), Krl (liquid), or Krgl (gas or liquid). In application, use the
following guidelines.
1.When the fluid initiating rupture (in contact with rupture disk) is compressible, rupture disks rated with
Krg or Krgl should be used.
2.When the fluid initiating rupture (in contact with rupture disk) is incompressible, rupture disks rated
with Krl or Krgl should be used.
The rupture disk is also a temperature-sensitive device. Burst pressures can vary significantly
with the temperature of the rupture disk device. This temperature may be different from the normal fluid
operating temperature. As the temperature at the disk increases, the burst pressure usually decreases.
Since the effect of temperature depends on the rupture disk design and material, the manufacturer should
be consulted for specific applications. For these reasons, the rupture disk shall be specified at the
pressure and temperature the disk is expected to burst.

## Slide 68
Application of Rupture Disks
Rupture disks can be used in any application requiring overpressure protection where a non-reclosing
device is suitable. This includes single, multiple, and fire applications as specified in UG-134 of the ASME
Code.
Rupture Disk Device at the Inlet of a Pressure-relief Valve
Rupture disks are used upstream of PRVs to seal the system to meet emissions standards, to
provide corrosion protection for the valve, and to reduce valve maintenance.
When a rupture disk device is installed at the inlet of a PRV, the devices are considered to be
close coupled, and the specified burst pressure and set pressure should be the same nominal value.
When installed in liquid service, it is especially important for the disk and valve to be close coupled to
reduce shock loading on the valve
The space between the rupture disk and the PRV shall have a free vent, pressure gauge,
trycock, or suitable telltale indicator as required in UG-127 of the ASME Code. Users
are warned that a rupture disk will not burst in tolerance if backpressure builds up in a nonvented space
between the disk and the PRV, which will occur should leakage develop in the rupture disk due to
corrosion or other cause (

## Slide 69
Rupture Disk Device at the Outlet of a Pressure-relief Valve
A rupture disk device may be installed on the outlet of a PRV to protect the valve from atmospheric or
downstream fluids. Consideration should be given to the valve design so that it will open at its proper
pressure setting regardless of any backpressure that may accumulate between the valve and rupture
disk.
Types of Rupture Disks
There are three major rupture disk types
1. Forward-acting, tension-loaded
2. Reverse-acting, compression-loaded;
3. Graphite, shear-loaded.

## Slide 70
Forward-acting Solid Metal Rupture Disks
A forward-acting rupture disk is a formed (domed), solid metal disk designed to burst at a rated pressure
applied to the concave side (see Figure 21). This rupture disk typically has an angular seat design and
provides a satisfactory service life when operating pressures are up to 70 % of the marked burst pressure
of the disk (70 % operating ratio). Consult the manufacturer for the actual recommended operating ratio
for the specific disk under consideration. If vacuum or backpressure conditions are present, the disk can
be furnished with a support to prevent reverse flexing. These disks have a random opening pattern and
are considered fragmenting designs that are not suitable for installation upstream of a PRV

## Slide 72
Forward-acting Scored Rupture Disks
The scored forward-acting rupture disk is a formed (domed) disk designed to burst along scored lines
at a rated pressure applied to the concave side (see Figure 22). Some designs provide satisfactory
service life when operating pressures are up to 85 % to 90 % of the marked burst pressure of the disk
(85 % to 90 % operating ratio). Most designs withstand vacuum conditions without a vacuum
support. If backpressure conditions are present, the disk can be furnished with a support to prevent
reverse flexing. Because the score lines control the opening pattern, this type of disk can be manufactured to be
nonfragmenting and is acceptable for installation upstream of a PRV. The scored,
forward-acting rupture disk is manufactured from thicker material than nonscored designs with the
same burst pressure, and it provides additional resistance to mechanical damage.

## Slide 74
Forward-acting Scored Rupture Disks
A forward-acting composite rupture disk is a flat or domed multipiece construction disk (see
Figure 23). The domed composite rupture disk is designed to burst at a rated pressure applied to the
concave side. The flat composite rupture disk may be designed to burst at a rated pressure in either or
both directions. Some designs are nonfragmenting and acceptable for use upstream of a PRV. A flat composite
rupture disk is available for the protection of low-pressure vessels or the isolation of equipment such as exhaust
headers or the outlet side of a PRV. This disk usually comes complete with gaskets and is designed to be installed
between companion flanges rather than within a specific rupture disk holder. Flat composite rupture disks
generally provide satisfactory service life when operating pressures are 50 % or less of the marked burst pressure
(50 % operating ratio). The slits and tabs in the top section provide a predetermined opening pattern for the
rupture disk. If vacuum or backpressure conditions are present, composite disks can be furnished with a support
to prevent reverse flexing (see Figure 23). A domed, composite rupture disk generally provides satisfactory
service life when the operating pressure is 80 % or less of the marked burst pressure (80 % operating ratio).

## Slide 75
A flat composite rupture disk is available for the protection of low-pressure vessels or the
isolation of equipment such as exhaust headers or the outlet side of a PRV. This disk usually comes
complete with gaskets and is designed to be installed between companion flanges rather than within a
specific rupture disk holder. Flat composite rupture disks generally provide satisfactory service life when
operating pressures are 50 % or less of the marked burst pressure (50 % operating ratio).
Reverse-acting Rupture Disks
A reverse-acting rupture disk typically is a formed (domed) solid metal disk designed to reverse
and burst at a rated pressure applied on the convex side. Reverse-acting rupture disks are designed to
open by such methods as shear knife blades, tooth rings, or scored lines Reverse-acting rupture disks may be
manufactured as nonfragmenting and are suitable for installation upstream of PRVs. These disks provide
satisfactory service life when operating pressures are 90 % or less of marked burst pressure (90 % operating
ratio). Some types of reverse-buckling disks are designed to be exposed to pressures up to 95 % of the marked
burst pressure. Consult the manufacturer for the actual recommended operating ratio for the specific disk under
consideration. Because a reverse acting rupture disk is operated with pressure applied on the convex side,
thicker disk materials may be used, thereby lessening the effects of corrosion, eliminating the need for vacuum
support, and providing longer service life under pressure/vacuum cycling conditions and pressure fluctuations

## Slide 77
Graphite Rupture Disks
Graphite rupture disks are typically machined from a bar of fine graphite that has been
impregnated with a sealing compound to seal the porosity of the graphite matrix (see Figure 26). The disk
operates on a pressure differential across the center diaphragm or web portion of the disk. Graphite
rupture disks provide a satisfactory service life when operating pressures are up to 80 % of the marked
burst pressure (80 % operating ratio) and can be used in both liquid and vapor service.
If vacuum or backpressure conditions are present, the disk can be furnished with a support to
prevent reverse flexing. These disks have a random opening pattern and are considered fragmenting
designs that are not suitable for installation upstream of a PRV. A metallic ring called armoring is often
added to the outside diameter of the disk to help support uneven piping loads and minimize the potential
for cracking of the outer graphite ring and blowout of process fluid.

## Slide 79
Rupture Disk Selection
the user is cautioned to make sure that the upper limit of the manufacturing design range does not exceed the MAWP
of the equipment being protected.

## Slide 83
Selection Procedure

## Slide 84
Sizing Procedure