Rupture Disk

Rupture Disk

Rupture disk devices are non-reclosing PRDs used to protect vessels, piping, and other

pressure-containing components from excessive pressure and/or vacuum. Rupture disks are

used in single and multiple relief device installations. They are also used as redundant PRDs.

With no moving parts, rupture disks are simple, reliable, and faster acting than other PRDs.

Rupture disks react quickly enough to relieve some types of pressure spikes. Because of their

lightweight, rupture disks can be made from high alloy and corrosion resistant materials that are

not practical in PRVs.

Rupture disks can be specified for systems with vapor (gas) or liquid pressure-relief

requirements. Also, rupture disk designs are available for highly viscous fluids. The use of

rupture disk devices in liquid service should be carefully evaluated to ensure that the design of

the disk is suitable for liquid service. The user should consult the manufacturer for information

regarding liquid service applications.

Rupture disk devices often have different opening characteristics as a function of the fluid state

against the disk at the time of bursting. To account for the resulting differences in the resistance

to flow,certified Kr values are stated in terms of Krg (gas), Krl (liquid), or Krgl (gas or liquid). In

application, use the following guidelines.

1.When the fluid initiating rupture (in contact with rupture disk) is compressible, rupture disks

rated with Krg or Krgl should be used.

2.When the fluid initiating rupture (in contact with rupture disk) is incompressible, rupture disks

rated with Krl or Krgl should be used.

The rupture disk is also a temperature-sensitive device. Burst pressures can vary significantly

with the temperature of the rupture disk device. This temperature may be different from the

normal fluid operating temperature. As the temperature at the disk increases, the burst pressure

usually decreases.

Since the effect of temperature depends on the rupture disk design and material, the

manufacturer should be consulted for specific applications. For these reasons, the rupture disk

shall be specified at the pressure and temperature the disk is expected to burst.

Application of Rupture Disks

Rupture disks can be used in any application requiring overpressure protection where a non-

reclosing device is suitable. This includes single, multiple, and fire applications as specified in

UG-134 of the ASME Code.

Rupture Disk Device at the Inlet of a Pressure-relief Valve

Rupture disks are used upstream of PRVs to seal the system to meet emissions standards, to

provide corrosion protection for the valve, and to reduce valve maintenance.

When a rupture disk device is installed at the inlet of a PRV, the devices are considered to be

close coupled, and the specified burst pressure and set pressure should be the same nominal

value. When installed in liquid service, it is especially important for the disk and valve to be

close coupled to reduce shock loading on the valve

The space between the rupture disk and the PRV shall have a free vent, pressure gauge,

Try-cock, or suitable telltale indicator as required in UG-127 of the ASME Code. Users

are warned that a rupture disk will not burst in tolerance if backpressure builds up in a

non-vented space between the disk and the PRV, which will occur should leakage develop in

the rupture disk due to corrosion or other cause.

Rupture Disk Device at the Outlet of a Pressure-relief Valve

A rupture disk device may be installed on the outlet of a PRV to protect the valve from

atmospheric or downstream fluids. Consideration should be given to the valve design so that it

will open at its proper pressure setting regardless of any backpressure that may accumulate

between the valve and rupture disk.

Types of Rupture Disks

There are three major rupture disk types

1. Forward-acting, tension-loaded

2. Reverse-acting, compression-loaded;

3. Graphite, shear-loaded.

Forward-acting Solid Metal Rupture Disks

A forward-acting rupture disk is a formed (domed), solid metal disk designed to burst at a rated

pressure applied to the concave side (see Figure 21). This rupture disk typically has an angular

seat design and provides a satisfactory service life when operating pressures are up to 70 % of

the marked burst pressure of the disk (70 % operating ratio). Consult the manufacturer for the

actual recommended operating ratio for the specific disk under consideration. If vacuum or

backpressure conditions are present, the disk can be furnished with a support to prevent

reverse flexing. These disks have a random opening pattern and are considered fragmenting

designs that are not suitable for installation upstream of a PRV

Forward-acting Scored Rupture Disks

The scored forward-acting rupture disk is a formed (domed) disk designed to burst along scored

lines at a rated pressure applied to the concave side (see Figure 22). Some designs provide

satisfactory service life when operating pressures are up to 85 % to 90 % of the marked burst

pressure of the disk (85 % to 90 % operating ratio). Most designs withstand vacuum conditions

without a vacuum support. If backpressure conditions are present, the disk can be furnished

with a support to prevent reverse flexing. Because the score lines control the opening pattern,

this type of disk can be manufactured to be nonfragmenting and is acceptable for installation

upstream of a PRV. The scored, forward-acting rupture disk is manufactured from thicker

material than nonscored designs with the same burst pressure, and it provides additional

resistance to mechanical damage.

A forward-acting composite rupture disk

A forward-acting composite rupture disk is a flat or domed multipiece construction disk (see

Figure 23). The domed composite rupture disk is designed to burst at a rated pressure applied

to the concave side. The flat composite rupture disk may be designed to burst at a rated

pressure in either or both directions. Some designs are nonfragmenting and acceptable for use

upstream of a PRV. A flat composite rupture  disk is available for the protection of low-pressure

vessels or the isolation of equipment such as exhaust headers or the outlet side of a PRV. This

disk usually comes complete with gaskets and is designed to be installed between companion

flanges rather than within a specific rupture disk holder. Flat composite rupture disks generally

provide satisfactory service life when operating pressures are 50 % or less of the marked burst

pressure (50 % operating ratio). The slits and tabs in the top section provide a predetermined

opening pattern for the rupture disk. If vacuum or backpressure conditions are present,

composite disks can be furnished with a support to prevent reverse flexing (see Figure 23). A

domed, composite rupture disk generally provides satisfactory service life when the operating

pressure is 80 % or less of the marked burst pressure (80 % operating ratio).

A flat composite rupture disk is available for the protection of low-pressure vessels or the

isolation of equipment such as exhaust headers or the outlet side of a PRV. This disk usually

comes complete with gaskets and is designed to be installed between companion flanges rather

than within a specific rupture disk holder. Flat composite rupture disks generally provide

satisfactory service life when operating pressures are 50 % or less of the marked burst pressure

(50 % operating ratio).

Reverse-acting Rupture Disks

A reverse-acting rupture disk typically is a formed (domed) solid metal disk designed to reverse

and burst at a rated pressure applied on the convex side. Reverse-acting rupture disks are

designed to open by such methods as shear knife blades, tooth rings, or scored lines Reverse-

acting rupture disks may be manufactured as non-fragmenting and are suitable for installation

upstream of PRVs. These disks provide satisfactory service life when operating pressures are

90 % or less of marked burst pressure (90 % operating ratio). Some types of reverse-buckling

disks are designed to be exposed to pressures up to 95 % of the marked burst pressure.

Consult the manufacturer for the actual recommended operating ratio for the specific disk under

consideration. Because a reverse acting rupture disk is operated with pressure applied on the

convex side, thicker disk materials may be used, thereby lessening the effects of corrosion,

eliminating the need for vacuum support, and providing longer service life under

pressure/vacuum cycling conditions and pressure fluctuations

Graphite Rupture Disks

Graphite rupture disks are typically machined from a bar of fine graphite that has been

impregnated with a sealing compound to seal the porosity of the graphite matrix (see Figure 26).

The disk operates on a pressure differential across the center diaphragm or web portion of the

disk. Graphite rupture disks provide a satisfactory service life when operating pressures are up

to 80 % of the marked burst pressure (80 % operating ratio) and can be used in both liquid and

vapor service.

If vacuum or backpressure conditions are present, the disk can be furnished with a support to

prevent reverse flexing. These disks have a random opening pattern and are considered

fragmenting designs that are not suitable for installation upstream of a PRV. A metallic ring

called armoring is often added to the outside diameter of the disk to help support uneven piping

loads and minimize the potential for cracking of the outer graphite ring and blowout of process

fluid.

Rupture Disk Selection

the user is cautioned to make sure that the upper limit of the manufacturing design range does

not exceed the MAWP of the equipment being protected.

Selection Procedure

Sizing Procedure