## Notes
Notes for Instrument Catalogue | The catalogue consists of 7 worksheets. All data from Instrument Data Sheets can be found in this catalogue
Worksheet | Comment:
Notes | These Notes
Tag Number Register | A list of the Instrument loop numbers, one line per instrument loop no. In Column A a general Loop No is found. 50 is an instrument loop, 243 is a Control Valve and 288 is a Safety Relief Valve. This is the only worksheet that has been prepared for printing
Component Specifications | A spreadsheet with one line of information per component If there are remarks for a component, the quantity is counted in Column E. Properties pertaining to column R to AT is found in worksheet "Component Properties"
Remarks | Remarks pertaining to the instrument components.
Control Valve Calc. | Data from the calculation block of control valves, one line per control valve
Safety Valve Calc. | Data for calculation of the safety valves, one line per safety valve
Component Properties | Properties for each instrument components. The quantity of components (BOQ) are counted in the "Component Properties" worksheet in Column B

## Tag Number Register_d
Instrument Tag Number Register
Job No. | Loop No. | P&I | Loop Note | Equipment/Pipe | Fluid | P_Nor | T_Nor | P_Max | T_Min | T_Max | P_Unit | T_Unit | Xjno | Un | Type | Serial | Sub | Process Note
S-01722 | AFI-3004 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | [9 empty] | 50 |  | A | 3004
S-01722 | AI-1001 | P01 | Natural Gas from BL | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | A | 1001
S-01722 | AI-1035 | P04 | Outlet R 1001 Hydrogenerator | 16"-PRG-10-101-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | A | 1035
S-01722 | AI-1045 | P04 | Outlet R 1002 2 Sulphur Absorber | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 50 |  | A | 1045
S-01722 | AI-2223 | P13 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | A | 2223
S-01722 | AI-2224 | P13 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | A | 2224
S-01722 | AI-2379 | P18 | Outlet D 2001 HHP Steam Drum | 18"-HHPS-20-102-G24-H | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | A | 2379
S-01722 | AI-2382 | P18 | Outlet D 2001 HHP Steam Drum | 2"-CBD-20-102-G24-P | Continuous Blow Down | 103 | 313 | 113 |  | 330 | bar g | °C | 50 |  | A | 2382
S-01722 | AI-2384 | P18 | Outlet D 2001 HHP Steam Drum | 2"-CBD-20-102-G24-P | Continuous Blow Down | 103 | 313 | 113 |  | 330 | bar g | °C | 50 |  | A | 2384
S-01722 | AI-2479 | P21 | Outlet D 2005 Final Separator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | A | 2479
S-01722 | AI-2531 | U01 | Fuel Gas to Mixing Point | 24"-NG-20-102-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 50 |  | A | 2531
S-01722 | AI-2532 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 50 |  | A | 2532
S-01722 | AI-3001 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | A | 3001
S-01722 | AI-3002 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | A | 3002
S-01722 | AI-3003 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | A | 3003
S-01722 | AI-3053 | P23 | Outlet D 3003 MP Steam Drum | 2"-CBD-30-101-F24-P | Boiler Blow-down | 35 | 242 | 47 |  | 265 | bar g | °C | 50 |  | A | 3053
S-01722 | AI-3055 | P23 | Outlet D 3003 MP Steam Drum | 2"-CBD-30-101-F24-P | Boiler Blow-down | 35 | 242 | 47 |  | 265 | bar g | °C | 50 |  | A | 3055
S-01722 | AIC-7099 | U09 | Outlet D 7001 Deaerator | 18"-BFW-70-129-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | A | 7099
S-01722 | AP-1002 | P01 | Natural Gas from BL | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | A | 1002
S-01722 | AP-1036 | P04 | Outlet R 1001 Hydrogenator | 16"-PRG-10-101-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | A | 1036
S-01722 | AP-1039 | P04 | R 1002 1 Sulphur Absorber | R 1002 1 | Process Gas HDS | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | A | 1039
S-01722 | AP-1040 | P04 | Outlet R 1002 1 Sulphur Absorber | 16"-PRG-10-105-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | A | 1040
S-01722 | AP-1044 | P04 | R 1002 2 Sulphur Absorber | R 1002 2 | Process Gas HDS | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | A | 1044
S-01722 | AP-1046 | P04 | Outlet R 1002 2 Sulphur Absorber | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 50 |  | A | 1046
S-01722 | AP-2031 | P03 | HP Steam from Header | 4"-HPS-70-103-F34-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | A | 2031
S-01722 | AP-2160 | P12 | S 2001 Flue Gas Stack | Flue Gas Stack | Flue Gas | 0 | 161 |  |  |  | bar g | °C | 50 |  | A | 2160
S-01722 | AP-2222 | P13 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | A | 2222
S-01722 | AP-2266 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | A | 2266
S-01722 | AP-2267 | P14 | Outlet R 2003 Prereformer | 30"-RFG-20-101-F34-H | Reformed Gas | 37.7 | 441 | 46 |  | 500 | bar g | °C | 50 |  | A | 2267
S-01722 | AP-2294 | P15 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | A | 2294
S-01722 | AP-2296 | P15 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | A | 2296
S-01722 | AP-2306 | P15 | Cold Collector | Cold Collector | Reformed Gas | 32 | 742 | 34.7 |  | 800 | bar g | °C | 50 |  | A | 2306
S-01722 | AP-2380 | P18 | Outlet D 2001 HHP Steam Drum | 18"-HHPS-20-102-G24-H | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | A | 2380
S-01722 | AP-2383 | P18 | Outlet D 2001 HHP Steam Drum | 2"-CBD-20-102-G24-P | Continuous Blow Down | 103 | 313 | 113 |  | 330 | bar g | °C | 50 |  | A | 2383
S-01722 | AP-2454 | P20 | DMW from BL | 10"-DMW-20-101-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | A | 2454
S-01722 | AP-2480 | P21 | Outlet D 2005 Final Separator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | A | 2480
S-01722 | AP-2539 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 50 |  | A | 2539
S-01722 | AP-2571 | U02 | Start-up N2 from D 2005 | 10"-N-20-110-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | A | 2571
S-01722 | AP-2602 | U17 | Import H2 | 3"-HG-20-102-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | A | 2602
S-01722 | AP-3005 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | A | 3005
S-01722 | AP-3019 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 30"-SG-30-118-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | A | 3019
S-01722 | AP-3022 | P22 | Outlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 32"-SG-30-103-G40-N | Synthesis Gas | 80 | 74 | 99 |  | 120 | bar g | °C | 50 |  | A | 3022
S-01722 | AP-3049 | P23 | Outlet D 3003 MP Steam Drum | 24"-MPS-30-114-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 50 |  | A | 3049
S-01722 | AP-3054 | P23 | Outlet D 3003 MP Steam Drum | 2"-CBD-30-101-F24-P | Boiler Blow-down | 35 | 242 | 47 |  | 265 | bar g | °C | 50 |  | A | 3054
S-01722 | AP-3074 | P24 | Outlet R 3001 1 Methanol Reactor | 24"-SG-30-111-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | A | 3074
S-01722 | AP-3078 | P24 | Outlet R 3001 2 Methanol Reactor | 24"-SG-30-108-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | A | 3078
S-01722 | AP-3082 | P24 | Outlet R 3001 3 Methanol Reactor | 24"-SG-30-120-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | A | 3082
S-01722 | AP-3114 | P25 | Outlet E 3001 1 Feed/Effluent Exchanger | 24"-SG-30-135-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | A | 3114
S-01722 | AP-3195 | P28 | Outlet D 3002 LP Separator | 8"-PG-30-102-B40-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 50 |  | A | 3195
S-01722 | AP-3197 | P28 | Outlet D 3002 LP Separator | 10"-PMC-30-111-B40-N | Crude Methanol | 4 | 48 | 8 |  | 100 | bar g | °C | 50 |  | A | 3197
S-01722 | AP-5010 | P29 | Outlet TK 5001 Raw Methanol Buffer Tank | 16"-PMC-50-101-B40-N | Crude Methanol | 1 | 47 | 4.5 |  | 100 | bar g | °C | 50 |  | A | 5010
S-01722 | AP-5019 | P29 | Outlet P 5001 A/B Raw Methanol Pump | 10"-PMC-50-103-B40-N | Crude Methanol | 5 | 47 | 13 |  | 100 | bar g | °C | 50 |  | A | 5019
S-01722 | AP-5021 | P29 | Outlet T 5004 Vent Wash Column | 24"-VG-50-101-B40-N | Vent Gas | 0 | 59 | 3.5 |  | 100 | bar g | °C | 50 |  | A | 5021
S-01722 | AP-5044 | P30 | Outlet T 5001 Stabilizer Column | 16"-PMC-50-130-B24-H | Crude Methanol | 1 | 88 | 10 |  | 160 | bar g | °C | 50 |  | A | 5044
S-01722 | AP-5052 | P30 | T 5001 Stabilizer Column | T 5001 Top | Methanol Water Gas/Liquid | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5052
S-01722 | AP-5053 | P30 | T 5001 Stabilizer Column | T 5001 Top | Methanol Water Gas/Liquid | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5053
S-01722 | AP-5055 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5055
S-01722 | AP-5056 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5056
S-01722 | AP-5057 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5057
S-01722 | AP-5098 | P32 | Outlet D 5001 Stabilizer Column OH Accumulator | 10"-PMC-50-121-B24 | Crude Methanol | 0.6 | 65 | 13 |  | 150 | bar g | °C | 50 |  | A | 5098
S-01722 | AP-5112 | P32 | Outlet E 5010 OH Gas Condenser | 6"-PG-50-101-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 50 |  | A | 5112
S-01722 | AP-5164 | P34 | Outlet T 5002 LP Methanol Column | 10"-PMC-50-150-D24-H | Crude Methanol | 0.7 | 86 | 16 |  | 160 | bar g | °C | 50 |  | A | 5164
S-01722 | AP-5167 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5167
S-01722 | AP-5171 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5171
S-01722 | AP-5173 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5173
S-01722 | AP-5174 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5174
S-01722 | AP-5175 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5175
S-01722 | AP-5180 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5180
S-01722 | AP-5208 | P36 | Inlet D 5002 LP Column OH Accumulator, Vent | 2"-VA-50-101-B24-P | Vent to Atmosphere | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | A | 5208
S-01722 | AP-5218 | P36 | Outlet P 5004 A/B LP Column Reflux Pump | 12"-PMP-50-104-B24-H | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 50 |  | A | 5218
S-01722 | AP-5261 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5261
S-01722 | AP-5262 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5262
S-01722 | AP-5264 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5264
S-01722 | AP-5265 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5265
S-01722 | AP-5266 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5266
S-01722 | AP-5267 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5267
S-01722 | AP-5268 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5268
S-01722 | AP-5269 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | A | 5269
S-01722 | AP-5274 | P38 | Outlet T 5003 MP Methanol Column | 10"-PMW-50-120-D24-H | Methanol Water | 3.6 | 149 | 15 |  | 175 | bar g | °C | 50 |  | A | 5274
S-01722 | AP-5326 | P40 | Outlet D 5003 MP Cooling OH Accumulator | 24"-PMP-50-130-B24-H | Methanol Product | 2.6 | 101 | 7 |  | 165 | bar g | °C | 50 |  | A | 5326
S-01722 | AP-5382 | P42 | Outlet X 5001 Product Polisher Unit | 10"-PMP-50-143-D24-N | Methanol Product | 3 | 48 | 19 |  | 75 | bar g | °C | 50 |  | A | 5382
S-01722 | AP-5431 | P44 | Outlet P 5008 A/B Methanol Product Pump | 8"-PMP-50-153-B24-N | Methanol Product | 5 | 48 | 14 |  | 75 | bar g | °C | 50 |  | A | 5431
S-01722 | AP-5452 | P45 | Outlet TK 5003 Liquid Off-stream Tank | 2"-LOS-50-120-B24-N | Liquid Off-stream | 0 | 48 | 4.5 |  | 75 | bar g | °C | 50 |  | A | 5452
S-01722 | AP-6059 | P07 | Outlet D 6001 Feed Gas Separator | 16"-PRC-60-110-G40-H | Process Condensate | 43 | 225 | 56 |  | 290 | bar g | °C | 50 |  | A | 6059
S-01722 | AP-7001 | U18 | Outlet TK 7001 1 Demineralized Water Tank | 12"-DMW-70-107-B50-N | Demineralized Water | 0 | 35 | 4.5 |  | 65 | bar g | °C | 50 |  | A | 7001
S-01722 | AP-7002 | U18 | Outlet TK 7001 2 Demineralized Water Tank | 12"-DMW-70-113-B50-N | Demineralized Water | 0 | 35 | 4.5 |  | 65 | bar g | °C | 50 |  | A | 7002
S-01722 | AP-7100 | U09 | Outlet D 7001 Deaerator | 18"-BFW-70-129-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | A | 7100
S-01722 | AP-7101 | U22 | Outlet TK 7002 Process Condensate Tank | 2"-PRC-70-139-B40-N | Process Condensate | 1 | 65 | 7 |  | 100 | bar g | °C | 50 |  | A | 7101
S-01722 | AP-7126 | U10 | Outlet P 7001 A/B/C BFW Pump | 12"-BFW-70-140-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | A | 7126
S-01722 | FFI-2020 | P02 | O2/Carbon Ratio | [9 empty] | 50 |  | F | 2020
S-01722 | FFI-2042 | P03 | O2/Steam Ratio | [9 empty] | 50 |  | F | 2042
S-01722 | FFI-2069 | P09 | Steam/Carbon Ratio | [9 empty] | 50 |  | F | 2069
S-01722 | FFI-2152 | P12 | H2/NG Ratio | [9 empty] | 50 |  | F | 2152
S-01722 | FFSAH-2008 | P02 | O2/Carbon Ratio | [9 empty] | 50 |  | F | 2008
S-01722 | FFSAL-2064 | P09 | Steam/Carbon Ratio | [9 empty] | 50 |  | F | 2064
S-01722 | FHIC-2070 | P09 | Required Steam / Carbon Ratio | [9 empty] | 50 |  | F | 2070
S-01722 | FI-1006 | P01 | Inlet D 1001 Natural Gas K.O. Drum | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | F | 1006
S-01722 | FI-2065 | P09 | Saturated Steam | [9 empty] | 50 |  | F | 2065
S-01722 | FI-2115 | P11 | HP Steam to FT 2002 Steam Turbine for F 2002 | 8"-HPS-70-101-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | F | 2115
S-01722 | FI-2151 | P12 | Inlet E 2006 1st Natural Gas Feed Preheat Coil | 14"-NG-10-105-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 50 |  | F | 2151
S-01722 | FI-2165 | P12 | HP Steam to FT 2001 Steam Turbine for F 2001 | 6"-HPS-70-111-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | F | 2165
S-01722 | FI-2372 | P18 | Outlet D 2001 HHP Steam Drum | 18"-HHPS-20-102-G24-H | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | F | 2372
S-01722 | FI-2476 | P21 | Outlet D 2005 Final Separator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | F | 2476
S-01722 | FI-2582 | U02 | Outlet C 2001 Start-up Nitrogen Compressor | 10"-N-20-104-B24-P | Nitrogen Gas | 8 | 84 | 10.5 |  | 110 | bar g | °C | 50 |  | F | 2582
S-01722 | FI-2607 | U17 | Recycle Hydrogen from Loop | 3"-SG-30-128-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | F | 2607
S-01722 | FI-3010 | P22 | Synthesis Gas to R 3001 Catalyst Reduction | 3"-SG-30-129-D40-N | Synthesis Gas | 10 | 48 | 29 |  | 100 | bar g | °C | 50 |  | F | 3010
S-01722 | FI-3013 | P22 | Hydrogen from BL | 3"-HG-30-101-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | F | 3013
S-01722 | FI-3016 | P22 | Process Air from BL | 3"-PA-30-101-B24-N | Process Air | 7.5 | 35 | 10.5 |  | 75 | bar g | °C | 50 |  | F | 3016
S-01722 | FI-3020 | P22 | Outlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 18"-SG-30-101-H40-H | Synthesis Gas | 80 | 122 | 99 |  | 165 | bar g | °C | 50 |  | F | 3020
S-01722 | FI-3050 | P23 | Outlet D 3003 MP Steam Drum | 24"-MPS-30-114-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 50 |  | F | 3050
S-01722 | FI-3167 | P27 | Outlet D 3001 HP Separator | 30"-SG-30-118-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | F | 3167
S-01722 | FI-3168 | P27 | Total Synthesis Gas Circulation | [9 empty] | 50 |  | F | 3168
S-01722 | FI-3194 | P28 | Outlet D 3002 LP Separator | 8"-PG-30-102-B40-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 50 |  | F | 3194
S-01722 | FI-3198 | P28 | Outlet D 3002 LP Separator | 10"-PMC-30-108-B40-N | Crude Methanol | 4 | 48 | 8 |  | 100 | bar g | °C | 50 |  | F | 3198
S-01722 | FI-5021 | P29 | Nitrogen for blanketing of TK 5001 | 2"-N-50-101-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | F | 5021
S-01722 | FI-5068 | P31 | Inlet E 5001 Stabilizer Column Steam Reboiler | 14"-LPS-70-104-D24-H | Low Pressure Steam | 7 | 188 | 9.5 |  | 340 | bar g | °C | 50 |  | F | 5068
S-01722 | FI-5111 | P32 | Outlet E 5010 OH Gas Condenser | 6"-PG-50-101-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 50 |  | F | 5111
S-01722 | FI-5338 | P40 | Production | [9 empty] | 50 |  | F | 5338
S-01722 | FI-5407 | P43 | Outlet P 5012 Methanol Start-up Pump | 3"-PMP-50-161-F24-N | Methanol Product | 47 | 48 | 52 |  | 75 | bar g | °C | 50 |  | F | 5407
S-01722 | FI-5408 | P43 | Nitrogen for blanketing of TK 5002 1 | 2"-N-50-113-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | F | 5408
S-01722 | FI-5421 | P44 | Methanol Product to Production Tank | 8"-PMP-50-153-B24-N | Methanol Product | 5 | 48 | 14 |  | 75 | bar g | °C | 50 |  | F | 5421
S-01722 | FI-5422 |  | Nitrogen for blanketing of TK 5002 2 | 2"-N-50-108-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | F | 5422
S-01722 | FI-5442 | P45 | Nitrogen for blanketing of TK 5003 | 2"-N-50-111-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | F | 5442
S-01722 | FI-6032 | P06 | BFW from Header | 4"-BFW-70-102-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 50 |  | F | 6032
S-01722 | FI-6057 | P07 | Liquid Off-stream from P 5009 A/B | 2"-LOS-50-122-F24-N | Liquid Off-stream | 53 | 50 | 60 |  | 75 | bar g | °C | 50 |  | F | 6057
S-01722 | FI-6068 | P07 | Outlet P 6001 A/B Saturator Circulation Pump | 10"-PRC-60-111-G40-H | Process Condensate | 44 | 225 | 72 |  | 290 | bar g | °C | 50 |  | F | 6068
S-01722 | FI-7001 | U03 | HP Extraction Steam from FT 3001 1/2 | 16"-HPS-30-129-F24-H | High Pressure Steam | 45 | 355 | 52 |  | 410 | bar g | °C | 50 |  | F | 7001
S-01722 | FI-7029 | U04 | HP Steam Header | 24"-HPS-70-107-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | F | 7029
S-01722 | FI-7030 | U04 | HP Import Steam to Header | 24"-HPS-70-136-F34-H | High Pressure Steam | 42 | 410 | 52 |  | 470 | bar g | °C | 50 |  | F | 7030
S-01722 | FI-7101 | U22 | Outlet P 7004 A/B Excess Condensate Pumps | 2"-PRC-70-141-G40-N | Process Condensate | 46 | 65 | 71 |  | 100 | bar g | °C | 50 |  | F | 7101
S-01722 | FI-7129 | U10 | HP Steam to FP 7001 A Steam Turbine for FP 7001 A | 8"-HPS-70-117-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | F | 7129
S-01722 | FI-7134 | U10 | HP Steam to FP 7001 B Steam Turbine for FP 7001 B | 8"-HPS-70-118-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | F | 7134
S-01722 | FIC-2007 | P02 | Process Oxygen to E 2008 Oxygen Preheater | 10"-PO-20-106-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | F | 2007
S-01722 | FIC-2009 | P02 | Process Oxygen to E 2008 Oxygen Preheater, Start-up | 6"-PO-20-104-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | F | 2009
S-01722 | FIC-2040 | P03 | HP Steam to Mixing Point | 4"-HPS-20-108-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | F | 2040
S-01722 | FIC-2061 | P09 | Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-60-104-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 50 |  | F | 2061
S-01722 | FIC-2072 | P09 | HP Steam from Header | 12"-HPS-70-125-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | F | 2072
S-01722 | FIC-2079 | P09 | H2 from Recycle Header | 3"-HG-20-110-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 50 |  | F | 2079
S-01722 | FIC-2091 | P10 | Saturated Natural Gas to Steam/NG Mixture, Start-up | 12"-PRG-20-106-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 50 |  | F | 2091
S-01722 | FIC-2111 | P11 | Outlet F 2002 Combustion Air Blower | Ducting | Combustion Air | 21 | 54 |  |  | 80 | mbar g | °C | 50 |  | F | 2111
S-01722 | FIC-2150 | P12 | H2 Recycle from Header | 3"-HG-20-112-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 50 |  | F | 2150
S-01722 | FIC-2233 | P13 | Quench of Process Gas | 3"-PRC-20-102-G40-N | Process Condensate | 52 | 49 | 80 |  | 106 | bar g | °C | 50 |  | F | 2233
S-01722 | FIC-2417 | P19 | BFW from Header | 12"-BFW-70-107-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | F | 2417
S-01722 | FIC-2531 | U01 | Fuel Gas to Mixing Point | 24"-NG-20-102-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 50 |  | F | 2531
S-01722 | FIC-2536 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 50 |  | F | 2536
S-01722 | FIC-3041 | P23 | HP BFW from Header | 10"-MPC-30-102-F24-H | Medium Pressure Steam Condensate | 33.7 | 230 | 47 |  | 260 | bar g | °C | 50 |  | F | 3041
S-01722 | FIC-3169 | P27 | Purge Gas to Fuel Gas Header | 6"-SG-30-138-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | F | 3169
S-01722 | FIC-3171 | P27 | Inlet J 3001 Ejector | 6"-SG-30-139-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | F | 3171
S-01722 | FIC-5020 | P29 | Wash Water to T 5004 Vent Wash Column | 2"-PMW-50-101-B24-N | Methanol Water | 4 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | F | 5020
S-01722 | FIC-5041 | P30 | Inlet T 5001 Stabilizer Column | 10"-PMC-50-103-B40-N | Crude Methanol | 5 | 47 | 13 |  | 100 | bar g | °C | 50 |  | F | 5041
S-01722 | FIC-5093 | P32 | Reflux to T 5001 | 8"-PMC-50-123-B24-N | Crude Methanol | 3.8 | 65 | 13 |  | 150 | bar g | °C | 50 |  | F | 5093
S-01722 | FIC-5107 | P32 | Liquid Off-stream to E 5011 | 2"-LOS-50-101-B24-P | Liquid Off-stream | 3.8 | 65 | 13 |  | 150 | bar g | °C | 50 |  | F | 5107
S-01722 | FIC-5161 | P34 | Inlet T 5002 LP Methanol Column | 10"-PMC-50-132-B24-H | Crude Methanol | 2.5 | 88 | 10 |  | 160 | bar g | °C | 50 |  | F | 5161
S-01722 | FIC-5203 | P36 | Outlet P 5004 A/B LP Column Reflux Pump | 12"-PMP-50-104-B24-H | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 50 |  | F | 5203
S-01722 | FIC-5239 | P37 | Outlet P 5005 A/B MP Column Feed Pump | 8"-PMC-50-152-D24-H | Crude Methanol | 6.5 | 86 | 16 |  | 160 | bar g | °C | 50 |  | F | 5239
S-01722 | FIC-5301 | P39 | LP Steam to E 5003 1/2/3 MP Column Reboiler No. 1 | 32"-LPS-70-105-D24-H | Low Pressure Steam | 7 | 188 | 9.5 |  | 340 | bar g | °C | 50 |  | F | 5301
S-01722 | FIC-5321 | P40 | Methanol to T 5003 | 12"-PMP-50-132-D24-H | Methanol Product | 6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | F | 5321
S-01722 | FIC-5336 | P40 | Outlet E 5012 Methanol Product Cooler No. 2 | 6"-PMP-50-141-D24-N | Methanol Product | 5.7 | 48 | 19 |  | 75 | bar g | °C | 50 |  | F | 5336
S-01722 | FIC-5337 | P40 | Methanol from E 5008 Methanol Product Cooler No. 1 | 6"-PMP-50-111-D24-N | Methanol Product | 3.5 | 48 | 19 |  | 75 | bar g | °C | 50 |  | F | 5337
S-01722 | FIC-5367 | P41 | Outlet P 5010 A/B Excess Water Pump | 3"-PMW-50-132-F24-H | Methanol Water | 50 | 150 | 82 |  | 175 | bar g | °C | 50 |  | F | 5367
S-01722 | FIC-5383 | P42 | DMW from Header | 2"-DMW-50-101-B50-N | Demineralized Water | 5 | 35 | 7 |  | 65 | bar g | °C | 50 |  | F | 5383
S-01722 | FIC-5441 | P45 | Liquid Off-stream from T 5003 | 2"-LOS-50-110-B24-P | Liquid Off-stream | 3.4 | 115 | 7.5 |  | 175 | bar g | °C | 50 |  | F | 5441
S-01722 | FIC-5501 | U23A | Inlet E 5014 Feed Effluent Exchanger (optional) | 6"-PMW-50-194-B24-H | Methanol Water | 3.6 | 149 | 7.5 |  | 175 | bar g | °C | 50 |  | F | 5501
S-01722 | FIC-6031 | P06 | Outlet X 6001 A/B Particle Filter | 8"-PRC-60-102-G40-H | Process Condensate | 44 | 119 | 71 |  | 180 | bar g | °C | 50 |  | F | 6031
S-01722 | FIC-6070 | P07 | Inlet E 6001 Saturator Feed/Effluent Exchanger | 16"-PRG-60-110-F24-H | Process Gas | 43.8 | 358 | 55 |  | 410 | bar g | °C | 50 |  | F | 6070
S-01722 | FIC-6081 | P08 | Inlet D 6002 Saturator Blow Down Drum | 2"-BD-60-109-G40-H | Blow-down | 44 | 78 | 57 |  | 260 | bar g | °C | 50 |  | F | 6081
S-01722 | FIC-6082 | P08 | Saturator Blowdown to BL | 2"-BD-60-121-B40-P | Process Condensate | 2.5 | 100 | 9 |  | 125 | bar g | °C | 50 |  | F | 6082
S-01722 | FIC-6086 | P08 | Inlet D 6002 Saturator Blow Down Drum | 4"-BD-60-114-G40-H | Boiler Blow-down | 43 | 225 | 56 |  | 290 | bar g | °C | 50 |  | F | 6086
S-01722 | FIC-7091 | U09 | DMW to D 7001 Deaerator | 8"-DMW-20-104-B50-H | Demineralized Water | 4.5 | 72 | 14 |  | 110 | bar g | °C | 50 |  | F | 7091
S-01722 | FIC-7141 | U11 | HHP BFW To HP BFW Header | 8"-BFW-70-163-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | F | 7141
S-01722 | FO-2483 | P21 | Outlet D 2005 Final Separator, Vent | 12"-SG-20-107-D40-N | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | F | 2483
S-01722 | FO-2552 | U01 | Fuel Gas for Burner Tightness Test | 2"-NG-20-113-B24-N | Fuel Gas | 3 | 35 | 7 |  | 85 | bar g | °C | 50 |  | F | 2552
S-01722 | FO-3191 | P28 | Inlet D 3002 LP Separator | 12"-PMC-30-105-G40-N | Crude Methanol | 32 | 47 | 100 |  | 100 | bar g | °C | 50 |  | F | 3191
S-01722 | FO-7096 | U09 | D 7001 Deaerator, Vent | 2"-LPS-70-130-B24-H | Low Pressure Steam | 1 | 120 | 3.5 |  | 340 | bar g | °C | 50 |  | F | 7096
S-01722 | FSAL-2062 | P09 | Saturated Steam | [9 empty] | 50 |  | F | 2062
S-01722 | FSY-2063 | P09 | Multiplier | [9 empty] | 50 |  | F | 2063
S-01722 | FV-2007 | P02 | Process Oxygen to E 2008 Oxygen Preheater | 10"-PO-20-106-F70-N | Process Oxygen | 39 | 35 | 47 |  | 85 | bar g | °C | 243 |  | F | 2007
S-01722 | FV-2009 | P02 | Process Oxygen to E 2008 Oxygen Preheater, Start-up | 4"-PO-20-105-F70-N | Process Oxygen | 39 | 35 | 47 |  | 85 | bar g | °C | 243 |  | F | 2009
S-01722 | FV-2040 | P03 | HP Steam to Mixing Point | 4"-HPS-20-108-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | F | 2040
S-01722 | FV-2061 | P10 | Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-60-104-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 243 |  | F | 2061
S-01722 | FV-2072 | P09 | HP Steam from Header to mixpoint | 12"-HPS-70-125-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | F | 2072
S-01722 | FV-2079 | P09 | H2 from Recycle Header | 3"-HG-20-110-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 243 |  | F | 2079
S-01722 | FV-2091 | P10 | Saturated Natural Gas to Steam/NG Mixture, Start-up | 12"-PRG-20-106-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 243 |  | F | 2091
S-01722 | FV-2150 | P12 | H2 Recycle from Header | 3"-HG-20-112-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 243 |  | F | 2150
S-01722 | FV-2233/1 | P13 | Process Condensate from P 2003 A/B | 3"-PRC-20-130-G40-N | Process Condensate | 53 | 49 | 80 |  | 100 | bar g | °C | 243 |  | F | 2233 | 1
S-01722 | FV-2233/2 | P13 | HP BFW from Header | 3"-BFW-70-103-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | F | 2233 | 2
S-01722 | FV-2417 | P19 | BFW from Header to D 2001 HHP Steam Drum | 12"-BFW-70-107-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | F | 2417
S-01722 | FV-2531/1 | U01 | Fuel Gas to Mixing Point | 10"-NG-20-104-B24-N | Fuel Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 243 |  | F | 2531 | 1
S-01722 | FV-2531/2 | U01 | Fuel Gas to Mixing Point | 24"-NG-20-112-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 243 |  | F | 2531 | 2
S-01722 | FV-2536 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 243 |  | F | 2536
S-01722 | FV-3041 | P23 | HP BFW from Header | 8"-BFW-70-101-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 243 |  | F | 3041
S-01722 | FV-3169 | P27 | Purge Gas to Fuel Gas Header | 6"-SG-30-138-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 243 |  | F | 3169
S-01722 | FV-3171 | P27 | Inlet J 3001 Ejector | 6"-SG-30-139-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 243 |  | F | 3171
S-01722 | FV-5020 | P29 | Wash Water to T 5004 Vent Wash Column | 2"-PMW-50-101-B24-N | Methanol Water | 4 | 48 | 7.5 |  | 100 | bar g | °C | 243 |  | F | 5020
S-01722 | FV-5041 | P30 | Inlet T 5001 Stabilizer Column | 10"-PMC-50-103-B40-N | Crude Methanol | 5 | 47 | 13 |  | 100 | bar g | °C | 243 |  | F | 5041
S-01722 | FV-5093 | P32 | Reflux to T 5001 | 8"-PMC-50-123-B24-N | Crude Methanol | 3.8 | 65 | 13 |  | 150 | bar g | °C | 243 |  | F | 5093
S-01722 | FV-5107 | P32 | Liquid Off-stream to E 5011 | 2"-LOS-50-101-B24-P | Liquid Off-stream | 3.8 | 65 | 13 |  | 150 | bar g | °C | 243 |  | F | 5107
S-01722 | FV-5161 | P34 | Inlet T 5002 LP Methanol Column | 10"-PMC-50-132-B24-H | Crude Methanol | 2.5 | 88 | 10 |  | 160 | bar g | °C | 243 |  | F | 5161
S-01722 | FV-5203 | P36 | Reflux TO T 5002 | 12"-PMP-50-104-B24-H | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 243 |  | F | 5203
S-01722 | FV-5239 | P37 | Outlet P 5005 A/B MP Column Feed Pump | 8"-PMC-50-152-D24-H | Crude Methanol | 6.5 | 86 | 16 |  | 160 | bar g | °C | 243 |  | F | 5239
S-01722 | FV-5301 | P39 | LP Steam Condensate to D 7001 | 16"-LPC-50-115-B24-H | Low Pressure Steam Condensate | 6.5 | 168 | 10.5 |  | 190 | bar g | °C | 243 |  | F | 5301
S-01722 | FV-5321 | P40 | Methanol to T 5003 | 12"-PMP-50-132-D24-H | Methanol Product | 6 | 101 | 19 |  | 165 | bar g | °C | 243 |  | F | 5321
S-01722 | FV-5336 | P40 | Outlet E 5012 Methanol Product Cooler No. 2 | 6"-PMP-50-141-D24-N | Methanol Product | 5.7 | 48 | 19 |  | 75 | bar g | °C | 243 |  | F | 5336
S-01722 | FV-5337 | P40 | Methanol from E 5008 Methanol Product Cooler No. 1 | 6"-PMP-50-111-D24-N | Methanol Product | 3.5 | 48 | 19 |  | 75 | bar g | °C | 243 |  | F | 5337
S-01722 | FV-5367 | P41 | Outlet P 5010 A/B Excess Water Pump | 3"-PMW-50-132-F24-H | Methanol Water | 50 | 150 | 82 |  | 175 | bar g | °C | 243 |  | F | 5367
S-01722 | FV-5383 | P42 | DMW from Header | 2"-DMW-50-101-B50-N | Demineralized Water | 5 | 35 | 7 |  | 65 | bar g | °C | 243 |  | F | 5383
S-01722 | FV-5441 | P45 | Liquid Off-stream from T 5003 | 2"-LOS-50-110-B24-P | Liquid Off-stream | 3.4 | 115 | 7.5 |  | 175 | bar g | °C | 243 |  | F | 5441
S-01722 | FV-5501 | U23A | Inlet E 5014 Feed Effluent Exchanger (optional) | 6"-PMW-50-194-B24-H | Methanol Water | 3.6 | 149 | 7.5 |  | 175 | bar g | °C | 243 |  | F | 5501
S-01722 | FV-6031 | P06 | BFW from Header | 4"-BFW-70-102-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | F | 6031
S-01722 | FV-6070 | P07 | Natural Gas from R 1002 2 Sulphur Absorber | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 243 |  | F | 6070
S-01722 | FV-6081 | P08 | Inlet D 6002 Saturator Blow Down Drum from T 6001 Saturator | 2"-BD-60-109-G40-H | Blow-down | 44 | 78 | 57 |  | 260 | bar g | °C | 243 |  | F | 6081
S-01722 | FV-6082 | P08 | Outlet P 7003 A&B Excess Process Condensate Pumps | 2"-BD-60-121-B40-P | Process Condensate | 2.5 | 100 | 9 |  | 125 | bar g | °C | 243 |  | F | 6082
S-01722 | FV-6086 | P08 | Inlet D 6002 Saturator BD Drum from D 6001 Feed Gas Sep. | 4"-BD-60-114-G40-H | Boiler Blow-down | 43 | 225 | 56 |  | 290 | bar g | °C | 243 |  | F | 6086
S-01722 | FV-7091 | U09 | DMW to D 7001 Deaerator | 8"-DMW-20-104-B50-H | Demineralized Water | 4.5 | 72 | 14 |  | 110 | bar g | °C | 243 |  | F | 7091
S-01722 | FV-7141 | U11 | HHP BFW To HP BFW Header | 8"-BFW-70-163-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | F | 7141
S-01722 | FZ-2233 | P13 | Quench of Process Gas from Mixing Point | 24"-PRG-20-112-F24-H | Process Gas | 42.1 | 267 | 46 |  | 410 | bar g | °C | 243 |  | F | 2233
S-01722 | FZ-6058 | P07 | Liquid Off-stream from P 5009 A/B | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 243 |  | F | 6058
S-01722 | HIC-2031 | P03 | HP Steam to Process Oxygen Warm-up Vent | [9 empty] | 50 |  | H | 2031
S-01722 | HIC-2076 | P09 | HV-2076 | [9 empty] | 50 |  | H | 2076
S-01722 | HIC-2097 | P10 | HP Steam to Mixing Point (Vent) | [9 empty] | 50 |  | H | 2097
S-01722 | HIC-2119 | P11 | FT 2002 Steam Turbine for F 2002 | [9 empty] | 50 |  | H | 2119
S-01722 | HIC-2151 | P12 | H2/NG | [9 empty] | 50 |  | H | 2151
S-01722 | HIC-2167 | P12 | FT 2001 Steam Turbine for F 2001 | [9 empty] | 50 |  | H | 2167
S-01722 | HIC-2225 | P13 | False Air Dampers | [9 empty] | 50 |  | H | 2225
S-01722 | HIC-2371 | P18 | HV-2371 | [9 empty] | 50 |  | H | 2371
S-01722 | HIC-2472 | P21 | AE 2026 Air Cooler | [9 empty] | 50 |  | H | 2472
S-01722 | HIC-2532 | U01 | LHV NG | [9 empty] | 50 |  | H | 2532
S-01722 | HIC-2533 | U01 | Air/NG | [9 empty] | 50 |  | H | 2533
S-01722 | HIC-2534 | U01 | Min. NG | [9 empty] | 50 |  | H | 2534
S-01722 | HIC-2537 | U01 | LHV PG | [9 empty] | 50 |  | H | 2537
S-01722 | HIC-2538 | U01 | Air/Purge Gas | [9 empty] | 50 |  | H | 2538
S-01722 | HIC-3011 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | [9 empty] | 50 |  | H | 3011
S-01722 | HIC-3020 | P22 | MW of Make Up Gas | [9 empty] | 50 |  | H | 3020
S-01722 | HIC-3142 | P26 | AE 3002 1 Loop Air Cooler | [9 empty] | 50 |  | H | 3142
S-01722 | HIC-3145 | P26 | AE 3002 2 Loop Air Cooler | [9 empty] | 50 |  | H | 3145
S-01722 | HIC-3148 | P26 | AE 3002 3 Loop Air Cooler | [9 empty] | 50 |  | H | 3148
S-01722 | HIC-3167 | P27 | MW of Recycle gas | [9 empty] | 50 |  | H | 3167
S-01722 | HIC-5093 | P32 | AE 5004 Stabilizer Column OH Condenser | [9 empty] | 50 |  | H | 5093
S-01722 | HIC-5202 | P36 | AE 5005 LP Column OH Condenser | [9 empty] | 50 |  | H | 5202
S-01722 | HIC-5336 | P40 | Ratio Reflux / Product MP Column | [9 empty] | 50 |  | H | 5336
S-01722 | HIC-5337 | P40 | Ratio Reflux / Product LP Column | [9 empty] | 50 |  | H | 5337
S-01722 | HIC-5338 | P40 | Vent from D 5003 MP Column OH Accumulator | [9 empty] | 50 |  | H | 5338
S-01722 | HIC-5369 | P41 | AE 5006 Wash Water Air Cooler | [9 empty] | 50 |  | H | 5369
S-01722 | HIC-5403 | P43 | P 5012 Methanol Start-up Pump | [9 empty] | 50 |  | H | 5403
S-01722 | HIC-5454 | P45 | P 5009 A Liquid Off-stream Pump | [9 empty] | 50 |  | H | 5454
S-01722 | HIC-5458 | P45 | P 5009 B Liquid Off-stream Pump | [9 empty] | 50 |  | H | 5458
S-01722 | HIC-6068 | P07 | Moleweight of NG & Offstream | [9 empty] | 50 |  | H | 6068
S-01722 | HIC-6069 | P07 | HV-6069 | [9 empty] | 50 |  | H | 6069
S-01722 | HIC-7102 | U22 | P 7004 A Excess Process Condensate Pump | [9 empty] | 50 |  | H | 7102
S-01722 | HIC-7104 | U22 | P 7004 B Excess Process Condensate Pump | [9 empty] | 50 |  | H | 7104
S-01722 | HIC-7131 | U10 | FP 7001 A Steam Turbine for P 7001 A | [9 empty] | 50 |  | H | 7131
S-01722 | HIC-7136 | U10 | FP 7001 B Steam Turbine for P 7001 B | [9 empty] | 50 |  | H | 7136
S-01722 | HS-1003 | P01 | Natural Gas from BL | [9 empty] | 50 |  | H | 1003
S-01722 | HS-2003 | P02 | Process Oxygen from BL | [9 empty] | 50 |  | H | 2003
S-01722 | HS-2095 | P10 | Common Local Reset for USY-2092, USY-2093 & USY-2094 | [9 empty] | 50 |  | H | 2095
S-01722 | HS-2098 | P10 | HV-2098 | [9 empty] | 50 |  | H | 2098
S-01722 | HS-2410 | P19 | P 2001 A Process Condensate Pump No. 1 | [9 empty] | 50 |  | H | 2410
S-01722 | HS-2414 | P19 | P 2001 B Process Condensate Pump No. 1 | [9 empty] | 50 |  | H | 2414
S-01722 | HS-2447 | P20 | P 2002 A Process Condensate Pump No. 2 | [9 empty] | 50 |  | H | 2447
S-01722 | HS-2451 | P20 | P 2002 B Process Condensate Pump No. 2 | [9 empty] | 50 |  | H | 2451
S-01722 | HS-2471 | P21 | AE 2026 Air Cooler | [9 empty] | 50 |  | H | 2471
S-01722 | HS-2487 | P21 | P 2003 A Process Condensate Pump No. 3 | [9 empty] | 50 |  | H | 2487
S-01722 | HS-2491 | P21 | P 2003 B Process Condensate Pump No. 3 | [9 empty] | 50 |  | H | 2491
S-01722 | HS-2544 | U01 | Common Local Reset for USY-2541, USY-2542 & USY-2543 | [9 empty] | 50 |  | H | 2544
S-01722 | HS-2550 | U01 | Burner Leak Test | [9 empty] | 50 |  | H | 2550
S-01722 | HS-2577 | U02 | C 2001 Start-up Nitrogen Compressor | [9 empty] | 50 |  | H | 2577
S-01722 | HS-3141 | P26 | AE 3002 1 Loop Air Cooler | [9 empty] | 50 |  | H | 3141
S-01722 | HS-3144 | P26 | AE 3002 2 Loop Air Cooler | [9 empty] | 50 |  | H | 3144
S-01722 | HS-3147 | P26 | AE 3002 3 Loop Air Cooler | [9 empty] | 50 |  | H | 3147
S-01722 | HS-5013 | P29 | P 5001 A Raw Methanol Pump | [9 empty] | 50 |  | H | 5013
S-01722 | HS-5017 | P29 | P 5001 B Raw Methanol Pump | [9 empty] | 50 |  | H | 5017
S-01722 | HS-5077 | P31 | P 5011 A Steam Condensate Pump | [9 empty] | 50 |  | H | 5077
S-01722 | HS-5081 | P31 | P 5011 B Steam Condensate Pump | [9 empty] | 50 |  | H | 5081
S-01722 | HS-5092 | P32 | AE 5004 Stabilizer Column OH Condenser | [9 empty] | 50 |  | H | 5092
S-01722 | HS-5101 | P32 | P 5003 A Stabilizer Column Reflux Pump | [9 empty] | 50 |  | H | 5101
S-01722 | HS-5105 | P32 | P 5003 B Stabilizer Column Reflux Pump | [9 empty] | 50 |  | H | 5105
S-01722 | HS-5133 | P33 | P 5002 A Stabilizer Methanol Pump | [9 empty] | 50 |  | H | 5133
S-01722 | HS-5137 | P33 | P 5002 B Stabilizer Methanol Pump | [9 empty] | 50 |  | H | 5137
S-01722 | HS-5201 | P36 | AE 5005 LP Column OH Condenser | [9 empty] | 50 |  | H | 5201
S-01722 | HS-5212 | P36 | P 5004 A LP Column Reflux Pump | [9 empty] | 50 |  | H | 5212
S-01722 | HS-5216 | P36 | P 5004 B LP Column Reflux Pump | [9 empty] | 50 |  | H | 5216
S-01722 | HS-5232 | U15 | P 5080 A Morpholine Dosing Pump | [9 empty] | 50 |  | H | 5232
S-01722 | HS-5233 | P37 | P 5005 A MP Column Feed Pump | [9 empty] | 50 |  | H | 5233
S-01722 | HS-5236 | U15 | P 5080 B Morpholine Dosing Pump | [9 empty] | 50 |  | H | 5236
S-01722 | HS-5237 | P37 | P 5005 B MP Column Feed Pump | [9 empty] | 50 |  | H | 5237
S-01722 | HS-5329 | P40 | P 5006 A MP Column Reflux Pump | [9 empty] | 50 |  | H | 5329
S-01722 | HS-5333 | P40 | P 5006 B MP Column Reflux Pump | [9 empty] | 50 |  | H | 5333
S-01722 | HS-5353 | P41 | P 5007 A MP Column Recycle Pump | [9 empty] | 50 |  | H | 5353
S-01722 | HS-5357 | P41 | P 5007 B MP Column Recycle Pump | [9 empty] | 50 |  | H | 5357
S-01722 | HS-5361 | P41 | P 5010 A Excess Water Pump | [9 empty] | 50 |  | H | 5361
S-01722 | HS-5365 | P41 | P 5010 B Excess Water Pump | [9 empty] | 50 |  | H | 5365
S-01722 | HS-5368 | P41 | AE 5006 Wash Water Air Cooler | [9 empty] | 50 |  | H | 5368
S-01722 | HS-5404 | P43 | P 5012 Methanol Start-up Pump | [9 empty] | 50 |  | H | 5404
S-01722 | HS-5425 | P44 | P 5008 A Methanol Product Pump | [9 empty] | 50 |  | H | 5425
S-01722 | HS-5429 | P44 | P 5008 B Methanol Product Pump | [9 empty] | 50 |  | H | 5429
S-01722 | HS-5455 | P45 | P 5009 A Liquid Off-stream Pump | [9 empty] | 50 |  | H | 5455
S-01722 | HS-5459 | P45 | P 5009 B Liquid Off-stream Pump | [9 empty] | 50 |  | H | 5459
S-01722 | HS-5511 | U24 | P 5070 A NaOH Solution Dosing Pump (optional) | [9 empty] | 50 |  | H | 5511
S-01722 | HS-5517 | U24 | P 5070 B NaOH Solution Dosing Pump (optional) | [9 empty] | 50 |  | H | 5517
S-01722 | HS-6004 | P05 | P 6002 A Steam Condensate Return Pump | [9 empty] | 50 |  | H | 6004
S-01722 | HS-6008 | P05 | P 6002 B Steam Condensate Return Pump | [9 empty] | 50 |  | H | 6008
S-01722 | HS-6062 | P07 | P 6001 A Saturator Circulation Pump | [9 empty] | 50 |  | H | 6062
S-01722 | HS-6066 | P07 | P 6001 B Saturator Circulation Pump | [9 empty] | 50 |  | H | 6066
S-01722 | HS-6081 | P08 | P 7003 A Excess Process Condensate Pump | [9 empty] | 50 |  | H | 6081
S-01722 | HS-6086 | P08 | P 7003 B Excess Process Condensate Pump | [9 empty] | 50 |  | H | 6086
S-01722 | HS-7001 | U03 | [10 empty] | 50 |  | H | 7001
S-01722 | HS-7005 | U18 | P 7002 A Demineralized Water Pump | [9 empty] | 50 |  | H | 7005
S-01722 | HS-7006 | U18 | P 7002 B Demineralized Water Pump | [9 empty] | 50 |  | H | 7006
S-01722 | HS-7101 | U22 | P 7004 A Excess Process Condensate Pump | [9 empty] | 50 |  | H | 7101
S-01722 | HS-7103 | U22 | P 7004 B Excess Process Condensate Pump | [9 empty] | 50 |  | H | 7103
S-01722 | HS-7122 | U10 | P 7001 C BFW Pump | [9 empty] | 50 |  | H | 7122
S-01722 | HS-7163 | U12 | P 7051 A Phosphate Dosing Pump | [9 empty] | 50 |  | H | 7163
S-01722 | HS-7166 | U12 | P 7051 B Phosphate Dosing Pump | [9 empty] | 50 |  | H | 7166
S-01722 | HS-7169 | U12 | P 7052 A Phosphate Dosing Pump | [9 empty] | 50 |  | H | 7169
S-01722 | HS-7172 | U12 | P 7052 B Phosphate Dosing Pump | [9 empty] | 50 |  | H | 7172
S-01722 | HS-7193 | U13 | P 7060 A Ammonia Dosing Pump | [9 empty] | 50 |  | H | 7193
S-01722 | HS-7196 | U13 | P 7060 B Ammonia Dosing Pump | [9 empty] | 50 |  | H | 7196
S-01722 | HS-7213 | U14 | P 7070 A Oxygen Scavenger Dosing Pump | [9 empty] | 50 |  | H | 7213
S-01722 | HS-7216 | U14 | P 7070 B Oxygen Scavenger Dosing Pump | [9 empty] | 50 |  | H | 7216
S-01722 | HSIC-2063 | P09 | Carbon No. HC Feed | [9 empty] | 50 |  | H | 2063
S-01722 | HV-1003 | P01 | Natural Gas from BL | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 243 |  | H | 1003
S-01722 | HV-2003 | P02 | Process Oxygen from BL | 10"-PO-20-110-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 243 |  | H | 2003
S-01722 | HV-2031 | P03 | HP Steam to Process Oxygen Warm-up Vent | 2"-HPS-20-110-F44-H | Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | H | 2031
S-01722 | HV-2076 | P09 | HP Steam to Saturated NG - Start-up | 8"-HPS-20-114-F24-H | High Pressure Steam | 44 | 343 | 52 |  | 410 | bar g | °C | 243 |  | H | 2076
S-01722 | HV-2097 | P10 | HP Steam to Steam/NG Mixture, Vent | 3"-HPS-20-112-F24-H | High Pressure Steam | 42.1 | 343 | 52 |  | 410 | bar g | °C | 243 |  | H | 2097
S-01722 | HV-2098 | P10 | HP Steam to Steam/NG Mixture | 12"-HPS-20-104-F24-H | High Pressure Steam | 42.1 | 343 | 52 |  | 410 | bar g | °C | 243 |  | H | 2098
S-01722 | HV-2225/1 | P13 | False Air Damper | [9 empty] | 243 |  | H | 2225 | 1
S-01722 | HV-2225/2 | P13 | False Air Damper | [9 empty] | 243 |  | H | 2225 | 2
S-01722 | HV-2334 | P16B | Intermittent Blow-Down from E 2020 1 Waste Heat Boiler | 2"-BD-20-101-G24-P | Boiler Blow-down | 103 | 313 | 113 |  | 330 | bar g | °C | 243 |  | H | 2334
S-01722 | HV-2335 | P16B | Intermittent Blow-Down from E 2020 2 Waste Heat Boiler | 2"-BD-20-139-G24-P | Boiler Blow-down | 103 | 313 | 113 |  | 330 | bar g | °C | 243 |  | H | 2335
S-01722 | HV-2371 | P18 | BFW to D 7001 Deaerator | 6"-BFW-20-109-G24-H | Boiler Feed Water | 103 | 276 | 113 |  | 310 | bar g | °C | 243 |  | H | 2371
S-01722 | HV-2385 | P18 | Continuous Blow Down from D 2001 HHP Steam Drum | 2"-CBD-20-102-G24-P | Continuous Blow Down | 103 | 313 | 113 |  | 330 | bar g | °C | 243 |  | H | 2385
S-01722 | HV-2545 | U01 | Nitrogen from Header | 2"-N-20-116-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | H | 2545
S-01722 | HV-3010 | P22 | Synthesis Gas to R 3001 Catalyst Reduction | 3"-SG-30-129-D40-N | Synthesis Gas | 10 | 48 | 29 |  | 100 | bar g | °C | 243 |  | H | 3010
S-01722 | HV-3011 | P22 | Vent inlet C 3001/C 3002 Synthesis Gas Compr./Recirculator | 2"-SG-30-131-D40-ET | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 243 |  | H | 3011
S-01722 | HV-3013 | P22 | Hydrogen from BL for R 3001 Catalyst Reduction | 3"-HG-30-101-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 243 |  | H | 3013
S-01722 | HV-3016 | P22 | Process Air from BL for R 3001 Catalyst Oxidation | 3"-PA-30-101-B24-N | Process Air | 7.5 | 35 | 10.5 |  | 75 | bar g | °C | 243 |  | H | 3016
S-01722 | HV-3054 | P23 | Continuous Blow Down from D 3003 MP Steam Drum | 2"-CBD-30-101-F24-P | Boiler Blow-down | 35 | 242 | 47 |  | 265 | bar g | °C | 243 |  | H | 3054
S-01722 | HV-3087 | P24 | Intermittent Blow-Down from R 3001 1 Methanol Reactor | 2"-CBD-30-107-F24-P | Continuous Blow Down | 33.7 | 242 | 48 |  | 265 | bar g | °C | 243 |  | H | 3087
S-01722 | HV-3090 | P24 | Intermittent Blow-Down from R 3001 2 Methanol Reactor | 2"-CBD-30-105-F24-P | Continuous Blow Down | 33.7 | 242 | 48 |  | 265 | bar g | °C | 243 |  | H | 3090
S-01722 | HV-3093 | P24 | Intermittent Blow-Down from R 3001 3 Methanol Reactor | 2"-CBD-30-103-F24-P | Continuous Blow Down | 33.7 | 242 | 48 |  | 265 | bar g | °C | 243 |  | H | 3093
S-01722 | HV-3166 | P27 | Outlet D 3001 HP Separator, Vent | 4"-SG-30-141-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 243 |  | H | 3166
S-01722 | HV-5338 | P40 | Vent from D 5003 MP Column OH Accumulator | 3"-PMV-50-116-B24-P | Methanol Vapour | 2.6 | 101 | 6 |  | 165 | bar g | °C | 243 |  | H | 5338
S-01722 | HV-6069 | P07 | Bypass of T 6001 Saturator (gas side) | 16"-PRG-60-107-F24-H | Process Gas | 43.3 | 265 | 55 |  | 290 | bar g | °C | 243 |  | H | 6069
S-01722 | LA-8001 | U21 | Flare KO Drum | [9 empty] | 50 |  | L | 8001
S-01722 | LG-1005 | P01 | D 1001 Natural Gas K.O. Drum | D 1001 | Oily Water | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | L | 1005
S-01722 | LG-2017 | P02 | D 2011 Steam Condensate K.O. Drum for E 2008 | D 2011 | High Pressure Steam Condensate | 43.5 | 257 | 52 |  | 290 | bar g | °C | 50 |  | L | 2017
S-01722 | LG-2374 | P18 | D 2001 HHP Steam Drum | D 2001 Bottom | Boiler Water | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | L | 2374
S-01722 | LG-2405 | P19 | D 2002 1st Separator | D 2002 | Process Condensate | 25.8 | 165 | 29 |  | 200 | bar g | °C | 50 |  | L | 2405
S-01722 | LG-2420 | P19 | D 2003 2nd Separator | D 2003 | Process Condensate | 25.3 | 159 | 29 |  | 200 | bar g | °C | 50 |  | L | 2420
S-01722 | LG-2443 | P20 | D 2004 3rd Separator | D 2004 | Process Condensate | 25.6 | 138 | 29 |  | 200 | bar g | °C | 50 |  | L | 2443
S-01722 | LG-2475 | P21 | D 2005 Final Separator | D 2005 | Process Condensate | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | L | 2475
S-01722 | LG-3044 | P23 | D 3003 MP Steam Drum | D 3003 Bottom | Boiler Water | 33.7 | 242 | 45 |  | 290 | bar g | °C | 50 |  | L | 3044
S-01722 | LG-3162 | P27 | D 3001 HP Separator | D 3001 | Crude Methanol | 83.7 | 48 | 99 |  | 100 | bar g | °C | 50 |  | L | 3162
S-01722 | LG-3193 | P28 | D 3002 LP Separator | D 3002 Bottom | Crude Methanol | 4 | 47 | 7 |  | 100 | bar g | °C | 50 |  | L | 3193
S-01722 | LG-5038 | P30 | E 2024 1 Stabilizer Column Reboiler | E 2024 1 | Crude Methanol | 1 | 87 | 5 |  | 160 | bar g | °C | 50 |  | L | 5038
S-01722 | LG-5043 | P30 | T 5001 Stabilizer Column | T 5001 Bottom | Methanol/Water | 1 | 88 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5043
S-01722 | LG-5061 | P31 | E 5001 Stabilizer Column Steam Reboiler | E 5001 | Crude Methanol | 1 | 87 | 5 |  | 160 | bar g | °C | 50 |  | L | 5061
S-01722 | LG-5066 | P30 | E 2024 2 Stabilizer Column Reboiler | E 2024 2 | Crude Methanol | 1 | 87 | 5 |  | 160 | bar g | °C | 50 |  | L | 5066
S-01722 | LG-5072 | P31 | D 5009 Steam Condensate K.O. Drum for E 5001 | D 5009 | Low Pressure Steam Condensate | 2.4 | 138 | 10.5 |  | 190 | bar g | °C | 50 |  | L | 5072
S-01722 | LG-5095 | P32 | D 5001 Stabilizer Column OH Accumulator | D 5001 Bottom | Crude Methanol | 0.6 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5095
S-01722 | LG-5163 | P34 | T 5002 LP Methanol Column | T 5002 Bottom | Crude Methanol | 0.7 | 86 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5163
S-01722 | LG-5183 | P34 | E 5002 4 LP Column Reboiler | E 5002 4 | Crude Methanol | 0.7 | 86 | 5 |  | 160 | bar g | °C | 50 |  | L | 5183
S-01722 | LG-5191 | P35 | E 5002 1 LP Column Reboiler | E 5002 1 | Crude Methanol | 0.7 | 86 | 5 |  | 160 | bar g | °C | 50 |  | L | 5191
S-01722 | LG-5192 | P35 | E 5002 2 LP Column Reboiler | E 5002 2 | Crude Methanol | 0.7 | 86 | 5 |  | 160 | bar g | °C | 50 |  | L | 5192
S-01722 | LG-5193 | P35 | E 5002 3 LP Column Reboiler | E 5002 3 | Crude Methanol | 0.7 | 86 | 5 |  | 160 | bar g | °C | 50 |  | L | 5193
S-01722 | LG-5205 | P36 | D 5002 LP Column OH Accumulator | D 5002 Bottom | Rich Methanol Liquid | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5205
S-01722 | LG-5272 | P38 | T 5003 MP Methanol Column | T 5003 Bottom | Methanol Water | 3.6 | 149 | 6 |  | 175 | bar g | °C | 50 |  | L | 5272
S-01722 | LG-5279 | P38 | E 2023 MP Column Reboiler No. 2 | E 2023 | Rich Methanol Gas Liquid | 3.6 | 149 | 7.5 |  | 175 | bar g | °C | 50 |  | L | 5279
S-01722 | LG-5309 | P39 | E 5003 1 MP Column Reboiler No. 1 | E 5003 1 Shell | Methanol Water | 3.6 | 149 | 7.5 |  | 175 |  | °C | 50 |  | L | 5309
S-01722 | LG-5311 | P39 | E 5003 2 MP Column Reboiler No. 1 | E 5003 2 Shell | Methanol Water | 3.6 | 149 | 7.5 |  | 175 |  | °C | 50 |  | L | 5311
S-01722 | LG-5323 | P40 | D 5003 MP Cooling OH Accumulator | D 5003 | Methanol | 2.7 | 101 | 6 |  | 165 | bar g | °C | 50 |  | L | 5323
S-01722 | LG-5502 | U23B | D 5010 Excess Water Drum (optional) | D 5010 | Methanol Water | 0 | 43 | 3.5 |  | 100 | bar g | °C | 50 |  | L | 5502
S-01722 | LG-6023/1 | P06 | T 6001 1 Saturator | T 6001 1 Bottom | Process Condensate | 42.8 | 226 | 55 |  | 300 | bar g | °C | 50 |  | L | 6023 | 1
S-01722 | LG-6023/2 | P06 | T 6001 2 Saturator | T 6001 2 Bottom | Process Condensate | 42.8 | 226 | 55 |  | 300 | bar g | °C | 50 |  | L | 6023 | 2
S-01722 | LG-6052 | P07 | D 6001 Feed Gas Separator | D 6001 | Process Condensate | 49 | 226 | 55 |  | 290 | bar g | °C | 50 |  | L | 6052
S-01722 | LG-6084 | P08 | D 6002 Saturator Blow Down Drum | D 6002 | Boiler Blow-down | 0 | 100 | 3.5 |  | 125 | bar g | °C | 50 |  | L | 6084
S-01722 | LG-7092 | U09 | D 7001 Deaerator | D 7001 | Boiler Water | 1 | 120 | 3.5 |  | 200 | bar g | °C | 50 |  | L | 7092
S-01722 | LG-7252 | U16 | D 7002 Continuous Blow Down Drum | D 7002 | Boiler Blow-down | 7.5 | 173 | 9.5 |  | 340 | bar g | °C | 50 |  | L | 7252
S-01722 | LG-7255 | U16 | D 7003 Intermittent Blow-Down Drum No. 1 | D 7003 | Boiler Blow-down | 102 | 313 |  |  |  | bar g | °C | 50 |  | L | 7255
S-01722 | LG-7257 | U16 | D 7004 Intermittent Blow-Down Drum No. 2 | D 7004 | Boiler Blow-down | 40.8 | 253 |  |  |  | bar g | °C | 50 |  | L | 7257
S-01722 | LI-1004 | P01 | D 1001 Natural Gas K.O. Drum | D 1001 | Oily Water | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | L | 1004
S-01722 | LI-2373 | P18 | D 2001 HHP Steam Drum | D 2001 Bottom | Boiler Water | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | L | 2373
S-01722 | LI-2404 | P19 | D 2002 1st Separator | D 2002 | Process Condensate | 25.8 | 165 | 29 |  | 200 | bar g | °C | 50 |  | L | 2404
S-01722 | LI-2442 | P20 | D 2004 3rd Separator | D 2004 | Process Condensate | 25.6 | 138 | 29 |  | 200 | bar g | °C | 50 |  | L | 2442
S-01722 | LI-3043 | P23 | D 3003 MP Steam Drum | D 3003 Bottom | Boiler Water | 33.7 | 242 | 45 |  | 290 | bar g | °C | 50 |  | L | 3043
S-01722 | LI-5001 | P29 | TK 5001 Raw Methanol Buffer Tank | TK 5001 | Raw Methanol | 0 | 46 | -0.3 |  | 100 | mbar g | °C | 50 |  | L | 5001
S-01722 | LI-5002 | P29 | TK 5001 Raw Methanol Buffer Tank | TK 5001 | Raw Methanol | 0 | 46 | -0.3 |  | 100 | mbar g | °C | 50 |  | L | 5002
S-01722 | LI-5042 | P30 | T 5001 Stabilizer Column | T 5001 Bottom | Methanol/Water | 1 | 88 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5042
S-01722 | LI-5065 | P30 | E 2024 2 Stabilizer Column Reboiler | E 2024 2 | Crude Methanol | 1 | 87 | 5 |  | 160 | bar g | °C | 50 |  | L | 5065
S-01722 | LI-5071 | P31 | D 5009 Steam Condensate K.O. Drum for E 5001 | D 5009 | Low Pressure Steam Condensate | 2.4 | 138 | 10.5 |  | 190 | bar g | °C | 50 |  | L | 5071
S-01722 | LI-5094 | P32 | D 5001 Stabilizer Column OH Accumulator | D 5001 Bottom | Crude Methanol | 0.6 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5094
S-01722 | LI-5162 | P34 | T 5002 LP Methanol Column | T 5002 Bottom | Crude Methanol | 0.7 | 86 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5162
S-01722 | LI-5182 | P34 | E 5002 4 LP Column Reboiler | E 5002 4 | Crude Methanol | 0.7 | 86 | 5 |  | 160 | bar g | °C | 50 |  | L | 5182
S-01722 | LI-5204 | P36 | D 5002 LP Column OH Accumulator | D 5002 Bottom | Rich Methanol Liquid | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5204
S-01722 | LI-5232 | U15 | TK 5080 Morpholine Tank | TK 5080 | [6 empty] | bar g | °C | 50 |  | L | 5232
S-01722 | LI-5271 | P38 | T 5003 MP Methanol Column | T 5003 Bottom | Methanol Water | 3.6 | 149 | 6 |  | 175 | bar g | °C | 50 |  | L | 5271
S-01722 | LI-5278 | P39 | E 5003 2 MP Column Reboiler No. 1 | E 5003 2 Shell | Methanol Water | 3.6 | 149 | 7.5 |  | 175 |  | °C | 50 |  | L | 5278
S-01722 | LI-5308 | P39 | E 5003 1 MP Column Reboiler No. 1 | E 5003 1 Tube | Low Pressure Steam Condensate | 6.5 | 188 | 9.5 |  | 340 | bar g | °C | 50 |  | L | 5308
S-01722 | LI-5310 | P39 | E 5003 2 MP Column Reboiler No. 1 | E 5003 2 Tube | Low Pressure Steam Condensate | 6.5 | 188 | 9.5 |  | 175 | bar g | °C | 50 |  | L | 5310
S-01722 | LI-5322 | P40 | D 5003 MP Cooling OH Accumulator | D 5003 | Methanol | 2.7 | 101 | 6 |  | 165 | bar g | °C | 50 |  | L | 5322
S-01722 | LI-5396 | P43 | TK 5002 1 Methanol Product Buffer Tank | TK 5002 1 | Methanol Product | 0 | 48 | -0.03 |  | 85 | bar g | °C | 50 |  | L | 5396
S-01722 | LI-5397 | P43 | TK 5002 1 Methanol Product Buffer Tank | TK 5002 1 | Methanol Product | 0 | 48 | -0.03 |  | 85 | bar g | °C | 50 |  | L | 5397
S-01722 | LI-5413 | P44 | TK 5002 2 Methanol Product Buffer Tank | TK 5002 2 | Methanol Product | 0 | 48 | -0.3 |  | 85 | bar g | °C | 50 |  | L | 5413
S-01722 | LI-5414 | P44 | TK 5002 2 Methanol Product Buffer Tank | TK 5002 2 | Methanol Product | 0 | 48 | -0.3 |  | 85 | bar g | °C | 50 |  | L | 5414
S-01722 | LI-5446 | P45 | TK 5003 Liquid Off-stream Tank | TK 5003 | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 100 | bar g | °C | 50 |  | L | 5446
S-01722 | LI-5447 | P45 | TK 5003 Liquid Off-stream Tank | TK 5003 | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 100 | bar g | °C | 50 |  | L | 5447
S-01722 | LI-5511 | U24 | TK 5050 NaOH Tank (optional) | TK 5050 | NaOH Solution | [6 empty] | °C | 50 |  | L | 5511
S-01722 | LI-6022/1 | P06 | T 6001 1 Saturator | T 6001 1 Bottom | Process Condensate | 42.8 | 226 | 55 |  | 300 | bar g | °C | 50 |  | L | 6022 | 1
S-01722 | LI-6022/2 | P06 | T 6001 2 Saturator | T 6001 2 Bottom | Process Condensate | 42.8 | 226 | 55 |  | 300 | bar g | °C | 50 |  | L | 6022 | 2
S-01722 | LI-6033/1 | P06 | T 6001 1 Saturator | T 6001 1 Top | Process Water | 42.8 | 168 | 45 |  | 300 | bar g | °C | 50 |  | L | 6033 | 1
S-01722 | LI-6033/2 | P06 | T 6001 2 Saturator | T 6001 2 Top | Process Water | 42.8 | 168 | 45 |  | 300 | bar g | °C | 50 |  | L | 6033 | 2
S-01722 | LI-6034/1 | P06 | T 6001 1 Saturator | T 6001 1 Top | Process Water | 42.8 | 168 | 45 |  | 300 | bar g | °C | 50 |  | L | 6034 | 1
S-01722 | LI-6034/2 | P06 | T 6001 2 Saturator | T 6001 2 Top | Process Water | 42.8 | 168 | 45 |  | 300 | bar g | °C | 50 |  | L | 6034 | 2
S-01722 | LI-6083 | P08 | D 6002 Saturator Blow Down Drum | D 6002 | Boiler Blow-down | 0 | 100 | 3.5 |  | 125 | bar g | °C | 50 |  | L | 6083
S-01722 | LI-7001 | U18 | TK 7001 1 Demineralized Water Tank | TK 7001 1 | Demineralized Water | Atmospheric | 35 |  |  | 85 | bar g | °C | 50 |  | L | 7001
S-01722 | LI-7002 | U18 | TK 7001 2 Demineralized Water Tank | TK 7001 2 | Demineralized Water | Atmospheric | 35 |  |  | 85 | bar g | °C | 50 |  | L | 7002
S-01722 | LI-7060 | U18 | TK 7001 1 Demineralized Water Tank | TK 7001 1 | Demineralized Water | Atmospheric | 35 |  |  | 85 | bar g | °C | 50 |  | L | 7060
S-01722 | LI-7061 | U18 | TK 7001 2 Demineralized Water Tank | TK 7001 2 | Demineralized Water | Atmospheric | 35 |  |  | 85 | bar g | °C | 50 |  | L | 7061
S-01722 | LI-7101 | U22 | TK 7002 Process Condensate Tank | TK 7002 | Process Condensate | Atmospheric | 65 | Atmospheric |  | 100 | bar g | °C | 50 |  | L | 7101
S-01722 | LI-7102 | U22 | TK 7002 Process Condensate Tank | TK 7002 | Process Condensate | Atmospheric | 65 | Atmospheric |  | 100 | bar g | °C | 50 |  | L | 7102
S-01722 | LI-7162 | U12 | TK 7050 Phosphate Solution Tank | TK 7050 | [6 empty] | bar g | °C | 50 |  | L | 7162
S-01722 | LI-7192 | U13 | TK 7060 Ammonia Tank | TK 7060 | Ammonia | [5 empty] | bar g | °C | 50 |  | L | 7192
S-01722 | LI-7212 | U14 | TK 7070 Oxygen Scavenger Tank | TK 7070 | [6 empty] | bar g | °C | 50 |  | L | 7212
S-01722 | LIC-2016 | P02 | D 2011 Steam Condensate K.O. Drum for E 2008 | D 2011 | High Pressure Steam Condensate | 43.5 | 257 | 52 |  | 290 | bar g | °C | 50 |  | L | 2016
S-01722 | LIC-2372 | P18 | D 2001 HHP Steam Drum | D 2001 Bottom | Boiler Water | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | L | 2372
S-01722 | LIC-2403 | P19 | D 2002 1st Separator | D 2002 | Process Condensate | 25.8 | 165 | 29 |  | 200 | bar g | °C | 50 |  | L | 2403
S-01722 | LIC-2419 | P19 | D 2003 2nd Separator | D 2003 | Process Condensate | 25.3 | 159 | 29 |  | 200 | bar g | °C | 50 |  | L | 2419
S-01722 | LIC-2441 | P20 | D 2004 3rd Separator | D 2004 | Process Condensate | 25.6 | 138 | 29 |  | 200 | bar g | °C | 50 |  | L | 2441
S-01722 | LIC-2474 | P21 | D 2005 Final Separator | D 2005 | Process Condensate | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | L | 2474
S-01722 | LIC-3042 | P23 | D 3003 MP Steam Drum | D 3003 Bottom | Boiler Water | 33.7 | 242 | 45 |  | 290 | bar g | °C | 50 |  | L | 3042
S-01722 | LIC-3161 | P27 | D 3001 HP Separator | D 3001 | Crude Methanol | 83.7 | 48 | 99 |  | 100 | bar g | °C | 50 |  | L | 3161
S-01722 | LIC-3192 | P28 | D 3002 LP Separator | D 3002 Bottom | Crude Methanol | 4 | 47 | 7 |  | 100 | bar g | °C | 50 |  | L | 3192
S-01722 | LIC-5041 | P30 | T 5001 Stabilizer Column | T 5001 Bottom | Methanol/Water | 1 | 88 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5041
S-01722 | LIC-5070 | P31 | D 5009 Steam Condensate K.O. Drum for E 5001 | D 5009 | Low Pressure Steam Condensate | 2.4 | 138 | 10.5 |  | 190 | bar g | °C | 50 |  | L | 5070
S-01722 | LIC-5093 | P32 | D 5001 Stabilizer Column OH Accumulator | D 5001 Bottom | Crude Methanol | 0.6 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5093
S-01722 | LIC-5161 | P34 | T 5002 LP Methanol Column | T 5002 Bottom | Crude Methanol | 0.7 | 86 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5161
S-01722 | LIC-5203 | P36 | D 5002 LP Column OH Accumulator | D 5002 Bottom | Rich Methanol Liquid | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | L | 5203
S-01722 | LIC-5270 | P38 | T 5003 MP Methanol Column | T 5003 Bottom | Methanol Water | 3.6 | 149 | 6 |  | 175 | bar g | °C | 50 |  | L | 5270
S-01722 | LIC-5321 | P40 | D 5003 MP Cooling OH Accumulator | D 5003 | Methanol | 2.7 | 101 | 6 |  | 165 | bar g | °C | 50 |  | L | 5321
S-01722 | LIC-5501 | U23B | D 5010 Excess Water Drum (optional) | D 5010 | Methanol Water | 0 | 43 | 3.5 |  | 100 | bar g | °C | 50 |  | L | 5501
S-01722 | LIC-6021 | P06 | T 6001 1 Saturator | T 6001 1 Bottom | Process Condensate | 42.8 | 226 | 55 |  | 300 | bar g | °C | 50 |  | L | 6021
S-01722 | LIC-6051 | P07 | D 6001 Feed Gas Separator | D 6001 | Process Condensate | 49 | 226 | 55 |  | 290 | bar g | °C | 50 |  | L | 6051
S-01722 | LIC-6082 | P08 | D 6002 Saturator Blow Down Drum | D 6002 | Boiler Blow-down | 0 | 100 | 3.5 |  | 125 | bar g | °C | 50 |  | L | 6082
S-01722 | LIC-7091 | U09 | D 7001 Deaerator | D 7001 | Boiler Water | 1 | 120 | 3.5 |  | 200 | bar g | °C | 50 |  | L | 7091
S-01722 | LIC-7251 | U16 | D 7002 Continuous Blow Down Drum | D 7002 | Boiler Blow-down | 7.5 | 173 | 9.5 |  | 340 | bar g | °C | 50 |  | L | 7251
S-01722 | LV-2016 | P02 | Outlet D 2011 Steam Condensate K.O. Drum for E 2008 | 6"-HPC-20-102-F24-H | High Pressure Steam Condensate | 43.5 | 257 | 53 |  | 290 | bar g | °C | 243 |  | L | 2016
S-01722 | LV-2372 | P19 | BFW from Header to D 2001 HHP Steam Drum (start-up) | 6"-BFW-20-106-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | L | 2372
S-01722 | LV-2403 | P19 | Outlet P 2001 A/B Process Condensate Pump No. 1 | 3"-PRC-20-114-G40-H | Process Condensate | 55 | 165 | 71 |  | 200 | bar g | °C | 243 |  | L | 2403
S-01722 | LV-2419 | P19 | Outlet D 2003 2nd Separator | 4"-PRC-20-123-F40-H | Process Condensate | 26 | 159 | 30 |  | 200 | bar g | °C | 243 |  | L | 2419
S-01722 | LV-2441 | P20 | Outlet P 2002 A/B Process Condensate Pump No. 2 | 6"-PRC-20-118-G40-H | Process Condensate | 53 | 138 | 71 |  | 200 | bar g | °C | 243 |  | L | 2441
S-01722 | LV-2474 | P21 | Outlet P 2003 A/B Process Condensate Pump No. 3 | 4"-PRC-20-104-G40-N | Process Condensate | 53 | 49 | 80 |  | 100 | bar g | °C | 243 |  | L | 2474
S-01722 | LV-3161/A | P27 | Outlet D 3001 HP Separator | 10"-PMC-30-101-G40-N | Crude Methanol | 76.2 | 48 | 100 |  | 100 | bar g | °C | 243 |  | L | 3161 | A
S-01722 | LV-3161/B | P27 | Outlet D 3001 HP Separator | 10"-PMC-30-103-G40-N | Crude Methanol | 76.2 | 48 | 100 |  | 100 | bar g | °C | 243 |  | L | 3161 | B
S-01722 | LV-3192 | P28 | Outlet D 3002 LP Separator | 10"-PMC-30-108-B40-N | Crude Methanol | 4 | 48 | 8 |  | 100 | bar g | °C | 243 |  | L | 3192
S-01722 | LV-5070 | P31 | Outlet P 5011 A/B Steam Condensate Pump | 4"-LPC-50-108-D24-H | Low Pressure Steam Condensate | 5.7 | 138 | 18 |  | 190 | bar g | °C | 243 |  | L | 5070
S-01722 | LV-5501 | U23B | Outlet P 5010 A/B Excess Water Pump (optional) | 3"-PMW-50-149-F24-N | Methanol Water | 50 | 43 | 82 |  | 100 | bar g | °C | 243 |  | L | 5501
S-01722 | LV-6021/A | P05 | Outlet P 6002 A/B Steam Condensate Return Pump | 10"-MPC-60-106-F24-H | Medium Pressure Steam Condensate | 45 | 241 | 73 |  | 260 | bar g | °C | 243 |  | L | 6021 | A
S-01722 | LV-6021/B | P05 | MP Steam Condensate to D 7001 Deaerator | 18"-MPC-60-104-F24-H | Medium Pressure Steam Condensate | 32.5 | 240 | 47 |  | 260 | bar g | °C | 243 |  | L | 6021 | B
S-01722 | LV-6082 | P08 | Outlet P 7003 A&B Excess Process Condensate Pumps | 4"-BD-60-111-B40-N | Process Condensate | 1.5 | 65 | 9 |  | 125 | bar g | °C | 243 |  | L | 6082
S-01722 | LV-7251 | U16 | Outlet D 7002 Continuous Blow Down Drum | 3"-BD-70-111-B24-N | Boiler Blow-down | 8 | 173 | 10.5 |  | 200 | bar g | °C | 243 |  | L | 7251
S-01722 | ML-2124 | P11 | F 2002 Combustion Air Blower | [9 empty] | 50 |  | M | 2124
S-01722 | ML-2159 | P12 | F 2001 Flue Gas Blower | [9 empty] | 50 |  | M | 2159
S-01722 | ML-2410 | P19 | P 2001 A Process Condensate Pump No. 1 | [9 empty] | 50 |  | M | 2410
S-01722 | ML-2414 | P19 | P 2001 B Process Condensate Pump No. 1 | [9 empty] | 50 |  | M | 2414
S-01722 | ML-2447 | P20 | P 2002 A Process Condensate Pump No. 2 | [9 empty] | 50 |  | M | 2447
S-01722 | ML-2451 | P20 | P 2002 B Process Condensate Pump No. 2 | [9 empty] | 50 |  | M | 2451
S-01722 | ML-2471 | P21 | AE 2026 Air Cooler | [9 empty] | 50 |  | M | 2471
S-01722 | ML-2487 | P21 | P 2003 A Process Condensate Pump No. 3 | [9 empty] | 50 |  | M | 2487
S-01722 | ML-2491 | P21 | P 2003 B Process Condensate Pump No. 3 | [9 empty] | 50 |  | M | 2491
S-01722 | ML-2577 | U02 | C 2001 Start-up Nitrogen Compressor | [9 empty] | 50 |  | M | 2577
S-01722 | ML-3141 | P26 | AE 3002 1 Loop Air Cooler | [9 empty] | 50 |  | M | 3141
S-01722 | ML-3144 | P26 | AE 3002 2 Loop Air Cooler | [9 empty] | 50 |  | M | 3144
S-01722 | ML-3147 | P26 | AE 3002 3 Loop Air Cooler | [9 empty] | 50 |  | M | 3147
S-01722 | ML-5013 | P29 | P 5001 A Raw Methanol Pump | [9 empty] | 50 |  | M | 5013
S-01722 | ML-5017 | P29 | P 5001 B Raw Methanol Pump | [9 empty] | 50 |  | M | 5017
S-01722 | ML-5077 | P31 | P 5011 A Steam Condensate Pump | [9 empty] | 50 |  | M | 5077
S-01722 | ML-5081 | P31 | P 5011 B Steam Condensate Pump | [9 empty] | 50 |  | M | 5081
S-01722 | ML-5092 | P32 | AE 5004 Stabilizer Column OH Condenser | [9 empty] | 50 |  | M | 5092
S-01722 | ML-5101 | P32 | P 5003 A Stabilizer Column Reflux Pump | [9 empty] | 50 |  | M | 5101
S-01722 | ML-5105 | P32 | P 5003 B Stabilizer Column Reflux Pump | [9 empty] | 50 |  | M | 5105
S-01722 | ML-5133 | P33 | P 5002 A Stabilizer Methanol Pump | [9 empty] | 50 |  | M | 5133
S-01722 | ML-5137 | P33 | P 5002 B Stabilizer Methanol Pump | [9 empty] | 50 |  | M | 5137
S-01722 | ML-5201 | P36 | AE 5005 LP Column OH Condenser | [9 empty] | 50 |  | M | 5201
S-01722 | ML-5212 | P36 | P 5004 A LP Column Reflux Pump | [9 empty] | 50 |  | M | 5212
S-01722 | ML-5216 | P36 | P 5004 B LP Column Reflux Pump | [9 empty] | 50 |  | M | 5216
S-01722 | ML-5231 | U15 | TK 5080 Morpholine Tank | [9 empty] | 50 |  | M | 5231
S-01722 | ML-5232 | U15 | P 5080 A Morpholine Dosing Pump | [9 empty] | 50 |  | M | 5232
S-01722 | ML-5233 | P37 | P 5005 A MP Column Feed Pump | [9 empty] | 50 |  | M | 5233
S-01722 | ML-5236 | U15 | P 5080 B Morpholine Dosing Pump | [9 empty] | 50 |  | M | 5236
S-01722 | ML-5237 | P37 | P 5005 B MP Column Feed Pump | [9 empty] | 50 |  | M | 5237
S-01722 | ML-5329 | P40 | P 5006 A MP Column Reflux Pump | [9 empty] | 50 |  | M | 5329
S-01722 | ML-5333 | P40 | P 5006 B MP Column Reflux Pump | [9 empty] | 50 |  | M | 5333
S-01722 | ML-5353 | P41 | P 5007 A MP Column Recycle Pump | [9 empty] | 50 |  | M | 5353
S-01722 | ML-5357 | P41 | P 5007 B MP Column Recycle Pump | [9 empty] | 50 |  | M | 5357
S-01722 | ML-5361 | P41 | P 5010 A Excess Water Pump | [9 empty] | 50 |  | M | 5361
S-01722 | ML-5365 | P41 | P 5010 B Excess Water Pump | [9 empty] | 50 |  | M | 5365
S-01722 | ML-5368 | P41 | AE 5006 Wash Water Air Cooler | [9 empty] | 50 |  | M | 5368
S-01722 | ML-5404 | P43 | P 5012 Methanol Start-up Pump | [9 empty] | 50 |  | M | 5404
S-01722 | ML-5425 | P44 | P 5008 A Methanol Product Pump | [9 empty] | 50 |  | M | 5425
S-01722 | ML-5429 | P44 | P 5008 B Methanol Product Pump | [9 empty] | 50 |  | M | 5429
S-01722 | ML-5455 | P45 | P 5009 A Liquid Off-stream Pump | [9 empty] | 50 |  | M | 5455
S-01722 | ML-5459 | P45 | P 5009 B Liquid Off-stream Pump | [9 empty] | 50 |  | M | 5459
S-01722 | ML-5511 | U24 | P 5070 A NaOH Solution Dosing Pump (optional) | [9 empty] | 50 |  | M | 5511
S-01722 | ML-5512 | U24 | P 5070 B NaOH Solution Dosing Pump (optional) | [9 empty] | 50 |  | M | 5512
S-01722 | ML-5513 | U24 | TK 5050 NaOH Tank, Stirrer (optional) | [9 empty] | 50 |  | M | 5513
S-01722 | ML-6004 | P05 | P 6002 A Steam Condensate Return Pump | [9 empty] | 50 |  | M | 6004
S-01722 | ML-6008 | P05 | P 6002 B Steam Condensate Return Pump | [9 empty] | 50 |  | M | 6008
S-01722 | ML-6062 | P07 | P 6001 A Saturator Circulation Pump | [9 empty] | 50 |  | M | 6062
S-01722 | ML-6066 | P07 | P 6001 B Saturator Circulation Pump | [9 empty] | 50 |  | M | 6066
S-01722 | ML-6081 | P08 | P 7003 A Excess Process Condensate Pump | [9 empty] | 50 |  | M | 6081
S-01722 | ML-6086 | P08 | P 7003 B Excess Process Condensate Pump | [9 empty] | 50 |  | M | 6086
S-01722 | ML-7005 | U18 | P 7002 A Demineralized Water Pump | [9 empty] | 50 |  | M | 7005
S-01722 | ML-7006 | U18 | P 7002 B Demineralized Water Pump | [9 empty] | 50 |  | M | 7006
S-01722 | ML-7101 | U22 | P 7004 A Excess Process Condensate Pump | [9 empty] | 50 |  | M | 7101
S-01722 | ML-7103 | U22 | P 7004 B Excess Process Condensate Pump | [9 empty] | 50 |  | M | 7103
S-01722 | ML-7122 | U10 | P 7001 C BFW Pump | [9 empty] | 50 |  | M | 7122
S-01722 | ML-7161 | U12 | TK 7050 Phosphate Solution Tank | [9 empty] | 50 |  | M | 7161
S-01722 | ML-7163 | U12 | P 7051 A Phosphate Dosing Pump | [9 empty] | 50 |  | M | 7163
S-01722 | ML-7166 | U12 | P 7051 B Phosphate Dosing Pump | [9 empty] | 50 |  | M | 7166
S-01722 | ML-7169 | U12 | P 7052 A Phosphate Dosing Pump | [9 empty] | 50 |  | M | 7169
S-01722 | ML-7172 | U12 | P 7052 B Phosphate Dosing Pump | [9 empty] | 50 |  | M | 7172
S-01722 | ML-7191 | U13 | TK 7060 Ammonia Tank | [9 empty] | 50 |  | M | 7191
S-01722 | ML-7193 | U13 | P 7060 A Ammonia Dosing Pump | [9 empty] | 50 |  | M | 7193
S-01722 | ML-7196 | U13 | P 7060 B Ammonia Dosing Pump | [9 empty] | 50 |  | M | 7196
S-01722 | ML-7211 | U14 | TK 7070 Oxygen Scavenger Tank | [9 empty] | 50 |  | M | 7211
S-01722 | ML-7213 | U14 | P 7070 A Oxygen Scavenger Dosing Pump | [9 empty] | 50 |  | M | 7213
S-01722 | ML-7216 | U14 | P 7070 B Oxygen Scavenger Dosing Pump | [9 empty] | 50 |  | M | 7216
S-01722 | PCV-2551 | U01 | Fuel Gas for Burner Tightness Test | 2"NG-20-113-B24-N | Fuel Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 243 |  | P | 2551
S-01722 | PCV-3008 | P22 | Synthesis Gas to R 3001 Catalyst Reduction | 3"-SG-30-129-D40-N | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 243 |  | P | 3008
S-01722 | PCV-5009 | P29 | Nitrogen for blanketing of TK 5001 | 2"-N-50-101-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | P | 5009
S-01722 | PCV-5395 | P43 | Nitrogen for blanketing of TK 5002 1 | 2"-N-50-113-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | P | 5395
S-01722 | PCV-5412 | P44 | Nitrogen for blanketing of TK 5002 2 | 2"-N-50-108-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | P | 5412
S-01722 | PCV-5445 | P45 | Nitrogen for blanketing of TK 5003 | 2"-N-50-111-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | P | 5445
S-01722 | PDI-1032 | P04 | Across R 1001 Hydrogenator | 16"-PRG-20-101-F24-H | Process Gas | 48.8 | 380 | 55 |  | 410 | bar g | °C | 50 |  | P | 1032
S-01722 | PDI-2004 | P02 | Across X 2001 A/B Oxygen Filter | 10"-PO-20-110-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | P | 2004
S-01722 | PDI-2032 | P03 | Across X 2002 A/B Steam Filter | 4"-HPS-70-103-F34-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2032
S-01722 | PDI-2036 | P03 | Across valves outlet X 2002 A/B Steam Filter | 4"-HPS-20-106-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2036
S-01722 | PDI-2051 | P03 | Across Mixing Point | 16"-PO-20-114-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 50 |  | P | 2051
S-01722 | PDI-2252 | P14 | Across R 2003 Prereformer | 30"-PRG-20-113-G36-H | Process Gas | 38.4 | 496 | 46 |  | 550 | bar g | °C | 50 |  | P | 2252
S-01722 | PDI-2283 | P15 | Across H 2001 Primary Reformer | 34"-RFG-20-114-H44-H | Process Gas | 36.3 | 638 | 46 |  | 675 | bar g | °C | 50 |  | P | 2283
S-01722 | PDI-2320 | P16A | Across Top of R 2004 Secondary Reformer (Oxygen) | R 2004 | Process Gas | 31.4 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | P | 2320
S-01722 | PDI-2321 | P16A | Across R 2004 Secondary Reformer (Natural Gas) | Cold Collector | Reformed Gas | 32 | 742 | 34.7 |  | 800 | bar g | °C | 50 |  | P | 2321
S-01722 | PDI-2323 | P16A | R 2004 Secondary Reformer (Catalyst) | R 2004 | Process Gas | 31.4 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | P | 2323
S-01722 | PDI-2574 | U02 | Across Strainer Inlet C 2001 Startup Nitrogen Compressor | 10"-N-20-110-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | P | 2574
S-01722 | PDI-3024 | P22 | Outlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 32"-SG-30-103-G40-N | Synthesis Gas | 80 | 74 | 99 |  | 120 | bar g | °C | 50 |  | P | 3024
S-01722 | PDI-3112 | P25 | Across E 3001 1 Feed/Effluent Exchanger | 24"-SG-30-135-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | P | 3112
S-01722 | PDI-3115 | P25 | Across E 3001 2 Feed/Effluent Exchanger | 24"-SG-30-107-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | P | 3115
S-01722 | PDI-3117 | P25 | Across E 3001 3 Feed/Effluent Exchanger | 24"-SG-30-119-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | P | 3117
S-01722 | PDI-5048 | P30 | T 5001 Stabilizer Column (Bottom) | [9 empty] | 50 |  | P | 5048
S-01722 | PDI-5050 | P30 | T 5001 Stabilizer Column (Top) | [9 empty] | 50 |  | P | 5050
S-01722 | PDI-5167 | P34 | T 5002 LP Methanol Column | [9 empty] | 50 |  | P | 5167
S-01722 | PDI-5169 | P34 | T 5002 LP Methanol Column | [9 empty] | 50 |  | P | 5169
S-01722 | PDI-5171 | P34 | T 5002 LP Methanol Column | [9 empty] | 50 |  | P | 5171
S-01722 | PDI-5173 | P34 | T 5002 LP Methanol Column | [9 empty] | 50 |  | P | 5173
S-01722 | PDI-5253 | P38 | T 5003 MP Methanol Column | [9 empty] | 50 |  | P | 5253
S-01722 | PDI-5255 | P38 | T 5003 MP Methanol Column | [9 empty] | 50 |  | P | 5255
S-01722 | PDI-5257 | P38 | T 5003 MP Methanol Column | [9 empty] | 50 |  | P | 5257
S-01722 | PDI-5259 | P38 | T 5003 MP Methanol Column | [9 empty] | 50 |  | P | 5259
S-01722 | PDI-5385 | P42 | Outlet X 5001 Product Polisher Unit | 10"-PMP-50-143-D24-N | Methanol Product | 3 | 48 | 19 |  | 75 | bar g | °C | 50 |  | P | 5385
S-01722 | PDI-6026 | P06 | Across T 6001 Saturator | 12"-PRC-60-101-G40-H | Process Condensate | 44 | 225 | 57 |  | 280 | bar g | °C | 50 |  | P | 6026
S-01722 | PDI-6028 | P06 | Across X 6001 A/B Particle Filter | 3"-PRC-20-107-G40-H | Process Condensate | 45 | 115 | 71 |  | 180 | bar g | °C | 50 |  | P | 6028
S-01722 | PDIC-2417 | P19 | Differential pressure across FV 2417 BFW to D 2001 | 12"-BFW-70-107-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | P | 2417
S-01722 | PDIC-2575 | U02 | Across C 2001 Start-up Nitrogen Compressor | 10"-N-20-104-B24-P | Nitrogen Gas | 8 | 84 | 10.5 |  | 110 | bar g | °C | 50 |  | P | 2575
S-01722 | PDV-2575 | U02 | Nitrogen Recycle to E 2027 | 8"-N-20-105-B24-P | Nitrogen Gas | 6 | 70 | 10.5 |  | 110 | bar g | °C | 243 |  | P | 2575
S-01722 | PG-1002 | P01 | Inlet D 1001 Natural Gas K.O. Drum | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | P | 1002
S-01722 | PG-1007 | P01 | Outlet D 1001 Natural Gas K.O. Drum | 14"-NG-10-103-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 50 |  | P | 1007
S-01722 | PG-1033 | P04 | Inlet R 1001 Hydrogenator | 16"-PRG-20-101-F24-H | Process Gas | 48.8 | 380 | 55 |  | 410 | bar g | °C | 50 |  | P | 1033
S-01722 | PG-1036 | P04 | Outlet R 1001 Hydrogenator | 16"-PRG-10-101-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | P | 1036
S-01722 | PG-1040 | P04 | Outlet R 1002 1 Sulphur Absorber | 16"-PRG-10-105-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | P | 1040
S-01722 | PG-1046 | P04 | Outlet R 1002 2 Sulphur Absorber | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 50 |  | P | 1046
S-01722 | PG-1048 | P04 | Nitrogen from BL | 1½"-N-10-103-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 70 | bar g | °C | 50 |  | P | 1048
S-01722 | PG-2002 | P02 | Process Oxygen from BL | 10"-PO-20-110-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | P | 2002
S-01722 | PG-2005 | P02 | Outlet X 2001 A Oxygen Filter | 10"-PO-20-107-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | P | 2005
S-01722 | PG-2006 | P02 | Outlet X 2001 B Oxygen Filter | 10"-PO-20-107-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | P | 2006
S-01722 | PG-2018 | P02 | D 2011 Steam Condensate K.O. Drum for E 2008 | 2"-HPC-20-104-F24-P | High Pressure Steam Condensate | 43.5 | 257 | 52 |  | 290 | bar g | °C | 50 |  | P | 2018
S-01722 | PG-2031 | P03 | HP Steam from Header | 4"-HPS-70-103-F34-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2031
S-01722 | PG-2033 | P03 | Outlet X 2002 A Steam Filter | 4"-HPS-20-106-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2033
S-01722 | PG-2034 | P03 | Outlet X 2002 B Steam Filter | 4"-HPS-20-107-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 470 | bar g | °C | 50 |  | P | 2034
S-01722 | PG-2075 | P09 | HP Steam from Header | 12"-HPS-70-125-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2075
S-01722 | PG-2096 | P10 | HP Steam to Steam/NG Mixture | 12"-HPS-20-104-F24-H | High Pressure Steam | 42.1 | 343 | 52 |  | 410 | bar g | °C | 50 |  | P | 2096
S-01722 | PG-2100 | P10 | Nitrogen from Header | 4"-N-20-112-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | P | 2100
S-01722 | PG-2101 | P10 | Nitrogen from Header | 4"-N-20-113-F24-N | Nitrogen Gas | 6 | 40 | 46 |  | 290 | bar g | °C | 50 |  | P | 2101
S-01722 | PG-2116 | P11 | HP Steam to FT 2002 Steam Turbine for F 2002 | 8"-HPS-70-101-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2116
S-01722 | PG-2120 | P11 | LP Steam from FT 2002 Steam Turbine for F 2002 | 16"-LPS-20-102-D24-H | Low Pressure Steam | 7.5 | 194 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 2120
S-01722 | PG-2164 | P12 | HP Steam to FT 2001 Steam Turbine for F 2001 | 6"-HPS-70-111-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2164
S-01722 | PG-2170 | P12 | LP Steam from FT 2001 Steam Turbine for F 2001 | 12"-LPS-20-106-D24-H | Low Pressure Steam | 7.5 | 204 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 2170
S-01722 | PG-2230 | P13 | Process Condensate from P 2003 A/B | 3"-PRC-20-130-G40-N | Process Condensate | 53 | 49 | 80 |  | 100 | bar g | °C | 50 |  | P | 2230
S-01722 | PG-2231 | P13 | HP BFW from Header | 3"-BFW-70-103-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 50 |  | P | 2231
S-01722 | PG-2251 | P14 | Inlet R 2003 Prereformer | 30"-PRG-20-113-G36-H | Process Gas | 38.4 | 496 | 46 |  | 550 | bar g | °C | 50 |  | P | 2251
S-01722 | PG-2267 | P14 | Outlet R 2003 Prereformer | 30"-RFG-20-101-F34-H | Reformed Gas | 37.7 | 441 | 46 |  | 500 | bar g | °C | 50 |  | P | 2267
S-01722 | PG-2281 | P15 | Inlet H 2001 Primary Reformer | 34"-RFG-20-114-H44-H | Process Gas | 36.3 | 638 | 46 |  | 675 | bar g | °C | 50 |  | P | 2281
S-01722 | PG-2286/1 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 4"-FG-20-115-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2286 | 1
S-01722 | PG-2286/2 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-116-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2286 | 2
S-01722 | PG-2286/3 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-117-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2286 | 3
S-01722 | PG-2286/4 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 6"-FG-20-118-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2286 | 4
S-01722 | PG-2287/1 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2287 | 1
S-01722 | PG-2287/2 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2287 | 2
S-01722 | PG-2287/3 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2287 | 3
S-01722 | PG-2287/4 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2287 | 4
S-01722 | PG-2288/1 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2288 | 1
S-01722 | PG-2288/2 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2288 | 2
S-01722 | PG-2288/3 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2288 | 3
S-01722 | PG-2288/4 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2288 | 4
S-01722 | PG-2289/1 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 4"-FG-20-107-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2289 | 1
S-01722 | PG-2289/2 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-108-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2289 | 2
S-01722 | PG-2289/3 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-109-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2289 | 3
S-01722 | PG-2289/4 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 6"-FG-20-110-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2289 | 4
S-01722 | PG-2290/1 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 4"-FG-20-111-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2290 | 1
S-01722 | PG-2290/2 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-112-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2290 | 2
S-01722 | PG-2290/3 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-113-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2290 | 3
S-01722 | PG-2290/4 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 6"-FG-20-114-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2290 | 4
S-01722 | PG-2291/1 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2291 | 1
S-01722 | PG-2291/2 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2291 | 2
S-01722 | PG-2291/3 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2291 | 3
S-01722 | PG-2291/4 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2291 | 4
S-01722 | PG-2292/1 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2292 | 1
S-01722 | PG-2292/2 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2292 | 2
S-01722 | PG-2292/3 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2292 | 3
S-01722 | PG-2292/4 | P15 | Combustion Air to Burner H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2292 | 4
S-01722 | PG-2293/1 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 4"-FG-20-120-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2293 | 1
S-01722 | PG-2293/2 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-121-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2293 | 2
S-01722 | PG-2293/3 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 8"-FG-20-122-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2293 | 3
S-01722 | PG-2293/4 | P15 | Fuel Gas to Burner H 2001 Primary Reformer | 6"-FG-20-123-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2293 | 4
S-01722 | PG-2294 | P15 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | P | 2294
S-01722 | PG-2296 | P15 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | P | 2296
S-01722 | PG-2362 | P17 | Outlet E 2021 1&2 Steam Superheater | 24"-HHPS-20-115-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 50 |  | P | 2362
S-01722 | PG-2364 | P17 | HHP Steam to Header | 24"-HHPS-20-112-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 50 |  | P | 2364
S-01722 | PG-2375 | P18 | D 2001 HHP Steam Drum | D 2001 Top | Saturated HHP Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | P | 2375
S-01722 | PG-2408 | P19 | Inlet P 2001 A Process Condensate Pump No. 1 | 4"-PRC-20-116-G40-H | Process Condensate | 27 | 165 | 71 |  | 200 | bar g | °C | 50 |  | P | 2408
S-01722 | PG-2411 | P19 | Outlet P 2001 A Process Condensate Pump No. 1 | 3"-PRC-20-114-G40-H | Process Condensate | 55 | 165 | 71 |  | 200 | bar g | °C | 50 |  | P | 2411
S-01722 | PG-2412 | P19 | Inlet P 2001 B Process Condensate Pump No. 1 | 4"-PRC-20-115-G40-H | Process Condensate | 27 | 165 | 71 |  | 200 | bar g | °C | 50 |  | P | 2412
S-01722 | PG-2415 | P19 | Outlet P 2001 B Process Condensate Pump No. 1 | 3"-PRC-20-110-G40-H | Process Condensate | 55 | 165 | 71 |  | 200 | bar g | °C | 50 |  | P | 2415
S-01722 | PG-2445 | P20 | Inlet P 2002 A Process Condensate Pump No. 2 | 8"-PRC-20-121-G40-H | Process Condensate | 26 | 138 | 71 |  | 200 | bar g | °C | 50 |  | P | 2445
S-01722 | PG-2448 | P20 | Outlet P 2002 A Process Condensate Pump No. 2 | 6"-PRC-20-118-G40-H | Process Condensate | 53 | 138 | 71 |  | 200 | bar g | °C | 50 |  | P | 2448
S-01722 | PG-2449 | P20 | Inlet P 2002 B Process Condensate Pump No. 2 | 8"-PRC-20-120-G40-H | Process Condensate | 26 | 138 | 71 |  | 200 | bar g | °C | 50 |  | P | 2449
S-01722 | PG-2452 | P20 | Outlet P 2002 B Process Condensate Pump No. 2 | 6"-PRC-20-126-G40-H | Process Condensate | 53 | 138 | 71 |  | 200 | bar g | °C | 50 |  | P | 2452
S-01722 | PG-2454 | P20 | DMW from BL | 10"-DMW-20-101-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | P | 2454
S-01722 | PG-2485 | P21 | Inlet P 2003 A Process Condensate Pump No. 3 | 6"-PRC-20-127-G40-N | Process Condensate | 25 | 48 | 80 |  | 100 | bar g | °C | 50 |  | P | 2485
S-01722 | PG-2488 | P21 | Outlet P 2003 A Process Condensate Pump No. 3 | 4"-PRC-20-104-G40-N | Process Condensate | 53 | 49 | 80 |  | 100 | bar g | °C | 50 |  | P | 2488
S-01722 | PG-2489 | P21 | Inlet P 2003 B Process Condensate Pump No. 3 | 6"-PRC-20-128-G40-N | Process Condensate | 25 | 48 | 80 |  | 100 | bar g | °C | 50 |  | P | 2489
S-01722 | PG-2492 | P21 | Outlet P 2003 B Process Condensate Pump No. 3 | 4"-PRC-20-129-G40-N | Process Condensate | 53 | 49 | 80 |  | 100 | bar g | °C | 50 |  | P | 2492
S-01722 | PG-2539 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 50 |  | P | 2539
S-01722 | PG-2552 | U01 | Fuel Gas for Burner Tightness Test | 2"-NG-20-113-B24-N | Fuel Gas | 3 | 35 | 7 |  | 85 | bar g | °C | 50 |  | P | 2552
S-01722 | PG-2573 | U02 | Start-up N2 from D 2005 | 10"-N-20-110-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | P | 2573
S-01722 | PG-2578 | U02 | Make-up Nitrogen from Header | 3"-N-20-115-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | P | 2578
S-01722 | PG-2580 | U02 | Outlet C 2001 Start-up Nitrogen Compressor | 10"-N-20-104-B24-P | Nitrogen Gas | 8 | 84 | 10.5 |  | 110 | bar g | °C | 50 |  | P | 2580
S-01722 | PG-2602 | U17 | Import H2 | 3"-HG-20-102-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | P | 2602
S-01722 | PG-2606 | U17 | H2 Recycle System | 3"-HG-20-103-F24-N | Hydrogen Gas | 50.4 | 48 | 55 |  | 200 | bar g | °C | 50 |  | P | 2606
S-01722 | PG-3006 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | P | 3006
S-01722 | PG-3009 | P22 | Synthesis Gas to R 3001 Catalyst Reduction | 3"-SG-30-129-D40-N | Synthesis Gas | 10 | 48 | 29 |  | 100 | bar g | °C | 50 |  | P | 3009
S-01722 | PG-3011 | P22 | Hydrogen from BL | 3"-HG-30-101-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | P | 3011
S-01722 | PG-3012 | P22 | Hydrogen from BL | 3"-HG-30-101-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | P | 3012
S-01722 | PG-3014 | P22 | Process Air from BL | 3"-PA-30-101-B24-N | Process Air | 7.5 | 35 | 10.5 |  | 75 | bar g | °C | 50 |  | P | 3014
S-01722 | PG-3015 | P22 | Process Air from BL | 3"-PA-30-101-B24-N | Process Air | 7.5 | 35 | 10.5 |  | 75 | bar g | °C | 50 |  | P | 3015
S-01722 | PG-3017 | P22 | Synthesis Gas to R 3001 Catalyst Reduction | 3"-SG-30-150-D24-N | Synthesis Gas | 6 | 48 | 29 |  | 100 | bar g | °C | 50 |  | P | 3017
S-01722 | PG-3046 | P23 | D 3003 MP Steam Drum | D 3003 Top | Medium Pressure Steam | 33.7 | 242 | 45 |  | 290 | bar g | °C | 50 |  | P | 3046
S-01722 | PG-3056 | P23 | MP Steam from Header | 4"-MPS-70-118-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 50 |  | P | 3056
S-01722 | PG-3083 | P24 | MP Steam for heating of R 3001 1/2/3 | 12"-MPS-70-120-F24-H | Medium Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | P | 3083
S-01722 | PG-3165 | P27 | Outlet D 3001 HP Separator | 30"-SG-30-118-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | P | 3165
S-01722 | PG-3191 | P28 | Inlet D 3002 LP Separator | 12"-PMC-30-105-G40-N | Crude Methanol | 32 | 47 | 100 |  | 100 | bar g | °C | 50 |  | P | 3191
S-01722 | PG-3195 | P28 | D 3002 LP Separator | D 3002 Top | Purge Gas | 4 | 47 | 7 |  | 100 | bar g | °C | 50 |  | P | 3195
S-01722 | PG-5005 | P29 | TK 5001 Raw Methanol Buffer Tank | TK 5001 | Raw Methanol | 0 | 46 | -0.3 |  | 100 | mbar g | °C | 50 |  | P | 5005
S-01722 | PG-5011 | P29 | Inlet P 5001 A Raw Methanol Pump | 16"-PMC-50-101-B40-N | Crude Methanol | 1 | 47 | 13 |  | 100 | bar g | °C | 50 |  | P | 5011
S-01722 | PG-5014 | P29 | Outlet P 5001 A Raw Methanol Pump | 10"-PMC-50-103-B40-N | Crude Methanol | 5 | 47 | 13 |  | 100 | bar g | °C | 50 |  | P | 5014
S-01722 | PG-5015 | P29 | Inlet P 5001 B Raw Methanol Pump | 16"-PMC-50-102-B40-N | Crude Methanol | 1 | 47 | 13 |  | 100 | bar g | °C | 50 |  | P | 5015
S-01722 | PG-5018 | P29 | Outlet P 5001 B Raw Methanol Pump | 10"-PMC-50-104-B40-N | Crude Methanol | 5 | 47 | 13 |  | 100 | bar g | °C | 50 |  | P | 5018
S-01722 | PG-5046 | P30 | Nitrogen for Purge | 2"N-50-103-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 70 | bar g | °C | 50 |  | P | 5046
S-01722 | PG-5075 | P31 | Inlet P 5011 A Steam Condensate Pump | 8"-LPC-50-110-D24-H | Low Pressure Steam Condensate | 2.4 | 138 | 18 |  | 190 | bar g | °C | 50 |  | P | 5075
S-01722 | PG-5078 | P31 | Outlet P 5011 A Steam Condensate Pump | 4"-LPC-50-108-D24-H | Low Pressure Steam Condensate | 5.7 | 138 | 18 |  | 190 | bar g | °C | 50 |  | P | 5078
S-01722 | PG-5079 | P31 | Inlet P 5011 B Steam Condensate Pump | 8"-LPC-50-104-D24-H | Low Pressure Steam Condensate | 2.4 | 168 | 18 |  | 190 | bar g | °C | 50 |  | P | 5079
S-01722 | PG-5082 | P31 | Outlet P 5011 B Steam Condensate Pump | 4"-LPC-50-107-D24-H | Low Pressure Steam Condensate | 5.7 | 138 | 18 |  | 190 | bar g | °C | 50 |  | P | 5082
S-01722 | PG-5096 | P32 | D 5001 Stabilizer Column OH Accumulator | D 5001 | Rich Methanol Gas Liquid | 0.6 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5096
S-01722 | PG-5099 | P32 | Inlet P 5003 A Stabilizer Column Reflux Pump | 10"-PMC-50-121-B24 | Crude Methanol | 0.6 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5099
S-01722 | PG-5102 | P32 | Outlet P 5003 A Stabilizer Column Reflux Pump | 8"-PMC-50-123-B24-N | Crude Methanol | 3.8 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5102
S-01722 | PG-5103 | P32 | Inlet P 5003 B Stabilizer Column Reflux Pump | 10"-PMC-50-122-B24 | Crude Methanol | 0.6 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5103
S-01722 | PG-5106 | P32 | Outlet P 5003 B Stabilizer Column Reflux Pump | 8"-PMC-50-124-B24-P | Crude Methanol | 3.8 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5106
S-01722 | PG-5112 | P32 | Outlet E 5010 OH Gas Condenser | 6"-PG-50-101-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 50 |  | P | 5112
S-01722 | PG-5113 | P32 | Off-Gas to J 3001 | 6"-PG-50-102-B24-N | Purge Gas | 0.2 | 47 | 3.5 |  | 75 | bar g | °C | 50 |  | P | 5113
S-01722 | PG-5131 | P33 | Inlet P 5002 A Stabilizer Methanol Pump | 16"-PMC-50-130-B24-H | Crude Methanol | 1 | 88 | 10 |  | 160 | bar g | °C | 50 |  | P | 5131
S-01722 | PG-5134 | P33 | Outlet P 5002 A Stabilizer Methanol Pump | 10"-PMC-50-132-B24-H | Crude Methanol | 2.5 | 88 | 10 |  | 160 | bar g | °C | 50 |  | P | 5134
S-01722 | PG-5135 | P33 | Inlet P 5002 B Stabilizer Methanol Pump | 16"-PMC-50-131-B24-H | Crude Methanol | 1 | 88 | 10 |  | 160 | bar g | °C | 50 |  | P | 5135
S-01722 | PG-5138 | P33 | Outlet P 5002 B Stabilizer Methanol Pump | 10"-PMC-50-133-B24-H | Crude Methanol | 2.5 | 88 | 10 |  | 160 | bar g | °C | 50 |  | P | 5138
S-01722 | PG-5178 | P34 | Outlet T 5002 LP Methanol Column | 72"PMV-50-130-B24-P | Methanol Vapour | 0.1 | 67 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5178
S-01722 | PG-5206 | P36 | D 5002 LP Column OH Accumulator | D 5002 Top | Methanol Vapour | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5206
S-01722 | PG-5210 | P36 | Inlet P 5004 A LP Column Reflux Pump | 20"-PMP-50-102-B24-H | Methanol Product | 0 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5210
S-01722 | PG-5213 | P36 | Outlet P 5004 A LP Column Reflux Pump | 12"-PMP-50-104-B24-H | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5213
S-01722 | PG-5214 | P36 | Inlet P 5004 B LP Column Reflux Pump | 20"-PMP-50-103-B24-H | Methanol Product | 0 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5214
S-01722 | PG-5217 | P36 | Outlet P 5004 B LP Column Reflux Pump | 12"-PMP-50-105-B24-H | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5217
S-01722 | PG-5231 | P37 | Inlet P 5005 A MP Column Feed Pump | 10"-PMC-50-150-D24-H | Crude Methanol | 0.7 | 86 | 16 |  | 160 | bar g | °C | 50 |  | P | 5231
S-01722 | PG-5232 | U15 | Outlet P 5080 A Morpholine Dosing Pump | 1 1/2"-MOR-70-101-B40-N | Morpholine | 2 | 35 | 7 |  | 65 | bar g | °C | 50 |  | P | 5232
S-01722 | PG-5234 | P37 | Outlet P 5005 A MP Column Feed Pump | 8"-PMC-50-152-D24-H | Crude Methanol | 6.5 | 86 | 16 |  | 160 | bar g | °C | 50 |  | P | 5234
S-01722 | PG-5235 | P37 | Inlet P 5005 B MP Column Feed Pump | 10"-PMC-50-151-D24-H | Crude Methanol | 0.7 | 86 | 16 |  | 160 | bar g | °C | 50 |  | P | 5235
S-01722 | PG-5237 | U15 | Outlet P 5080 B Morpholine Dosing Pump | 1 1/2"-MOR-70-101-B40-N | Morpholine | 2 | 35 | 7 |  | 65 | bar g | °C | 50 |  | P | 5237
S-01722 | PG-5238 | P37 | Outlet P 5005 B MP Column Feed Pump | 8"-PMC-50-153-D24-H | Crude Methanol | 6.5 | 86 | 16 |  | 160 | bar g | °C | 50 |  | P | 5238
S-01722 | PG-5303 | P39 | Inlet E 5003 1/2/3 MP Column Reboiler No. 1 | 24"-LPS-50-108-D24-H | Low Pressure Steam | 6.5 | 188 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 5303
S-01722 | PG-5306 | P39 | Outlet E 5003 1/2/3 MP Column Reboiler No. 1 | 16"-LPC-50-115-B24-H | Low Pressure Steam Condensate | 6.5 | 168 | 10.5 |  | 190 | bar g | °C | 50 |  | P | 5306
S-01722 | PG-5324 | P40 | D 5003 MP Cooling OH Accumulator | D 5003 | Methanol | 2.7 | 101 | 6 |  | 165 | bar g | °C | 50 |  | P | 5324
S-01722 | PG-5327 | P40 | Inlet P 5006 A MP Column Reflux Pump | 24"-PMP-50-130-D24-H | Methanol Product | 2.6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | P | 5327
S-01722 | PG-5330 | P40 | Outlet P 5006 A MP Column Reflux Pump | 6"-PMP-50-140-D24-H | Methanol Product | 6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | P | 5330
S-01722 | PG-5331 | P40 | Inlet P 5006 B MP Column Reflux Pump | 24"-PMP-50-131-D24-H | Methanol Product | 2.6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | P | 5331
S-01722 | PG-5334 | P40 | Outlet P 5006 B MP Column Reflux Pump | 12"-PMP-50-133-D24-H | Methanol Product | 3.6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | P | 5334
S-01722 | PG-5351 | P41 | Inlet P 5007 A MP Column Recycle Pump | 10"-PMW-50-120-D24-H | Methanol Water | 3.6 | 149 | 15 |  | 175 | bar g | °C | 50 |  | P | 5351
S-01722 | PG-5354 | P41 | Outlet P 5007 A MP Column Recycle Pump | 6"-PMW-50-122-D24-H | Methanol Water | 4.5 | 149 | 15 |  | 175 | bar g | °C | 50 |  | P | 5354
S-01722 | PG-5355 | P41 | Inlet P 5007 B MP Column Recycle Pump | 3"-PMW-50-121-D24-H | Methanol Water | 3.6 | 149 | 15 |  | 175 | bar g | °C | 50 |  | P | 5355
S-01722 | PG-5358 | P41 | Outlet P 5007 B MP Column Recycle Pump | 6"-PMW-50-123-D24-H | Methanol Water | 4.5 | 149 | 15 |  | 175 | bar g | °C | 50 |  | P | 5358
S-01722 | PG-5359 | P41 | Inlet P 5010 A Excess Water Pump | 6"-PMW-50-130-F24-H | Methanol Water | 3.6 | 149 | 82 |  | 175 | bar g | °C | 50 |  | P | 5359
S-01722 | PG-5362 | P41 | Outlet P 5010 A Excess Water Pump | 3"-PMW-50-132-F24-H | Methanol Water | 50 | 150 | 82 |  | 175 | bar g | °C | 50 |  | P | 5362
S-01722 | PG-5363 | P41 | Inlet P 5010 B Excess Water Pump | 6"-PMW-50-131-F24-H | Methanol Water | 3.6 | 149 | 82 |  | 175 | bar g | °C | 50 |  | P | 5363
S-01722 | PG-5366 | P41 | Outlet P 5010 B Excess Water Pump | 3"-PMW-50-133-F24-H | Methanol Water | 50 | 150 | 82 |  | 175 | bar g | °C | 50 |  | P | 5366
S-01722 | PG-5388 | P42 | Inlet X 5001 Product Polisher Unit | 10"-PMP-50-142-B24-N | Methanol Product | 3 | 48 | 19 |  | 75 | bar g | °C | 50 |  | P | 5388
S-01722 | PG-5399 | P43 | TK 5002 1 Methanol Product Buffer Tank | TK 5002 1 | Methanol Product | 0 | 48 | -0.03 |  | 85 | bar g | °C | 50 |  | P | 5399
S-01722 | PG-5402 | P43 | Inlet P 5012 Methanol Start-up Pump | 4"-PMP-50-160-F24-N | Methanol Product | 1 | 48 | 52 |  | 75 | bar g | °C | 50 |  | P | 5402
S-01722 | PG-5406 | P43 | Outlet P 5012 Methanol Start-up Pump | 3"-PMP-50-161-F24-N | Methanol Product | 47 | 48 | 52 |  | 75 | bar g | °C | 50 |  | P | 5406
S-01722 | PG-5416 | P44 | TK 5002 2 Methanol Product Buffer Tank | TK 5002 2 | Methanol Product | 0 | 48 | -0.3 |  | 85 | bar g | °C | 50 |  | P | 5416
S-01722 | PG-5423 | P44 | Inlet P 5008 A Methanol Product Pump | 10"-PMP-50-150-B24-N | Methanol Product | 1 | 48 | 14 |  | 75 | bar g | °C | 50 |  | P | 5423
S-01722 | PG-5426 | P44 | Outlet P 5008 A Methanol Product Pump | 8"-PMP-50-153-B24-N | Methanol Product | 5 | 48 | 14 |  | 75 | bar g | °C | 50 |  | P | 5426
S-01722 | PG-5427 | P44 | Inlet P 5008 B Methanol Product Pump | 10"-PMP-50-151-B24-N | Methanol Product | 1 | 48 | 14 |  | 75 | bar g | °C | 50 |  | P | 5427
S-01722 | PG-5430 | P44 | Outlet P 5008 B Methanol Product Pump | 8"-PMP-50-154-B24-N | Methanol Product | 5 | 48 | 14 |  | 75 | bar g | °C | 50 |  | P | 5430
S-01722 | PG-5449 | P45 | TK 5003 Liquid Off-stream Tank | TK 5003 | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 100 | bar g | °C | 50 |  | P | 5449
S-01722 | PG-5453 | P45 | Inlet P 5009 A Liquid Off-stream Pump | 2"-LOS-50-120-F24-N | Liquid Off-stream | 0 | 48 | 60 |  | 75 | bar g | °C | 50 |  | P | 5453
S-01722 | PG-5456 | P45 | Outlet P 5009 A Liquid Off-stream Pump | 2"-LOS-50-122-F24-N | Liquid Off-stream | 53 | 50 | 60 |  | 75 | bar g | °C | 50 |  | P | 5456
S-01722 | PG-5457 | P45 | Inlet P 5009 B Liquid Off-stream Pump | 2"-LOS-50-121-F24-N | Liquid Off-stream | 0 | 48 | 60 |  | 75 | bar g | °C | 50 |  | P | 5457
S-01722 | PG-5460 | P45 | Outlet P 5009 B Liquid Off-stream Pump | 2"-LOS-50-123-F24-N | Liquid Off-stream | 53 | 50 | 60 |  | 75 | bar g | °C | 50 |  | P | 5460
S-01722 | PG-5501 | U23B | Inlet P 5010 A Excess Water Pump (optional) | 6"-PMW-50-148-F24-N | Methanol Water | 0 | 43 | 82 |  | 100 | bar g | °C | 50 |  | P | 5501
S-01722 | PG-5502 | U23B | Outlet P 5010 A Excess Water Pump (optional) | 3"-PMW-50-149-F24-N | Methanol Water | 50 | 43 | 82 |  | 100 | bar g | °C | 50 |  | P | 5502
S-01722 | PG-5503 | U23B | Inlet P 5010 B Excess Water Pump (optional) | 6"-PMW-50-151-F24-H | Methanol Water | 0 | 43 | 82 |  | 100 | bar g | °C | 50 |  | P | 5503
S-01722 | PG-5504 | U23B | Outlet P 5010 B Excess Water Pump (optional) | 3"-PMW-50-152-F24-N | Methanol Water | 50 | 43 | 82 |  | 100 | bar g | °C | 50 |  | P | 5504
S-01722 | PG-5511 | U24 | Outlet P 5070 A NaOH Solution Dosing Pump (optional) | 1 1/2"-NS-50-101-B40-N | NaOH Solution | 2 | 35 | 7 |  | 75 | bar g | °C | 50 |  | P | 5511
S-01722 | PG-5513 | U24 | Outlet P 5070 A NaOH Solution Dosing Pump (optional) | 1 1/2"-NS-50-101-B40-N | NaOH Solution | 2 | 35 | 7 |  | 75 | bar g | °C | 50 |  | P | 5513
S-01722 | PG-6002 | P05 | Inlet P 6002 A Steam Condensate Return Pump | 18"-MPC-60-101-F24-H | Medium Pressure Steam Condensate | 32.5 | 240 | 73 |  | 260 | bar g | °C | 50 |  | P | 6002
S-01722 | PG-6005 | P05 | Outlet P 6002 A Steam Condensate Return Pump | 10"-MPC-60-106-F24-H | Medium Pressure Steam Condensate | 45 | 241 | 73 |  | 260 | bar g | °C | 50 |  | P | 6005
S-01722 | PG-6006 | P05 | Inlet P 6002 B Steam Condensate Return Pump | 18"-MPC-60-102-F24-H | Medium Pressure Steam Condensate | 32.5 | 240 | 73 |  | 260 | bar g | °C | 50 |  | P | 6006
S-01722 | PG-6009 | P05 | Outlet P 6002 B Steam Condensate Return Pump | 10"-MPC-60-108-F24-H | Medium Pressure Steam Condensate | 45 | 241 | 73 |  | 260 | bar g | °C | 50 |  | P | 6009
S-01722 | PG-6023 | P06 | Inlet T 6001 Saturator | 16"-PRG-60-102-F24-H | Process Gas | 43.3 | 265 | 55 |  | 290 | bar g | °C | 50 |  | P | 6023
S-01722 | PG-6029 | P06 | Outlet X 6001 A Particle Filter | 8"-PRC-60-103-G40-H | Process Condensate | 44 | 115 | 71 |  | 180 | bar g | °C | 50 |  | P | 6029
S-01722 | PG-6030 | P06 | Outlet X 6001 B Particle Filter | 8"-PRC-60-104-G40-H | Process Condensate | 44 | 115 | 71 |  | 180 | bar g | °C | 50 |  | P | 6030
S-01722 | PG-6055 | P07 | Outlet D 6001 Feed Gas Separator | 24"-PRG-60-103-F24-H | Process Gas | 42.8 | 226 | 55 |  | 290 | bar g | °C | 50 |  | P | 6055
S-01722 | PG-6060 | P07 | Inlet P 6001 A Saturator Circulation Pump | 16"-PRC-60-109-G40-H | Process Condensate | 43 | 225 | 72 |  | 290 | bar g | °C | 50 |  | P | 6060
S-01722 | PG-6063 | P07 | Outlet P 6001 A Saturator Circulation Pump | 10"-PRC-60-111-G40-H | Process Condensate | 44 | 225 | 72 |  | 290 | bar g | °C | 50 |  | P | 6063
S-01722 | PG-6064 | P07 | Inlet P 6001 B Saturator Circulation Pump | 16"-PRC-60-110-G40-H | Process Condensate | 43 | 225 | 56 |  | 290 | bar g | °C | 50 |  | P | 6064
S-01722 | PG-6067 | P07 | Outlet P 6001 B Saturator Circulation Pump | 10"-PRC-60-112-G40-H | Process Condensate | 44 | 225 | 72 |  | 280 | bar g | °C | 50 |  | P | 6067
S-01722 | PG-6081 | P08 | Inlet P 7003 A Excess Process Condensate Pump | 4"-BD-60-117-B40-P | Process Condensate | 0 | 100 | 9 |  | 125 | bar g | °C | 50 |  | P | 6081
S-01722 | PG-6082 | P08 | Outlet P 7003 A Excess Process Condensate Pump | 4"-BD-60-119-B40-P | Process Condensate | 3 | 78 | 9 |  | 150 | bar g | °C | 50 |  | P | 6082
S-01722 | PG-6086 | P08 | Inlet P 7003 B Excess Process Condensate Pump | 4"-BD-60-117-B40-P | Process Condensate | 0 | 100 | 9 |  | 125 | bar g | °C | 50 |  | P | 6086
S-01722 | PG-6087 | P08 | Outlet P 7003 B Excess Process Condensate Pump | 4"-BD-60-123-B40-P | Process Condensate | 3 | 100 | 7 |  | 125 | bar g | °C | 50 |  | P | 6087
S-01722 | PG-7008 | U03 | HP Steam Header | 28"-HPS-70-116-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 7008
S-01722 | PG-7022 | U04 | HP Steam Export/Import | 24"-HPS-70-107-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | P | 7022
S-01722 | PG-7035 | U05 | MP Steam Header | 24"-MPS-30-115-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 50 |  | P | 7035
S-01722 | PG-7054 | U06 | LP Steam | 16"-LPS-70-138-D24-H | Low Pressure Steam | 7 | 240 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 7054
S-01722 | PG-7062 | U18 | Outlet P 7002 A Demineralized Water Pump | 10"-DMW-70-101-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | P | 7062
S-01722 | PG-7063 | U18 | Outlet P 7002 B Demineralized Water Pump | 10"-DMW-70-109-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | P | 7063
S-01722 | PG-7093 | U09 | D 7001 Deaerator | D 7001 Top | Low Pressure Steam | 1 | 120 | 3.5 |  | 200 | bar g | °C | 50 |  | P | 7093
S-01722 | PG-7102 | U22 | Inlet P 7004 A Excess Process Condensate Pump | 2"-PRC-70-139-G40-N | Process Condensate | 1 | 65 | 71 |  | 100 | bar g | °C | 50 |  | P | 7102
S-01722 | PG-7103 | U22 | Outlet P 7004 A Excess Process Condensate Pump | 2"-PRC-70-141-G40-N | Process Condensate | 46 | 65 | 71 |  | 100 | bar g | °C | 50 |  | P | 7103
S-01722 | PG-7105 | U22 | Inlet P 7004 B Excess Process Condensate Pump | 2"-PRC-70-143-G40-N | Process Condensate | 1 | 65 | 71 |  | 100 | bar g | °C | 50 |  | P | 7105
S-01722 | PG-7106 | U22 | Outlet P 7004 B Excess Process Condensate Pump | 2"-PRC-70-144-G40-N | Process Condensate | 45 | 65 | 71 |  | 100 | bar g | °C | 50 |  | P | 7106
S-01722 | PG-7111 | U10 | Inlet P 7001 A BFW Pump | 14"-BFW-70-151-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | P | 7111
S-01722 | PG-7113 | U10 | Outlet P 7001 A BFW Pump | 8"-BFW-70-160-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | P | 7113
S-01722 | PG-7114 | U10 | Outlet P 7001 A BFW Pump | 6"-BFW-70-138-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 50 |  | P | 7114
S-01722 | PG-7115 | U10 | Inlet P 7001 B BFW Pump | 14"-BFW-70-135-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | P | 7115
S-01722 | PG-7117 | U10 | Outlet P 7001 B BFW Pump | 8"-BFW-70-133-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | P | 7117
S-01722 | PG-7118 | U10 | Outlet P 7001 B BFW Pump | 4"-BFW-70-149-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 50 |  | P | 7118
S-01722 | PG-7119 | U10 | Inlet P 7001 C BFW Pump | 14"-BFW-70-136-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | P | 7119
S-01722 | PG-7123 | U10 | Outlet P 7001 C BFW Pump | 8"-BFW-70-147-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | P | 7123
S-01722 | PG-7124 | U10 | Outlet P 7001 C BFW Pump | 4"-BFW-70-148-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 50 |  | P | 7124
S-01722 | PG-7128 | U10 | HP Steam to FP 7001 A Steam Turbine for FP 7001 A | 8"-HPS-70-117-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 7128
S-01722 | PG-7133 | U10 | HP Steam to FP 7001 B Steam Turbine for FP 7001 B | 8"-HPS-70-118-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 7133
S-01722 | PG-7138 | U10 | LP Steam from FP 7001 A Steam Turbine for FP 7001 A | 14"-LPS-70-121-D24-H | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 7138
S-01722 | PG-7139 | U10 | LP Steam from FP 7001 B Steam Turbine for FP 7001 B | 14"-LPS-70-125-D24-H | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 7139
S-01722 | PG-7164 | U12 | Outlet P 7051 A Phosphate Dosing Pump | 1 1/2"-PH-70-101-H40-N | Phosphate | 103 | 35 | 114 |  | 75 | bar g | °C | 50 |  | P | 7164
S-01722 | PG-7167 | U12 | Outlet P 7051 B Phosphate Dosing Pump | 1 1/2"-PH-70-101-H40-N | Phosphate | 103 | 35 | 114 |  | 75 | bar g | °C | 50 |  | P | 7167
S-01722 | PG-7170 | U12 | Outlet P 7052 A Phosphate Dosing Pump | 1 1/2"-PH-70-102-F40-H | Phosphate | 35 | 35 | 47 |  | 75 | bar g | °C | 50 |  | P | 7170
S-01722 | PG-7173 | U12 | Outlet P 7052 B Phosphate Dosing Pump | 1 1/2"-PH-70-102-F40-H | Phosphate | 35 | 35 | 47 |  | 75 | bar g | °C | 50 |  | P | 7173
S-01722 | PG-7194 | U13 | Outlet P 7060 A Ammonia Dosing Pump | 1 1/2"-AM-70-101-B40-H | Ammonia | 2 | 35 | 7 |  | 75 | bar g | °C | 50 |  | P | 7194
S-01722 | PG-7197 | U13 | Outlet P 7060 B Ammonia Dosing Pump | 1 1/2"-AM-70-101-B40-H | Ammonia | 2 | 35 | 7 |  | 75 | bar g | °C | 50 |  | P | 7197
S-01722 | PG-7214 | U14 | Outlet P 7070 A Oxygen Scavenger Dosing Pump | 1 1/2"-HZ-70-101-B40-N | Oxygen Scavenger | 2 | 35 | 7 |  | 75 | bar g | °C | 50 |  | P | 7214
S-01722 | PG-7217 | U14 | Outlet P 7070 B Oxygen Scavenger Dosing Pump | 1 1/2"-HZ-70-101-B40-N | Oxygen Scavenger | 2 | 35 | 7 |  | 75 | bar g | °C | 50 |  | P | 7217
S-01722 | PG-8011 | U21 | Inlet Flare KO Drum | 72"-FLG-80-144-B24-P | Flare gas | 1.5 | 390 | 5 |  | 410 | bar g | °C | 50 |  | P | 8011
S-01722 | PG-8012 | U21 | Inlet Igniter | -IA-80-101- | Instrument Air | [5 empty] | bar g | °C | 50 |  | P | 8012
S-01722 | PI-1001 | P01 | Natural Gas from BL | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | P | 1001
S-01722 | PI-2001 | P02 | Process Oxygen from BL | 10"-PO-20-110-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | P | 2001
S-01722 | PI-2035 | P03 | Outlet X 2002 A/B Steam Filter | 4"-HPS-20-106-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 2035
S-01722 | PI-2046 | P03 | Process Oxygen/Steam to R 2004 Secondary Reformer | 18"-PO-20-116-F50-H | Process Oxygen | 34 | 236 | 47 |  | 270 | bar g | °C | 50 |  | P | 2046
S-01722 | PI-2047 | P03 | Process Oxygen to Mixing Point | 16"-PO-20-114-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 50 |  | P | 2047
S-01722 | PI-2061 | P09 | Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-60-104-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 50 |  | P | 2061
S-01722 | PI-2077 | P09 | HP Steam to Steam/NG Mixture | 12"-HPS-20-104-F24-H | High Pressure Steam | 42.1 | 343 | 52 |  | 410 | bar g | °C | 50 |  | P | 2077
S-01722 | PI-2099 | P10 | Process Gas to E 2002 Prereformer Feed Preheat Coil | 24"-PRG-20-112-F24-H | Process Gas | 42.1 | 267 | 46 |  | 410 | bar g | °C | 50 |  | P | 2099
S-01722 | PI-2111 | P11 | Air Intake F 2002 Combustion Air Blower | CA | Air | -3 | 48 |  |  |  | mbar g | °C | 50 |  | P | 2111
S-01722 | PI-2112 | P11 | Outlet F 2002 Combustion Air Blower | Ducting | Combustion Air | 21 | 54 |  |  | 80 | mbar g | °C | 50 |  | P | 2112
S-01722 | PI-2150 | P12 | N2 Recycle from Header | 3"-HG-20-112-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 50 |  | P | 2150
S-01722 | PI-2156 | P12 | WHS between E 2007 and F 2001 | WHS | Flue Gas | -70 | 150 |  |  |  | mbar g | °C | 50 |  | P | 2156
S-01722 | PI-2268 | P14 | Outlet R 2003 Prereformer | 30"-RFG-20-101-F34-H | Reformed Gas | 37.7 | 441 | 46 |  | 500 | bar g | °C | 50 |  | P | 2268
S-01722 | PI-2282 | P15 | Inlet H 2001 Primary Reformer | 34"-RFG-20-114-H44-H | Process Gas | 36.3 | 638 | 46 |  | 675 | bar g | °C | 50 |  | P | 2282
S-01722 | PI-2307 | P15 | Cold Collector | Cold Collector | Reformed Gas | 32 | 742 | 34.7 |  | 800 | bar g | °C | 50 |  | P | 2307
S-01722 | PI-2322 | P16A | R 2004 Secondary Reformer | R 2004 | Process Gas | 31.4 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | P | 2322
S-01722 | PI-2324 | P16A | R 2004 Secondary Reformer | R 2004 | Process Gas | 27.1 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | P | 2324
S-01722 | PI-2352 | P17 | Outlet E 2021 3 Steam Superheater | 42"-RFG-20-115-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 50 |  | P | 2352
S-01722 | PI-2372 | P18 | D 2001 HHP Steam Drum | D 2001 Top | Saturated HHP Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 50 |  | P | 2372
S-01722 | PI-2416 | P19 | Outlet P 2001 A/B Process Condensate Pump No. 1 | 3"-PRC-20-114-G40-H | Process Condensate | 55 | 165 | 71 |  | 200 | bar g | °C | 50 |  | P | 2416
S-01722 | PI-2453 | P20 | Outlet P 2002 A/B Process Condensate Pump No. 2 | 6"-PRC-20-118-G40-H | Process Condensate | 53 | 138 | 71 |  | 200 | bar g | °C | 50 |  | P | 2453
S-01722 | PI-2455 | P20 | DMW from BL | 10"-DMW-20-101-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | P | 2455
S-01722 | PI-2493 | P21 | Outlet P 2003 A/B Process Condensate Pump No. 3 | 4"-PRC-20-104-G40-N | Process Condensate | 53 | 49 | 80 |  | 100 | bar g | °C | 50 |  | P | 2493
S-01722 | PI-2540 | U01 | Fuel Gas to Mixing Point | 24"-NG-20-108-B24-N | Natural Gas | 2 | 35 | 7 |  | 85 | bar g | °C | 50 |  | P | 2540
S-01722 | PI-2579 | U02 | Outlet C 2001 Start-up Nitrogen Compressor | 10"-N-20-104-B24-P | Nitrogen Gas | 8 | 84 | 10.5 |  | 110 | bar g | °C | 50 |  | P | 2579
S-01722 | PI-2582 | U02 | Outlet C 2001 Start-up Nitrogen Compressor | 10"-N-20-104-B24-P | Nitrogen Gas | 8 | 84 | 10.5 |  | 110 | bar g | °C | 50 |  | P | 2582
S-01722 | PI-2601 | U17 | Import H2 | 3"-HG-20-102-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | P | 2601
S-01722 | PI-2607 | U17 | Recycle Hydrogen from Loop | 3"-SG-30-128-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | P | 2607
S-01722 | PI-3023 | P22 | Outlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 32"-SG-30-103-G40-N | Synthesis Gas | 80 | 74 | 99 |  | 120 | bar g | °C | 50 |  | P | 3023
S-01722 | PI-3071 | P24 | Inlet R 3001 1 Methanol Reactor | 24"-SG-30-135-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | P | 3071
S-01722 | PI-3075 | P24 | Inlet R 3001 2 Methanol Reactor | 24"-SG-30-107-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | P | 3075
S-01722 | PI-3079 | P24 | Inlet R 3001 3 Methanol Reactor | 24"-SG-30-119-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | P | 3079
S-01722 | PI-5004 | P29 | TK 5001 Raw Methanol Buffer Tank | TK 5001 | Raw Methanol | 0 | 46 | -0.3 |  | 100 | mbar g | °C | 50 |  | P | 5004
S-01722 | PI-5022 | P29 | Outlet P 5001 A/B Raw Methanol Pump | 10"-PMC-50-103-B40-N | Crude Methanol | 5 | 47 | 13 |  | 100 | bar g | °C | 50 |  | P | 5022
S-01722 | PI-5047 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5047
S-01722 | PI-5049 | P30 | T 5001 Stabilizer Column | T 5001 Top | Methanol Water Gas/Liquid | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5049
S-01722 | PI-5051 | P30 | Outlet T 5001 Stabilizer Column | 42"-PMV-50-110-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5051
S-01722 | PI-5083 | P31 | Outlet P 5011 A/B Steam Condensate Pump | 4"-LPC-50-108-D24-H | Low Pressure Steam Condensate | 5.7 | 138 | 18 |  | 190 | bar g | °C | 50 |  | P | 5083
S-01722 | PI-5093 | P32 | Outlet P 5003 A/B Stabilizer Column Reflux Pump | 8"-PMC-50-123-B24-N | Crude Methanol | 3.8 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5093
S-01722 | PI-5111 | P32 | Outlet E 5010 OH Gas Condenser | 6"-PG-50-101-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 50 |  | P | 5111
S-01722 | PI-5139 | P33 | Outlet P 5002 A Stabilizer Methanol Pump | 10"-PMC-50-132-B24-H | Crude Methanol | 2.5 | 88 | 10 |  | 160 | bar g | °C | 50 |  | P | 5139
S-01722 | PI-5166 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5166
S-01722 | PI-5168 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5168
S-01722 | PI-5170 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5170
S-01722 | PI-5172 | P34 | Outlet T 5002 LP Methanol Column | 72"PMV-50-130-B24-P | Methanol Vapour | 0.1 | 67 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5172
S-01722 | PI-5176 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5176
S-01722 | PI-5219 | P36 | Inlet E 5008 Methanol Product Cooler No. 1 | 6"-PMP-50-110-B24-P | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 50 |  | P | 5219
S-01722 | PI-5240 | P37 | Outlet P 5005 A/B MP Column Feed Pump | 8"-PMC-50-152-D24-H | Crude Methanol | 6.5 | 86 | 16 |  | 160 | bar g | °C | 50 |  | P | 5240
S-01722 | PI-5252 | P38 | Outlet T 5003 MP Methanol Column | 56"-PMV-50-150-B24-H | Methanol Vapour | 2.7 | 102 | 6 |  | 165 | bar g | °C | 50 |  | P | 5252
S-01722 | PI-5254 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | P | 5254
S-01722 | PI-5256 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | P | 5256
S-01722 | PI-5258 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | P | 5258
S-01722 | PI-5260 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | P | 5260
S-01722 | PI-5307 | P39 | Outlet E 5003 1/2/3 MP Column Reboiler No. 1 | 16"-LPC-50-115-B24-H | Low Pressure Steam Condensate | 6.5 | 168 | 10.5 |  | 190 | bar g | °C | 50 |  | P | 5307
S-01722 | PI-5335 | P40 | Inlet E 5012 Methanol Product Cooler No. 2 | 6"-PMP-50-140-D24-P | Methanol Product | 3.6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | P | 5335
S-01722 | PI-5367 | P41 | Outlet P 5010 A/B Excess Water Pump | 3"-PMW-50-132-F24-H | Methanol Water | 50 | 150 | 82 |  | 175 | bar g | °C | 50 |  | P | 5367
S-01722 | PI-5369 | P41 | Inlet AE 5006 Wash Water Air Cooler | 2"-PMW-50-124-B24-P | Methanol Water | 4.5 | 149 | 7.5 |  | 175 | bar g | °C | 50 |  | P | 5369
S-01722 | PI-5387 | P42 | Inlet X 5001 Product Polisher Unit | 10"-PMP-50-142-B24-N | Methanol | 3 | 48 | 19 |  | 75 | bar g | °C | 50 |  | P | 5387
S-01722 | PI-5398 | P43 | TK 5002 1 Methanol Product Buffer Tank | TK 5002 1 | Methanol Product | 0 | 48 | -0.03 |  | 85 | bar g | °C | 50 |  | P | 5398
S-01722 | PI-5415 | P44 | TK 5002 2 Methanol Product Buffer Tank | TK 5002 2 | Methanol Product | 0 | 48 | -0.3 |  | 85 | bar g | °C | 50 |  | P | 5415
S-01722 | PI-5421 | P44 | Methanol Product to Production Tank | 8"-PMP-50-153-B24-N | Methanol Product | 5 | 48 | 14 |  | 75 | bar g | °C | 50 |  | P | 5421
S-01722 | PI-5448 | P45 | TK 5003 Liquid Off-stream Tank | TK 5003 | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 100 | bar g | °C | 50 |  | P | 5448
S-01722 | PI-6010 | P05 | Outlet P 6002 A/B Steam Condensate Return Pump | 10"-MPC-60-106-F24-H | Medium Pressure Steam Condensate | 45 | 241 | 73 |  | 260 | bar g | °C | 50 |  | P | 6010
S-01722 | PI-6031 | P06 | Outlet X 6001 A/B Particle Filter | 8"-PRC-60-102-G40-H | Process Condensate | 44 | 119 | 71 |  | 180 | bar g | °C | 50 |  | P | 6031
S-01722 | PI-6054 | P07 | Outlet D 6001 Feed Gas Separator | 24"-PRG-60-103-F24-H | Process Gas | 42.8 | 226 | 55 |  | 290 | bar g | °C | 50 |  | P | 6054
S-01722 | PI-6088 | P08 | Outlet P 7003 A&B Excess Process Condensate Pumps | 4"-BD-60-119-B40-P | Process Condensate | 3 | 78 | 9 |  | 150 | bar g | °C | 50 |  | P | 6088
S-01722 | PI-7021 | U04 | HP Steam Export/Import | 24"-HPS-70-107-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | P | 7021
S-01722 | PI-7112 | U10 | Inlet P 7001 A BFW Pump | 14"-BFW-70-151-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | P | 7112
S-01722 | PI-7116 | U10 | Inlet P 7001 B BFW Pump | 14"-BFW-70-135-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | P | 7116
S-01722 | PI-7120 | U10 | Inlet P 7001 C BFW Pump | 14"-BFW-70-136-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 50 |  | P | 7120
S-01722 | PI-7127 | U10 | Outlet P 7001 A/B/C BFW Pump | 12"-BFW-70-140-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 50 |  | P | 7127
S-01722 | PI-8001 | U21 | Inlet Flare KO Drum | 72"-FLG-80-144-B24-P | Flare gas | 1.5 | 390 | 5 |  | 410 | bar g | °C | 50 |  | P | 8001
S-01722 | PIC-1006 | P01 | Outlet D 1001 Natural Gas K.O. Drum | 14"-NG-10-103-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 50 |  | P | 1006
S-01722 | PIC-1011 | P01 | Fuel Gas to H 2001 Primary Reformer | 24"-NG-20-102-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 50 |  | P | 1011
S-01722 | PIC-1045 | P04 | Outlet R 1002 2 Sulphur Absorber | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 50 |  | P | 1045
S-01722 | PIC-2015 | P02 | Inlet E 2008 Oxygen Preheater | 6"-HPS-20-102-F24-H | High Pressure Steam | 43.5 | 272 | 52 |  | 310 | bar g | °C | 50 |  | P | 2015
S-01722 | PIC-2073 | P09 | Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-60-104-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 50 |  | P | 2073
S-01722 | PIC-2163 | P12 | Combustion Air to H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | P | 2163
S-01722 | PIC-2224 | P13 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | P | 2224
S-01722 | PIC-2361 | P17 | Outlet E 2021 1&2 Steam Superheater | 24"-HHPS-20-115-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 50 |  | P | 2361
S-01722 | PIC-2363 | P17 | Outlet E 2021 1&2 Steam Superheater | 24"-HHPS-20-115-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 50 |  | P | 2363
S-01722 | PIC-2406 | P19 | Outlet D 2002 1st Separator | 34"-RFG-20-120-D40-H | Reformed Gas | 25.8 | 165 | 29 |  | 200 | bar g | °C | 50 |  | P | 2406
S-01722 | PIC-2481 | P21 | Outlet D 2005 Final Separator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | P | 2481
S-01722 | PIC-2536 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 50 |  | P | 2536
S-01722 | PIC-2554 | U01 | Fuel Gas to H 2001 | 28"-FG-20-101-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2554
S-01722 | PIC-2603 | U17 | Import H2 | 3"-HG-20-109-D24-N | Hydrogen Gas | 25 | 40 | 29 |  | 100 | bar g | °C | 50 |  | P | 2603
S-01722 | PIC-2608 | U17 | Recycle Hydrogen from Loop | 3"-HG-20-108-F24-N | Hydrogen Gas | 50.4 | 48 | 55 |  | 100 | bar g | °C | 50 |  | P | 2608
S-01722 | PIC-3007 | P22 | Inlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | P | 3007
S-01722 | PIC-3042 | P23 | D 3003 MP Steam Drum | D 3003 Top | Medium Pressure Steam | 33.7 | 242 | 45 |  | 290 | bar g | °C | 50 |  | P | 3042
S-01722 | PIC-3166 | P27 | Outlet D 3001 HP Separator | 30"-SG-30-118-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | P | 3166
S-01722 | PIC-3194 | P28 | D 3002 LP Separator | D 3002 Top | Purge Gas | 4 | 47 | 7 |  | 100 | bar g | °C | 50 |  | P | 3194
S-01722 | PIC-5069 | P31 | Inlet E 5001 Stabilizer Column Steam Reboiler | 14"-LPS-50-103-D24-H | Low Pressure Steam | 2.4 | 187 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 5069
S-01722 | PIC-5091 | P32 | Inlet AE 5004 Stabilizer Column OH Condenser | 42"-PMV-50-110-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5091
S-01722 | PIC-5109 | P32 | Outlet E 5010 OH Gas Condenser, Vent | [9 empty] | 50 |  | P | 5109
S-01722 | PIC-5207 | P36 | D 5002 LP Column OH Accumulator | D 5002 Top | Methanol Vapour | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | P | 5207
S-01722 | PIC-6025 | P06 | MP Steam to T 6001 Saturator | 24"-MPS-60-102-F24-H | Medium Pressure Steam | 32.2 | 240 | 45 |  | 300 | MPa g | °C | 50 |  | P | 6025
S-01722 | PIC-7001 | U03 | HP Extraction Steam from FT 7001 1/2 | 16"-HPS-30-129-F24-H | High Pressure Steam | 45 | 355 | 52 |  | 410 | bar g | °C | 50 |  | P | 7001
S-01722 | PIC-7002 | U03 | HHP Steam to Header | 24"-HHPS-20-112-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 50 |  | P | 7002
S-01722 | PIC-7003 | U03 | HP Steam Header | 28"-HPS-70-116-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 7003
S-01722 | PIC-7004 | U03 | HP Steam Header | 28"-HPS-70-116-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | P | 7004
S-01722 | PIC-7025 | U04 | HHP Steam Header | 24"-HHPS-20-112-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 50 |  | P | 7025
S-01722 | PIC-7028 | U04 | HP Import Steam to Header | 24"-HPS-70-133-F34-H | High Pressure Steam | 42.5 | 345 | 52 |  | 470 | bar g | °C | 50 |  | P | 7028
S-01722 | PIC-7031 | U05 | MP Steam Header | 24"-MPS-30-115-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 50 |  | P | 7031
S-01722 | PIC-7034 | U05 | MP Steam Header | 24"-MPS-30-115-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 50 |  | P | 7034
S-01722 | PIC-7051 | U06 | LP Steam | 16"-LPS-70-138-D24-H | Low Pressure Steam | 7 | 240 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 7051
S-01722 | PIC-7055 | U06 | LP Steam | 16"-LPS-70-138-D24-H | Low Pressure Steam | 7 | 240 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 7055
S-01722 | PIC-7056 | U06 | LP Steam | 32"-LPS-70-108-D24-H | Low Pressure Steam | 7 | 189 | 9.5 |  | 340 | bar g | °C | 50 |  | P | 7056
S-01722 | PIC-7094 | U09 | D 7001 Deaerator | D 7001 Top | Low Pressure Steam | 1 | 120 | 3.5 |  | 200 | bar g | °C | 50 |  | P | 7094
S-01722 | PIC-7101 | U09 | D 7001 Deaerator | [9 empty] | 50 |  | P | 7101
S-01722 | PIC-7141 | U11 | Outlet P 7001 A/B/C BFW Pump | 8"-BFW-70-164-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 50 |  | P | 7141
S-01722 | PSAL-2556 | U01 | Fuel Gas to H 2001 | 28"-FG-20-101-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | P | 2556
S-01722 | PSV-1008 | P01 | Natural Gas to E 2006 1st Natural Gas Feed Preheat Coil | 1 1/2"-NG-10-108-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 288 |  | P | 1008
S-01722 | PSV-1009 | P01 | Natural Gas to E 2006 1st Natural Gas Feed Preheat Coil | 1 1/2"-NG-10-109-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 288 |  | P | 1009
S-01722 | PSV-1013 | P01 | Fuel Gas to H 2001 Primary Reformer | 8"-NG-10-110-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 288 |  | P | 1013
S-01722 | PSV-1014 | P01 | Fuel Gas to H 2001 Primary Reformer | 8"-NG-10-111-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 288 |  | P | 1014
S-01722 | PSV-1015 | P01 | D 1001 Natural Gas K.O. Drum | 1 1/2"-NG-10-112-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 288 |  | P | 1015
S-01722 | PSV-1031 | P04 | R 1001 Hydrogenator | 1 1/2"-PRG-10-102-F24-H | Process Gas | 48.8 | 380 | 55 |  | 410 | bar g | °C | 288 |  | P | 1031
S-01722 | PSV-1038 | P04 | Inlet R 1002 1 Sulphur Absorber | 1 1/2"-PRG-10-103-F24-H | Process Gas | 48.3 | 375 | 60 |  | 410 | bar g | °C | 288 |  | P | 1038
S-01722 | PSV-1043 | P04 | Inlet R 1002 2 Sulphur Absorber | 1 1/2"-PRG-10-106-F24-H | Process Gas | 48.3 | 375 | 60 |  | 410 | bar g | °C | 288 |  | P | 1043
S-01722 | PSV-2019 | P02 | D 2011 Steam Condensate K.O. Drum for E 2008 | 2"-HPC-20-104-F24-P | High Pressure Steam Condensate | 43.5 | 257 | 52 |  | 290 | bar g | °C | 288 |  | P | 2019
S-01722 | PSV-2078 | P09 | HP Steam to Steam/NG Mixture | 1 1/2"-HPS-20-103-F24-H | High Pressure Steam | 41.1 | 343 | 52 |  | 410 | bar g | °C | 288 |  | P | 2078
S-01722 | PSV-2121 | P11 | Outlet FT 2002 Steam Turbine for F 2002 | HOLD-LPS-20-104-D24-H | Low Pressure Steam | 7.5 | 194 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 2121
S-01722 | PSV-2122 | P11 | Outlet FT 2002 Steam Turbine for F 2002 | HOLD-LPS-20-105-D24-H | Low Pressure Steam | 7.5 | 194 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 2122
S-01722 | PSV-2171 | P12 | Outlet FT 2001 Steam Turbine for F 2001 | HOLD-LPS-20-107-D24-P | Low Pressure Steam | 7.5 | 204 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 2171
S-01722 | PSV-2172 | P12 | Outlet FT 2001 Steam Turbine for F 2001 | HOLD-LPS-20-108-D24-P | Low Pressure Steam | 7.5 | 204 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 2172
S-01722 | PSV-2354 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-105-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2354
S-01722 | PSV-2355 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-107-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2355
S-01722 | PSV-2356 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-109-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2356
S-01722 | PSV-2357 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-111-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2357
S-01722 | PSV-2358 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-113-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2358
S-01722 | PSV-2359 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-129-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2359
S-01722 | PSV-2360 | P17 | Outlet E 2021 3 Steam Superheater | 10"-RFG-20-130-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 288 |  | P | 2360
S-01722 | PSV-2376 | P18 | D 2001 HHP Steam Drum | D 2001 | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 288 |  | P | 2376
S-01722 | PSV-2377 | P18 | D 2001 HHP Steam Drum | D 2001 | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 288 |  | P | 2377
S-01722 | PSV-2378 | P18 | D 2001 HHP Steam Drum | D 2001 | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 288 |  | P | 2378
S-01722 | PSV-2379 | P18 | D 2001 HHP Steam Drum | D 2001 | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 288 |  | P | 2379
S-01722 | PSV-2380 | P18 | D 2001 HHP Steam Drum | D 2001 | High High Pressure Steam | 102 | 313 | 112 |  | 330 | bar g | °C | 288 |  | P | 2380
S-01722 | PSV-2458 | P20 | Outlet E 2025 DMW Preheater | 3"-DMW-20-102-B50-H | Demineralized Water | 4.5 | 72 | 14 |  | 110 | bar g | °C | 288 |  | P | 2458
S-01722 | PSV-2494 | P21 | Outlet E 2027 Water Cooler | 3"-CWR-20-102-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 2494
S-01722 | PSV-2546 | U01 | Nitrogen from Header | 1 1/2"-N-20-118-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 288 |  | P | 2546
S-01722 | PSV-2555 | U01 | Nitrogen from Header | 1 1/2"-N-20-119-B24-N | Nitrogen Gas | 6 | 40 | 7 |  | 75 | bar g | °C | 288 |  | P | 2555
S-01722 | PSV-2581 | U02 | Outlet C 2001 Start-up Nitrogen Compressor | 6"-N-20-120-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 110 | bar g | °C | 288 |  | P | 2581
S-01722 | PSV-2604 | U17 | H2 Recycle System | 1 1/2"-HG-20-104-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 288 |  | P | 2604
S-01722 | PSV-2605 | U17 | H2 Recycle System | 1 1/2"-HG-20-106-G24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 288 |  | P | 2605
S-01722 | PSV-3021 | P22 | Outlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 1 1/2"-SG-30-132-G40-H | Synthesis Gas | 80 | 74 | 99 |  | 120 | bar g | °C | 288 |  | P | 3021
S-01722 | PSV-3047 | P23 | D 3003 MP Steam Drum | 8"-MPS-30-112-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 288 |  | P | 3047
S-01722 | PSV-3048 | P23 | D 3003 MP Steam Drum | 8"-MPS-30-110-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 288 |  | P | 3048
S-01722 | PSV-3057 | P23 | D 3003 MP Steam Drum | 8"-MPS-30-113-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 288 |  | P | 3057
S-01722 | PSV-3143 | P26 | Outlet E 3003 1 Loop Water Cooler | 6"-CWR-30-103-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 3143
S-01722 | PSV-3146 | P26 | Outlet E 3003 2 Loop Water Cooler | 6"-CWR-30-107-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 3146
S-01722 | PSV-3149 | P26 | Outlet E 3003 3 Loop Water Cooler | 6"-CWR-30-109-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 3149
S-01722 | PSV-3163 | P27 | D 3001 HP Separator | 3"-SG-30-137-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 288 |  | P | 3163
S-01722 | PSV-3173 | P27 | Purge Gas to Fuel Gas Header | 10"-PG-30-105-B24-N | Purge Gas | 4 | 47 | 7 |  | 100 | bar g | °C | 288 |  | P | 3173
S-01722 | PSV-3174 | P27 | Purge Gas to Fuel Gas Header | 10"-PG-30-107-B24-N | Purge Gas | 4 | 47 | 7 |  | 100 | bar g | °C | 288 |  | P | 3174
S-01722 | PSV-3196 | P28 | D 3002 LP Separator | 10"-PG-30-103-B40-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 288 |  | P | 3196
S-01722 | PSV-3197 | P28 | D 3002 LP Separator | 10"-PG-30-109-B40-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 288 |  | P | 3197
S-01722 | PSV-3206 | P28 | D 3002 LP Separator | 10"-PG-30-108-B24-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 288 |  | P | 3206
S-01722 | PSV-5006 | P29 | TK 5001 Raw Methanol Buffer Tank | HOLD-PMV-50-104-B40-N | Methanol Vapour | 0 | 46 | -0.3 |  | 100 | bar g | °C | 288 |  | P | 5006
S-01722 | PSV-5007 | P29 | TK 5001 Raw Methanol Buffer Tank | HOLD-PMV-50-102-B40-N | Methanol Vapour | 0 | 46 | -0.3 |  | 100 | bar g | °C | 288 |  | P | 5007
S-01722 | PSV-5058 | P30 | Outlet T 5001 Stabilizer Column | 10"-PMV-50-111-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 288 |  | P | 5058
S-01722 | PSV-5059 | P30 | Outlet T 5001 Stabilizer Column | 10"-PMV-50-112-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 288 |  | P | 5059
S-01722 | PSV-5060 | P30 | Outlet T 5001 Stabilizer Column | 10"-PMV-50-123-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 288 |  | P | 5060
S-01722 | PSV-5061 | P30 | Outlet T 5001 Stabilizer Column | 10"-PMV-50-124-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 288 |  | P | 5061
S-01722 | PSV-5073 | P31 | D 5009 Steam Condensate K.O. Drum for E 5001 | 1 1/2"-LPS-50-101-B24-P | Low Pressure Steam | 2.4 | 138 | 9.5 |  | 190 | bar g | °C | 288 |  | P | 5073
S-01722 | PSV-5085 | P31 | Outlet E 7003 A Excess Steam Condensate Cooler | 3/4"-CWR-70-125-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5085
S-01722 | PSV-5108 | P32 | Outlet E 5010 OH Gas Condenser | 3/4"-CWR-50-102-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5108
S-01722 | PSV-5179 | P34 | Outlet T 5002 LP Methanol Column | 6"-PMV-50-131-B24-P | Methanol Vapour | 0.1 | 67 | 3.5 |  | 150 | bar g | °C | 288 |  | P | 5179
S-01722 | PSV-5180 | P34 | Outlet T 5002 LP Methanol Column | 6"-PMV-50-132-N24-P | Methanol Vapour | 0.1 | 67 | 3.5 |  | 150 | bar g | °C | 288 |  | P | 5180
S-01722 | PSV-5220 | P36 | Outlet E 5008 Methanol Product Cooler No. 1 | 3/4"-CWR-50-105-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5220
S-01722 | PSV-5236 | U15 | Outlet P 5080 A Morpholine Dosing Pump | 1 1/2"-MOR-70-101-B40-N | Morpholine | 2 | 35 | 7 |  | 65 | bar g | °C | 288 |  | P | 5236
S-01722 | PSV-5239 | U15 | Outlet P 5080 B Morpholine Dosing Pump | 1 1/2"-MOR-70-101-B40-N | Morpholine | 2 | 35 | 7 |  | 65 | bar g | °C | 288 |  | P | 5239
S-01722 | PSV-5250 | P38 | Outlet T 5003 MP Methanol Column | 10"-PMV-50-151-B24-H | Methanol Vapour | 2.7 | 102 | 6 |  | 165 | bar g | °C | 288 |  | P | 5250
S-01722 | PSV-5251 | P38 | Outlet T 5003 MP Methanol Column | 10"-PMV-50-152-B24-H | Methanol Vapour | 2.7 | 102 | 6 |  | 165 | bar g | °C | 288 |  | P | 5251
S-01722 | PSV-5261 | P38 | Outlet T 5003 MP Methanol Column | 10"-PMV-50-193-B24-H | Methanol Vapour | 2.7 | 102 | 6 |  | 165 | bar g | °C | 288 |  | P | 5261
S-01722 | PSV-5308 | P39 | Outlet E 7003 B Excess Steam Condensate Cooler | 3/4"-CWR-50-128-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5308
S-01722 | PSV-5339 | P40 | Outlet E 5012 Methanol Product Cooler No. 2 | 3/4"-CWR-50-108-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5339
S-01722 | PSV-5370 | P41 | Outlet E 5007 Wash Water Cooler | 3/4"-CWR-50-110-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5370
S-01722 | PSV-5384 | P42 | X 5001 A Product Polisher Unit | 3"-PMP-50-180-D24-N | Methanol | 3 | 48 | 19 |  | 75 | bar g | °C | 288 |  | P | 5384
S-01722 | PSV-5386 | P42 | X 5001 B Product Polisher Unit | 3"-PMP-50-194-D24-N | Methanol | 3 | 48 | 19 |  | 75 | bar g | °C | 288 |  | P | 5386
S-01722 | PSV-5400 | P43 | TK 5002 1 Methanol Product Buffer Tank | HOLD-PMV-50-181-B24-H | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 85 | bar g | °C | 288 |  | P | 5400
S-01722 | PSV-5401 | P43 | TK 5002 1 Methanol Product Buffer Tank | HOLD-PMV-50-182-B24-H | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 85 | bar g | °C | 288 |  | P | 5401
S-01722 | PSV-5405 | P43 | Outlet P 5012 Methanol Start-up Pump | HOLD-PMP-50-162-F24-N | Methanol Product | 47 | 48 | 52 |  | 75 | bar g | °C | 288 |  | P | 5405
S-01722 | PSV-5417 | P44 | TK 5002 2 Methanol Product Buffer Tank | HOLD-PMV-50-183-B24-H | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 85 | bar g | °C | 288 |  | P | 5417
S-01722 | PSV-5418 | P44 | TK 5002 2 Methanol Product Buffer Tank | HOLD-PMV-50-184-B24-H | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 85 | bar g | °C | 288 |  | P | 5418
S-01722 | PSV-5444 | P45 | Outlet E 5011 Liquid Off-stream Cooler | 3/4"-CWR-50-114-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5444
S-01722 | PSV-5450 | P45 | TK 5003 Liquid Off-stream Tank | HOLD-PMV-50-190-B24-H | Nitrogen / Methanol vapour | 0.01 | 48 | -0.3 |  | 85 | bar g | °C | 288 |  | P | 5450
S-01722 | PSV-5451 | P45 | TK 5003 Liquid Off-stream Tank | HOLD-PMV-50-191-B24-H | Nitrogen / Methanol vapour | 0.01 | 48 | -0.3 |  | 85 | bar g | °C | 288 |  | P | 5451
S-01722 | PSV-5461 | P45 | Outlet P 5009 A Liquid Off-stream Pump | 2"-LOS-50-122-F24-N | Liquid Off-stream | 53 | 50 | 60 |  | 75 | bar g | °C | 288 |  | P | 5461
S-01722 | PSV-5462 | P45 | Outlet P 5009 B Liquid Off-stream Pump | 2"-LOS-50-123-F24-N | Liquid Off-stream | 53 | 50 | 60 |  | 75 | bar g | °C | 288 |  | P | 5462
S-01722 | PSV-5501 | U23A | Outlet E 5015 Excess Water Cooler (optional) | 3/4"-CWR-50-119-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5501
S-01722 | PSV-5505 | U23A | E 5014 Feed/Effluent Exchanger (Optional) | 6"-PMW-50-142-B24-N | Methanol Water | 1.5 | 62 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 5505
S-01722 | PSV-5512 | U24 | Outlet P 5070 A NaOH Solution Dosing Pump (optional) | 1 1/2"-NS-50-101-B40-N | NaOH Solution | 2 | 35 | 7 |  | 75 | bar g | °C | 288 |  | P | 5512
S-01722 | PSV-5514 | U24 | Outlet P 5070 A NaOH Solution Dosing Pump (optional) | 1 1/2"-NS-50-101-B40-N | NaOH Solution | 2 | 35 | 7 |  | 75 | bar g | °C | 288 |  | P | 5514
S-01722 | PSV-6021 | P06 | BFW Make-up to T 6001 Saturator | 1 1/2"-PRC-60-196-G40-H | Boiler Feed Water | 44 | 119 | 71 |  | 180 | bar g | °C | 288 |  | P | 6021
S-01722 | PSV-6022 | P06 | BFW Make-up to T 6001 Saturator | 1 1/2"-PRC-60-195-G40-H | Boiler Feed Water | 44 | 119 | 71 |  | 180 | bar g | °C | 288 |  | P | 6022
S-01722 | PSV-6027 | P06 | Inlet T 6001 Saturator | 1 1/2"-MPS-60-103-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 288 |  | P | 6027
S-01722 | PSV-6053 | P07 | D 6001 Feed Gas Separator | 1 1/2"-PRG-60-124-F24-H | Process Gas | 42.8 | 226 | 55 |  | 290 | bar g | °C | 288 |  | P | 6053
S-01722 | PSV-6056 | P07 | Natural Gas from R 1002 2 Sulphur Absorber | 1 1/2"-PRG-10-125-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 288 |  | P | 6056
S-01722 | PSV-6085 | P08 | Outlet E 6003 Saturator Blow Down Cooler | 3/4"-CWR-60-102-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 6085
S-01722 | PSV-7010 | U03 | HP Steam Header | 10"-HPS-70-110-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 470 | bar g | °C | 288 |  | P | 7010
S-01722 | PSV-7011 | U03 | HP Steam Header | 10"-HPS-70-112-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 470 | bar g | °C | 288 |  | P | 7011
S-01722 | PSV-7012 | U03 | HP Steam Header | 10"-HPS-70-114-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 470 | bar g | °C | 288 |  | P | 7012
S-01722 | PSV-7013 | U03 | Pressure Reducing Desuperheating Station | 2"-BFW-70-106-H34-H | Boiler Feed Water |  | 122 | 170 |  | 353 | bar g | °C | 288 |  | P | 7013
S-01722 | PSV-7014 | U03 | Pressure Reducing Desuperheating Station | 3"-BFW-70-144-H34-H | Boiler Feed Water |  | 122 | 170 |  | 353 | bar g | °C | 288 |  | P | 7014
S-01722 | PSV-7015 | U03 | Pressure Reducing Desuperheating Station | 3"-BFW-70-142-H34-H | Boiler Feed Water |  | 122 | 170 |  | 353 | bar g | °C | 288 |  | P | 7015
S-01722 | PSV-7016 | U04 | Pressure Reducing Desuperheating Station | 2"-BFW-70-158-H34-H | Boiler Feed Water |  | 122 | 170 |  | 353 | bar g | °C | 288 |  | P | 7016
S-01722 | PSV-7017 | U04 | Pressure Reducing Desuperheating Station | 2"-BFW-70-157-H34-H | Boiler Feed Water |  | 122 | 170 |  | 353 | bar g | °C | 288 |  | P | 7017
S-01722 | PSV-7023 | U04 | HP Steam Header | 10"-HPS-70-134-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 288 |  | P | 7023
S-01722 | PSV-7024 | U04 | HP Steam Header | 10"-HPS-70-135-F34-H | High Pressure Steam | 44 | 410 | 52 |  | 470 | bar g | °C | 288 |  | P | 7024
S-01722 | PSV-7032 | U05 | Pressure Reducing Desuperheating Station | 2"-BFW-70-109-F24-H | Boiler Feed Water |  | 122 | 80 |  | 296 | bar g | °C | 288 |  | P | 7032
S-01722 | PSV-7033 | U05 | Pressure Reducing Desuperheating Station | 2"-BFW-70-111-F24-H | Boiler Feed Water |  | 122 | 80 |  | 296 | bar g | °C | 288 |  | P | 7033
S-01722 | PSV-7036 | U05 | MP Steam Header | 1 1/2"-MPS-70-122-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 288 |  | P | 7036
S-01722 | PSV-7037 | U05 | MP Steam Header | 1 1/2"-MPS-70-123-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 288 |  | P | 7037
S-01722 | PSV-7052 | U06 | Pressure Reducing Desuperheating Station | 2"-BFW-70-122-F24-H | Boiler Feed Water |  | 122 | 80 |  | 296 | bar g | °C | 288 |  | P | 7052
S-01722 | PSV-7053 | U06 | Pressure Reducing Desuperheating Station | 2"-BFW-70-123-F24-H | Boiler Feed Water |  | 122 | 80 |  | 296 | bar g | °C | 288 |  | P | 7053
S-01722 | PSV-7057 | U06 | LP Steam Header | 10"-LPS-70-111-D24-P | Low Pressure Steam | 7 | 230 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7057
S-01722 | PSV-7058 | U06 | LP Steam Header | 10"-LPS-70-110-D24-P | Low Pressure Steam | 7 | 230 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7058
S-01722 | PSV-7059 | U06 | LP Steam Header | 10"-LPS-70-113-D24-P | Low Pressure Steam | 7 | 230 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7059
S-01722 | PSV-7060 | U06 | LP Steam Header | 10"-LPS-70-141-D24-P | Low Pressure Steam | 7 | 230 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7060
S-01722 | PSV-7061 | U06 | LP Steam Header | 10"-LPS-70-140-D24-P | Low Pressure Steam | 7 | 230 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7061
S-01722 | PSV-7072 | U07 | BFW from Header | 2"-BFW-70-124-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 288 |  | P | 7072
S-01722 | PSV-7073 | U07 | BFW from Header | 2"-BFW-70-145-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 288 |  | P | 7073
S-01722 | PSV-7095 | U09 | D 7001 Deaerator | 10"-LPS-70-132-B24-H | Low Pressure Steam | 1 | 120 | 3.5 |  | 340 | bar g | °C | 288 |  | P | 7095
S-01722 | PSV-7096 | U09 | D 7001 Deaerator | 10"-LPS-70-133-B24-H | Low Pressure Steam | 1 | 120 | 3.5 |  | 340 | bar g | °C | 288 |  | P | 7096
S-01722 | PSV-7097 | U09 | D 7001 Deaerator | 10"-LPS-70-197-B24-H | Low Pressure Steam | 1 | 120 | 3.5 |  | 340 | bar g | °C | 288 |  | P | 7097
S-01722 | PSV-7104 | U22 | Outlet P 7004 A Excess Process Condensate Pump | 1 1/2"-PRC-70-197-G40-N | Process Condensate | 46 | 65 | 71 |  | 100 | bar g | °C | 288 |  | P | 7104
S-01722 | PSV-7107 | U22 | Outlet P 7004 B Excess Process Condensate Pump | 1 1/2"-PRC-70-199-G40-N | Process Condensate | 45 | 65 | 71 |  | 100 | bar g | °C | 288 |  | P | 7107
S-01722 | PSV-7130 | U10 | Inlet P 7001 A BFW Pump | 14"-BFW-70-151-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 288 |  | P | 7130
S-01722 | PSV-7131 | U10 | Inlet P 7001 B BFW Pump | 14"-BFW-70-135-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 288 |  | P | 7131
S-01722 | PSV-7132 | U10 | LP Steam from FP 7001 A Steam Turbine for P 7001 A | HOLD-LPS-70-120-D24-P | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7132
S-01722 | PSV-7134 | U10 | FP 7001 A Steam Turbine for P 7001 A | HOLD-LPS-70-122-D24-P | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7134
S-01722 | PSV-7135 | U10 | Inlet P 7001 C BFW Pump | 14"-BFW-70-136-B24-H | Boiler Feed Water | 1 | 120 | 4.5 |  | 160 | bar g | °C | 288 |  | P | 7135
S-01722 | PSV-7136 | U10 | FP 7001 B Steam Turbine for P 7001 B | HOLD-LPS-70-124-D24-P | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7136
S-01722 | PSV-7137 | U10 | LP Steam from FP 7001 B Steam Turbine for FP 7001 B | HOLD-LPS-70-123-D24-P | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7137
S-01722 | PSV-7142 | U11 | HHP BFW To HP BFW Header | BFW-70-165-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 288 |  | P | 7142
S-01722 | PSV-7143 | U11 | HHP BFW To HP BFW Header | BFW-70-167-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 288 |  | P | 7143
S-01722 | PSV-7165 | U12 | Outlet P 7051 A Phosphate Dosing Pump | 1 1/2"-PH-70-101-H40-N | Phosphate | 103 | 35 | 114 |  | 75 | bar g | °C | 288 |  | P | 7165
S-01722 | PSV-7168 | U12 | Outlet P 7051 B Phosphate Dosing Pump | 1 1/2"-PH-70-101-H40-N | Phosphate | 103 | 35 | 114 |  | 75 | bar g | °C | 288 |  | P | 7168
S-01722 | PSV-7171 | U12 | Outlet P 7052 A Phosphate Dosing Pump | 1 1/2"-PH-70-102-F40-H | Phosphate | 35 | 35 | 47 |  | 75 | bar g | °C | 288 |  | P | 7171
S-01722 | PSV-7174 | U12 | Outlet P 7052 B Phosphate Dosing Pump | 1 1/2"-PH-70-102-F40-H | Phosphate | 35 | 35 | 47 |  | 75 | bar g | °C | 288 |  | P | 7174
S-01722 | PSV-7195 | U13 | Outlet P 7060 A Ammonia Dosing Pump | 1 1/2"-AM-70-101-B40-H | Ammonia | 2 | 35 | 7 |  | 75 | bar g | °C | 288 |  | P | 7195
S-01722 | PSV-7198 | U13 | Outlet P 7060 B Ammonia Dosing Pump | 1 1/2"-AM-70-101-B40-H | Ammonia | 2 | 35 | 7 |  | 75 | bar g | °C | 288 |  | P | 7198
S-01722 | PSV-7215 | U14 | Outlet P 7070 A Oxygen Scavenger Dosing Pump | 1 1/2"-HZ-70-101-B40-N | Oxygen Scavenger | 2 | 35 | 7 |  | 75 | bar g | °C | 288 |  | P | 7215
S-01722 | PSV-7218 | U14 | Outlet P 7070 B Oxygen Scavenger Dosing Pump | 1 1/2"-HZ-70-101-B40-N | Oxygen Scavenger | 2 | 35 | 7 |  | 75 | bar g | °C | 288 |  | P | 7218
S-01722 | PSV-7253 | U16 | Outlet D 7002 Continuous Blow Down Drum | 4"-LPS-70-134-D24-P | Low Pressure Steam | 7.5 | 173 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7253
S-01722 | PSV-7254 | U16 | Outlet D 7002 Continuous Blow Down Drum | 4"-LPS-70-135-D24-P | Low Pressure Steam | 7.5 | 173 | 9.5 |  | 340 | bar g | °C | 288 |  | P | 7254
S-01722 | PSV-7256 | U16 | Outlet E 7001 Blow-down Cooler for D 7003 | 3/4"-CWR-70-102-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 288 |  | P | 7256
S-01722 | PV-1006 | P01 | Outlet D 1001 Natural Gas K.O. Drum | 14"-NG-10-102-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 243 |  | P | 1006
S-01722 | PV-1011 | P01 | Fuel Gas to H 2001 Primary Reformer | 8"-NG-20-101-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 243 |  | P | 1011
S-01722 | PV-1045 | P04 | Outlet R 1002 2 Sulphur Absorber, Vent | 8"-PRG-10-108-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 243 |  | P | 1045
S-01722 | PV-2015 | P02 | HP Steam from Header | 6"-HPS-70-126-F24-H | High Pressure Steam | 44 | 272 | 52 |  | 310 | bar g | °C | 243 |  | P | 2015
S-01722 | PV-2073 | P09 | Saturated Natural Gas to Steam/NG Mixture, Vent | 12"-PRG-20-111-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 243 |  | P | 2073
S-01722 | PV-2361 | P17 | Outlet E 2021 1&2 Steam Superheater, Vent | 8"-HHPS-20-2054-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 243 |  | P | 2361
S-01722 | PV-2363 | P17 | Outlet E 2021 1&2 Steam Superheater | 24"-HHPS-20-115-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 243 |  | P | 2363
S-01722 | PV-2406 | P19 | Outlet D 2002 1st Separator, Vent | 18"-RFG-20-118-D40-H | Reformed Gas | 25.8 | 165 | 29 |  | 200 | bar g | °C | 243 |  | P | 2406
S-01722 | PV-2481 | P21 | Outlet D 2005 Final Separator, Vent | 18"-SG-20-105-D40-ET | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 243 |  | P | 2481
S-01722 | PV-2536 | U01 | Purge Gas to Mixing Point, Vent | 14"-PG-20-129-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 243 |  | P | 2536
S-01722 | PV-2603 | U17 | Import H2 | 3"-HG-20-102-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 243 |  | P | 2603
S-01722 | PV-2608 | U17 | Recycle Hydrogen from Loop | 3"-SG-30-128-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 243 |  | P | 2608
S-01722 | PV-3042 | P23 | Outlet D 3003 MP Steam Drum | 24"-MPS-30-114-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 243 |  | P | 3042
S-01722 | PV-3166 | P27 | Outlet D 3001 HP Separator, Vent | 4"-SG-30-141-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 243 |  | P | 3166
S-01722 | PV-3194 | P28 | Outlet D 3002 LP Separator | 8"-PG-30-102-B40-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 243 |  | P | 3194
S-01722 | PV-5069 | P31 | Inlet E 5001 Stabilizer Column Steam Reboiler | 14"-LPS-70-104-D24-H | Low Pressure Steam | 7 | 188 | 9.5 |  | 340 | bar g | °C | 243 |  | P | 5069
S-01722 | PV-5091/A | P32 | Nitrogen from Header | 2"-N-50-104-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | P | 5091 | A
S-01722 | PV-5091/B | P32 | Off-Gas to J 3001 | 6"-PG-50-101-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 243 |  | P | 5091 | B
S-01722 | PV-5109 | P32 | Outlet E 5010 OH Gas Condenser, Vent | 4"-PG-50-103-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 243 |  | P | 5109
S-01722 | PV-5207/A | P36 | Inlet D 5002 LP Column OH Accumulator | 2"-N-50-107-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 243 |  | P | 5207 | A
S-01722 | PV-5207/B | P36 | Inlet D 5002 LP Column OH Accumulator, Vent | 2"-VA-50-101-B24-P | Vent to Atmosphere | 0 | 65 | 3.5 |  | 150 | bar g | °C | 243 |  | P | 5207 | B
S-01722 | PV-6025 | P06 | MP Steam from Loop Header | 24"-MPS-70-101-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 243 |  | P | 6025
S-01722 | PV-7002/A | U03 | Pressure Reducing Desuperheating Station | 10"-HHPS-70-115-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 243 |  | P | 7002 | A
S-01722 | PV-7002/B | U03 | Pressure Reducing Desuperheating Station | 24"-HHPS-70-114-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 243 |  | P | 7002 | B
S-01722 | PV-7002/C | U03 | Pressure Reducing Desuperheating Station | 24"-HHPS-70-113-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 243 |  | P | 7002 | C
S-01722 | PV-7004 | U03 | HP Steam Header, Vent | 16"-HPS-70-108-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | P | 7004
S-01722 | PV-7025/A | U04 | Pressure Reducing Desuperheating Station | 18"-HHPS-70-121-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 243 |  | P | 7025 | A
S-01722 | PV-7025/B | U04 | Pressure Reducing Desuperheating Station | 18"-HHPS-70-120-H34-H | High High Pressure Steam | 98 | 454 | 112 |  | 490 | bar g | °C | 243 |  | P | 7025 | B
S-01722 | PV-7028 | U04 | HP Import Steam to Header | 24"-HPS-70-107-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 243 |  | P | 7028
S-01722 | PV-7031/A | U05 | Pressure Reducing Desuperheating Station | 24"-HPS-70-130-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | P | 7031 | A
S-01722 | PV-7031/B | U05 | Pressure Reducing Desuperheating Station | 24"-HPS-70-131-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | P | 7031 | B
S-01722 | PV-7031/C | U05 | MP Steam to LP Steam Header | 10"-MPS-70-115-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 243 |  | P | 7031 | C
S-01722 | PV-7031/D | U05 | MP Steam to LP Steam Header | 10"-MPS-70-103-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 243 |  | P | 7031 | D
S-01722 | PV-7034 | U05 | MP Steam Header, Vent | 14"-MPS-70-121-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 243 |  | P | 7034
S-01722 | PV-7051/A | U06 | Pressure Reducing Desuperheating Station | 16"-HPS-70-120-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | P | 7051 | A
S-01722 | PV-7051/B | U06 | Pressure Reducing Desuperheating Station | 16"-HPS-70-121-F34-H | High Pressure Steam | 44 | 345 | 52 |  | 470 | bar g | °C | 243 |  | P | 7051 | B
S-01722 | PV-7056 | U06 | LP Steam, Vent | 24"-LPS-70-109-D24-P | Low Pressure Steam | 7 | 188 | 9.5 |  | 340 | bar g | °C | 243 |  | P | 7056
S-01722 | PV-7094 | U09 | LP Steam to D 7001 Deaerator | 18"-LPS-70-127-D24-H | Low Pressure Steam | 7 | 188 | 9.5 |  | 340 | bar g | °C | 243 |  | P | 7094
S-01722 | PV-7101 | U09 | D 7001 Deaerator, Vent | 24"-VA-70-161-B24-P | Steam | 1 | 120 | 3.5 |  | 340 | bar g | °C | 243 |  | P | 7101
S-01722 | QIC-2535 | U01 | Total Duty | [9 empty] | 50 |  | Q | 2535
S-01722 | SC-7131 | U10 | FP 7001 A Steam Turbine for P 7001 A | [9 empty] | 50 |  | S | 7131
S-01722 | SC-7136 | U10 | FP 7001 B Steam Turbine for P 7001 B | [9 empty] | 50 |  | S | 7136
S-01722 | SC-7193 | U13 | P 7060 A Ammonia Dosing Pump | [9 empty] | 50 |  | S | 7193
S-01722 | SC-7196 | U13 | P 7060 B Ammonia Dosing Pump | [9 empty] | 50 |  | S | 7196
S-01722 | SI-2118 | P11 | FT 2002 Steam Turbine for F 2002 | [9 empty] | 50 |  | S | 2118
S-01722 | SI-2168 | P12 | FT 2001 Steam Turbine for F 2001 | [9 empty] | 50 |  | S | 2168
S-01722 | SIC-2119 | P11 | FT 2002 Steam Turbine for F 2002 | [9 empty] | 50 |  | S | 2119
S-01722 | SIC-2167 | P12 | FT 2001 Steam Turbine for F 2001 | [9 empty] | 50 |  | S | 2167
S-01722 | TG-1002 | P01 | Natural Gas from BL | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | T | 1002
S-01722 | TG-2002 | P02 | Process Oxygen from BL | 10"-PO-20-110-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | T | 2002
S-01722 | TG-2011 | P02 | Inlet E 2008 Oxygen Preheater | 12"-PO-20-102-F70-N | Process Oxygen | 35 | 35 | 47 |  | 85 | bar g | °C | 50 |  | T | 2011
S-01722 | TG-2012 | P02 | Inlet E 2008 Oxygen Preheater | 6"-HPS-20-102-F24-H | High Pressure Steam | 43.5 | 272 | 52 |  | 310 | bar g | °C | 50 |  | T | 2012
S-01722 | TG-2013 | P02 | Outlet E 2008 Oxygen Preheater | 6"-HPC-20-101-F24-H | High Pressure Steam Condensate | 43.5 | 257 | 53 |  | 290 | bar g | °C | 50 |  | T | 2013
S-01722 | TG-2116 | P11 | HP Steam to FT 2002 Steam Turbine for F 2002 | 8"-HPS-70-101-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 2116
S-01722 | TG-2120 | P11 | LP Steam from FT 2002 Steam Turbine for F 2002 | 16"-LPS-20-102-D24-H | Low Pressure Steam | 7.5 | 194 | 9.5 |  | 340 | bar g | °C | 50 |  | T | 2120
S-01722 | TG-2164 | P12 | HP Steam to FT 2001 Steam Turbine for F 2001 | 6"-HPS-70-111-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 2164
S-01722 | TG-2170 | P12 | LP Steam from FT 2001 Steam Turbine for F 2001 | 12"-LPS-20-106-D24-H | Low Pressure Steam | 7.5 | 204 | 9.5 |  | 340 | bar g | °C | 50 |  | T | 2170
S-01722 | TG-2401 | P19 | Outlet E 2022 1 BFW Preheater | 24"-RFG | Reformed Gas | 25.8 | 251 | 29 |  | 280 | bar g | °C | 50 |  | T | 2401
S-01722 | TG-2403 | P19 | Outlet E 2022 2 BFW Preheater | 24"-RFG | Reformed Gas | 25.8 | 208 | 29 |  | 280 | bar g | °C | 50 |  | T | 2403
S-01722 | TG-2404 | P19 | Outlet E 2022 3 BFW Preheater | 12"-BFW | Boiler Feed Water | 104 | 166 | 113 |  | 310 | bar g | °C | 50 |  | T | 2404
S-01722 | TG-2405 | P19 | Outlet E 2022 2 BFW Preheater | 12"-BFW | Boiler Feed Water | 104 | 210 | 113 |  | 310 | bar g | °C | 50 |  | T | 2405
S-01722 | TG-2454 | P20 | DMW from BL | 10"-DMW-20-101-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | T | 2454
S-01722 | TG-2456 | P20 | Outlet E 2025 DMW Preheater | 10"-DMW-20-104-B50-H | Demineralized Water | 4.5 | 72 | 14 |  | 110 | bar g | °C | 50 |  | T | 2456
S-01722 | TG-2494 | P21 | Outlet E 2027 Water Cooler | 12"-CWR-20-101-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 2494
S-01722 | TG-2574 | U02 | Inlet C 2001 Start-up Nitrogen Compressor | 10"-N-20-110-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | T | 2574
S-01722 | TG-3025 | P22 | Outlet C 3001/C 3002 Synthesis Gas Compressor/Recirculator | 20"-CWR-30-101-B24-N | Cooling Water Return | 1.5 | 48 | 7 |  | 100 | bar g | °C | 50 |  | T | 3025
S-01722 | TG-3051 | P23 | Outlet D 3003 MP Steam Drum | Downcomers | Blow-down | 35 | 242 | 47 |  | 265 | bar g | °C | 50 |  | T | 3051
S-01722 | TG-3074 | P24 | Outlet R 3001 1 Methanol Reactor | 24"-SG-30-111-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | T | 3074
S-01722 | TG-3078 | P24 | Outlet R 3001 2 Methanol Reactor | 24"-SG-30-108-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | T | 3078
S-01722 | TG-3082 | P24 | Outlet R 3001 3 Methanol Reactor | 24"-SG-30-120-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | T | 3082
S-01722 | TG-3085 | P24 | Outlet J 3002 1 Start-up Ejector | 16"-MPS-30-132-F24-H | Medium Pressure Steam | 28 | 230 | 46.5 |  | 260 | bar g | °C | 50 |  | T | 3085
S-01722 | TG-3086 | P24 | Outlet R 3001 1 Methanol Reactor | 16"-MPC-30-131-F24-H | Medium Pressure Steam | 28 | 230 | 46.5 |  | 260 | bar g | °C | 50 |  | T | 3086
S-01722 | TG-3088 | P24 | Outlet J 3002 2 Start-up Ejector | 16"-MPS-30-128-F24-H | Medium Pressure Steam | 28 | 230 | 46.5 |  | 260 | bar g | °C | 50 |  | T | 3088
S-01722 | TG-3089 | P24 | Outlet R 3001 2 Methanol Reactor | 16"-MPC-30-127-F24-H | Medium Pressure Steam | 28 | 230 | 46.5 |  | 260 | bar g | °C | 50 |  | T | 3089
S-01722 | TG-3091 | P24 | Outlet J 3002 3 Start-up Ejector | 16"-MPS-30-123-F24-H | Medium Pressure Steam | 28 | 230 | 46.5 |  | 260 | bar g | °C | 50 |  | T | 3091
S-01722 | TG-3092 | P24 | Outlet R 3001 3 Methanol Reactor | 16"-MPC-30-122-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 280 | bar g | °C | 50 |  | T | 3092
S-01722 | TG-3143 | P26 | Outlet E 3003 1 Loop Water Cooler | 24"-CWR-30-102-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 3143
S-01722 | TG-3146 | P26 | Outlet E 3003 2 Loop Water Cooler | 14"-CWR-30-106-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 3146
S-01722 | TG-3149 | P26 | Outlet E 3003 3 Loop Water Cooler | 14"-CWR-30-105-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 3149
S-01722 | TG-5008 | P29 | TK 5001 Raw Methanol Buffer Tank | TK 5001 | Raw Methanol | 0 | 46 | -0.3 |  | 100 | mbar g | °C | 50 |  | T | 5008
S-01722 | TG-5108 | P32 | Outlet E 5010 OH Gas Condenser | 3"-CWR-50-101-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5108
S-01722 | TG-5220 | P36 | Outlet E 5008 Methanol Product Cooler No. 1 | 6"-CWR-50-104-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5220
S-01722 | TG-5276 | P38 | Outlet E 2023 MP Column Reboiler No. 2 | 34"-RFG-20-121-D40-H | Reformed Gas | 25.3 | 159 | 29 |  | 200 | bar g | °C | 50 |  | T | 5276
S-01722 | TG-5339 | P40 | Outlet E 5012 Methanol Product Cooler No. 2 | 10"-CWR-50-103-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5339
S-01722 | TG-5370 | P41 | Outlet E 5007 Wash Water Cooler | 3"-CWR-50-112-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5370
S-01722 | TG-5394 | P43 | TK 5002 1 Methanol Product Buffer Tank | TK 5002 1 | Methanol Product | 0 | 48 | -0.03 |  | 85 | bar g | °C | 50 |  | T | 5394
S-01722 | TG-5411 | P44 | TK 5002 2 Methanol Product Buffer Tank | TK 5002 2 | Methanol Product | 0 | 48 | -0.3 |  | 85 | bar g | °C | 50 |  | T | 5411
S-01722 | TG-5444 | P45 | Outlet E 5011 Liquid Off-stream Cooler | 3"-CWR-50-115-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5444
S-01722 | TG-5445 | P45 | TK 5003 Liquid Off-stream Tank | TK 5003 | Nitrogen / Methanol vapour | 0 | 48 | -0.3 |  | 100 | bar g | °C | 50 |  | T | 5445
S-01722 | TG-5501 | U23A | Outlet E 5015 Excess Water Cooler (optional) | 4"-CWR-50-118-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5501
S-01722 | TG-6082 | P08 | Outlet E 6002 Process Condensate Preheater | 4"-PRC-60-108-G40-H | Process Condensate | 45 | 63 | 63 |  | 150 | bar g | °C | 50 |  | T | 6082
S-01722 | TG-6083 | P08 | Outlet E 6002 Process Condensate Preheater | 4"-BD-60-109-G40-P | Boiler Blow-down | 44 | 78 | 57 |  | 260 | bar g | °C | 50 |  | T | 6083
S-01722 | TG-6085 | P08 | Outlet E 6003 Saturator Blow Down Cooler | 3"-CWR-60-101-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 6085
S-01722 | TG-6086 | P08 | D 6002 Saturator Blow Down Drum | D 6002 | Boiler Blow-down | 0 | 100 | 3.5 |  | 125 | bar g | °C | 50 |  | T | 6086
S-01722 | TG-7008 | U03 | HP Steam Header | 28"-HPS-70-116-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 7008
S-01722 | TG-7022 | U04 | HP Steam Export/Import | 24"-HPS-70-107-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | T | 7022
S-01722 | TG-7128 | U10 | HP Steam to FP 7001 A Steam Turbine for FP 7001 A | 8"-HPS-70-117-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 7128
S-01722 | TG-7133 | U10 | HP Steam to FP 7001 B Steam Turbine for FP 7001 B | 8"-HPS-70-118-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 7133
S-01722 | TG-7138 | U10 | LP Steam from FP 7001 A Steam Turbine for FP 7001 A | 14"-LPS-70-121-D24-H | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 50 |  | T | 7138
S-01722 | TG-7139 | U10 | LP Steam from FP 7001 B Steam Turbine for FP 7001 B | 14"-LPS-70-125-D24-H | Low Pressure Steam | 7.5 | 191 | 9.5 |  | 340 | bar g | °C | 50 |  | T | 7139
S-01722 | TG-7256 | U16 | Outlet E 7001 Blow-down Cooler for D 7003 | 4"-CWR-70-101-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 7256
S-01722 | TI-1001 | P01 | Natural Gas from BL | 14"-NG-10-101-F24-N | Natural Gas | 52 | 40 | 60 |  | 85 | bar g | °C | 50 |  | T | 1001
S-01722 | TI-1010 | P01 | Fuel Gas to H 2001 Primary Reformer | 8"-NG-20-101-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 50 |  | T | 1010
S-01722 | TI-1012 | P01 | Fuel Gas to H 2001 Primary Reformer | 24"-NG-20-102-B24-N | Natural Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 50 |  | T | 1012
S-01722 | TI-1034 | P04 | R 1001 Hydrogenator | R 1001 | Process Gas | 48.8 | 380 | 55 |  | 410 | bar g | °C | 50 |  | T | 1034
S-01722 | TI-1035 | P04 | R 1001 Hydrogenator | R 1001 | Process Gas | 48.8 | 380 | 55 |  | 410 | bar g | °C | 50 |  | T | 1035
S-01722 | TI-1037 | P04 | Outlet R 1001 Hydrogenator | 16"-PRG-10-101-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | T | 1037
S-01722 | TI-1041 | P04 | Outlet R 1002 1 Sulphur Absorber | 16"-PRG-10-105-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | T | 1041
S-01722 | TI-1042 | P04 | Inlet R 1002 2 Sulphur Absorber | 16"-PRG-10-105-F24-H | Process Gas | 48.3 | 375 | 55 |  | 410 | bar g | °C | 50 |  | T | 1042
S-01722 | TI-1045 | P04 | Outlet R 1002 2 Sulphur Absorber | 16"-PRG-10-107-F24-H | Process Gas | 47.3 | 365 | 55 |  | 410 | bar g | °C | 50 |  | T | 1045
S-01722 | TI-1047 | P04 | Outlet R 1002 2 Sulphur Absorber, Vent | 8"-FLG-10-113-B24-P | Flare/Vent Gas |  |  | 5 |  | 410 | bar g | °C | 50 |  | T | 1047
S-01722 | TI-2001 | P02 | Process Oxygen from BL | 10"-PO-20-110-F50-N | Process Oxygen | 40 | 35 | 47 |  | 85 | bar g | °C | 50 |  | T | 2001
S-01722 | TI-2003 | P02 | Outlet E 2008 Oxygen Preheater | 6"-HPC-20-101-F24-H | High Pressure Steam Condensate | 43.5 | 257 | 53 |  | 290 | bar g | °C | 50 |  | T | 2003
S-01722 | TI-2039 | P03 | HP Steam to Mixing Point | 4"-HPS-20-109-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 2039
S-01722 | TI-2044 | P03 | Process Oxygen to Mixing Point, Vent | 6"-VA-20-104-F70-P | Vent to Atmosphere |  |  | 45 |  | 255 | bar g | °C | 50 |  | T | 2044
S-01722 | TI-2046 | P03 | Process Oxygen/Steam to R 2004 Secondary Reformer | 18"-PO-20-116-F50-H | Process Oxygen | 34 | 236 | 47 |  | 270 | bar g | °C | 50 |  | T | 2046
S-01722 | TI-2047 | P03 | Process Oxygen to Mixing Point | 16"-PO-20-114-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 50 |  | T | 2047
S-01722 | TI-2050 | P03 | Process Oxygen to Mixing Point, Vent | 2"-VA-20-101-F70-P | Vent to Atmosphere |  |  | 4.5 |  | 255 | bar g | °C | 50 |  | T | 2050
S-01722 | TI-2061 | P09 | Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-60-104-F24-H | Process Gas | 42.3 | 262 | 55 |  | 290 | bar g | °C | 50 |  | T | 2061
S-01722 | TI-2074 | P09 | Saturated Natural Gas to Steam/NG Mixture, Vent | 24"-FLG-20-107-B24-P | Flare/Vent Gas |  |  | 5 |  | 290 | bar g | °C | 50 |  | T | 2074
S-01722 | TI-2111 | P11 | Air Intake F 2002 Combustion Air Blower | CA | Air | -3 | 48 |  |  |  | mbar g | °C | 50 |  | T | 2111
S-01722 | TI-2112 | P11 | Outlet F 2002 Combustion Air Blower | Ducting | Combustion Air | 21 | 54 |  |  | 80 | mbar g | °C | 50 |  | T | 2112
S-01722 | TI-2148 | P12 | Outlet E 2006 1st Natural Gas Feed Preheat Coil | 16"-PRG-20-102-F24-P | Process Gas | 49.4 | 246 | 55 |  | 375 | bar g | °C | 50 |  | T | 2148
S-01722 | TI-2149 | P12 | Outlet E 2006 1st Natural Gas Feed Preheat Coil | 16"-PRG-20-102-F24-P | Process Gas | 49.4 | 246 | 55 |  | 375 | bar g | °C | 50 |  | T | 2149
S-01722 | TI-2150 | P12 | N2 Recycle from Header | 3"-HG-20-112-F24-N | Hydrogen Gas | 50.4 | 48 | 60 |  | 200 | bar g | °C | 50 |  | T | 2150
S-01722 | TI-2151 | P12 | Inlet E 2006 1st Natural Gas Feed Preheat Coil | 14"-NG-10-105-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 50 |  | T | 2151
S-01722 | TI-2154 | P12 | WHS between E 2006 and E 2007 | WHS | Flue Gas |  | 236.3 |  |  |  |  | °C | 50 |  | T | 2154
S-01722 | TI-2155 | P12 | WHS between E 2007 and F 2001 | WHS | Flue Gas | -70 | 150 |  |  |  | mbar g | °C | 50 |  | T | 2155
S-01722 | TI-2161 | P12 | Outlet E 2007 Combustion Air Preheat Coil | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | T | 2161
S-01722 | TI-2162 | P12 | Outlet E 2007 Combustion Air Preheat Coil | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | T | 2162
S-01722 | TI-2221 | P13 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | T | 2221
S-01722 | TI-2226 | P13 | WHS inlet E 2001 | WHS | Flue Gas | -0.01 | 1093 |  |  |  | bar g | °C | 50 |  | T | 2226
S-01722 | TI-2227 | P13 | WHS between E 2001 and E 2002 | WHS | Flue Gas | -0.01 | 794 |  |  |  | bar g | °C | 50 |  | T | 2227
S-01722 | TI-2228 | P13 | WHS between E 2002 and E 2004 | WHS | Flue Gas | -0.02 | 439 |  |  |  | bar g | °C | 50 |  | T | 2228
S-01722 | TI-2229 | P13 | WHS between E 2004 and E 2006 | WHS | Flue Gas | 0.05 | 350 |  |  |  | bar g | °C | 50 |  | T | 2229
S-01722 | TI-2234 | P13 | Outlet E 2001 Reformer Feed Preheat Coil | 34"-RFG-20-114-H44-H | Process Gas | 36.3 | 638 | 46 |  | 675 | bar g | °C | 50 |  | T | 2234
S-01722 | TI-2254 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2254
S-01722 | TI-2255 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2255
S-01722 | TI-2256 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2256
S-01722 | TI-2257 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2257
S-01722 | TI-2258 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2258
S-01722 | TI-2259 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2259
S-01722 | TI-2260 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2260
S-01722 | TI-2261 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2261
S-01722 | TI-2262 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2262
S-01722 | TI-2263 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2263
S-01722 | TI-2264 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2264
S-01722 | TI-2265 | P14 | R 2003 Prereformer | R 2003 | Process Gas | 38.4 | 500 | 46 |  | 550 | bar g | °C | 50 |  | T | 2265
S-01722 | TI-2268 | P14 | Outlet R 2003 Prereformer | 30"-RFG-20-101-F34-H | Reformed Gas | 37.7 | 441 | 46 |  | 500 | bar g | °C | 50 |  | T | 2268
S-01722 | TI-2285 | P15 | Combustion Air to H 2001 Primary Reformer | CA | Combustion Air | 20 | 161 |  |  |  | mbar g | °C | 50 |  | T | 2285
S-01722 | TI-2295 | P15 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | T | 2295
S-01722 | TI-2297 | P15 | Waste Heat Section | WHS | Flue Gas | 0 | 1095 |  |  |  | bar g | °C | 50 |  | T | 2297
S-01722 | TI-2303 | P15 | Cold Collector | Cold Collector | Reformed Gas | 32 | 742 | 34.7 |  | 800 | bar g | °C | 50 |  | T | 2303
S-01722 | TI-2304 | P15 | Cold Collector | Cold Collector | Reformed Gas | 32 | 742 | 34.7 |  | 800 | bar g | °C | 50 |  | T | 2304
S-01722 | TI-2305 | P15 | Cold Collector | Cold Collector | Reformed Gas | 32 | 742 | 34.7 |  | 800 | bar g | °C | 50 |  | T | 2305
S-01722 | TI-2325 | P16A | R 2004 Secondary Reformer (Combustion Zone) | R 2004 | Process Gas | 31.4 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | T | 2325
S-01722 | TI-2326 | P16A | R 2004 Secondary Reformer, Skin Temperature | R 2004 | [6 empty] | bar g | °C | 50 |  | T | 2326
S-01722 | TI-2327 | P16A | R 2004 Secondary Reformer, Skin Temperature | R 2004 | [6 empty] | bar g | °C | 50 |  | T | 2327
S-01722 | TI-2328 | P16A | R 2004 Secondary Reformer, Skin Temperature | R 2004 | [6 empty] | bar g | °C | 50 |  | T | 2328
S-01722 | TI-2329 | P16A | R 2004 Secondary Reformer (Burner Internal) | R 2004 | Process Oxygen/Steam | 31.4 | 236 | 34.7 |  |  | bar g | °C | 50 |  | T | 2329
S-01722 | TI-2330 | P16A | R 2004 Secondary Reformer, Skin Temperature | R 2004 | [6 empty] | bar g | °C | 50 |  | T | 2330
S-01722 | TI-2331 | P16A | R 2004 Secondary Reformer, Skin Temperature | R 2004 | [6 empty] | bar g | °C | 50 |  | T | 2331
S-01722 | TI-2332 | P16A | R 2004 Secondary Reformer, Skin Temperature | R 2004 | [6 empty] | bar g | °C | 50 |  | T | 2332
S-01722 | TI-2333 | P16A | R 2004 Secondary Reformer, outlet | R 2004 Outlet | Reformed Gas | 27.1 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | T | 2333
S-01722 | TI-2334 | P16A | R 2004 Secondary Reformer (Catalyst) | R 2004 | Process Gas | 27.1 | 1020 | 34.7 |  |  | bar g | °C | 50 |  | T | 2334
S-01722 | TI-2351 | P17 | Outlet E 2021 1 Steam Superheater | 24"-RFG-20-110-D34-H | Reformed Gas | 26.3 | 360 | 30 |  | 390 | bar g | °C | 50 |  | T | 2351
S-01722 | TI-2352 | P17 | Outlet E 2021 3 Steam Superheater | 42"-RFG-20-115-D34-H | Reformed Gas | 26.3 | 360 | 29 |  | 390 | bar g | °C | 50 |  | T | 2352
S-01722 | TI-2353 | P17 | Outlet E 2021 2 Steam Superheater | 24"-RFG-20-110-H24-H | Reformed Gas | 26.7 | 409 | 31 |  | 450 | bar g | °C | 50 |  | T | 2353
S-01722 | TI-2354 | P17 | Outlet E 2021 1&2 Steam Superheater | 42"-RFG-20-110-H24-H | Reformed Gas | 26.7 | 409 | 31 |  | 450 | bar g | °C | 50 |  | T | 2354
S-01722 | TI-2355 | P17 | Outlet E 2021 1 Steam Superheater | 24"-HHPS-20-115-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 50 |  | T | 2355
S-01722 | TI-2356 | P17 | Outlet E 2021 2 Steam Superheater | 24"-HHPS-20-117-H34-H | High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 50 |  | T | 2356
S-01722 | TI-2359 | P17 | Outlet E 2021 3 Steam Superheater | 20"-HHPS-20-103-H24-H | High High Pressure Steam | 101 | 338 | 112 |  | 370 | bar g | °C | 50 |  | T | 2359
S-01722 | TI-2371 | P18 | Inlet D 2001 HHP Steam Drum | 12"-BFW-20-102-G24-H | Boiler Feed Water | 103 | 276 | 113 |  | 310 | bar g | °C | 50 |  | T | 2371
S-01722 | TI-2402 | P19 | Inlet D 2002 1st Separator | 34"-RFG-20-117-D40-H | Reformed Gas | 25.8 | 165 | 29 |  | 200 | bar g | °C | 50 |  | T | 2402
S-01722 | TI-2407 | P19 | Outlet D 2002 1st Separator, Vent | 16"-FLG-20-120-B40-P | Flare/Vent Gas |  |  | 5 |  | 200 | bar g | °C | 50 |  | T | 2407
S-01722 | TI-2418 | P19 | Inlet E 2022 2 BFW Preheater | 12"-BFW-20-104-G24 | Boiler Feed Water | 104 | 122 | 113 |  | 160 | bar g | °C | 50 |  | T | 2418
S-01722 | TI-2421 | P19 | Outlet D 2003 2nd Separator | 34"-RFG-20-122-D40-H | Reformed Gas | 25.3 | 159 | 29 |  | 200 | bar g | °C | 50 |  | T | 2421
S-01722 | TI-2444 | P20 | Outlet E 2025 DMW Preheater | 34"-RFG-20-124-D40-P | Reformed Gas | 24.4 | 132 | 29 |  | 200 | bar g | °C | 50 |  | T | 2444
S-01722 | TI-2455 | P20 | DMW from BL | 10"-DMW-20-101-B50-N | Demineralized Water | 5 | 35 | 14 |  | 65 | bar g | °C | 50 |  | T | 2455
S-01722 | TI-2472 | P21 | Outlet AE 2026 Air Cooler | 34"-RFG-20-125-D40-P | Reformed Gas | 24.2 | 65 | 29 |  | 120 | bar g | °C | 50 |  | T | 2472
S-01722 | TI-2476 | P21 | Outlet D 2005 Final Separator | 28"-SG-20-109-D40-TR | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 50 |  | T | 2476
S-01722 | TI-2484 | P21 | Outlet D 2005 Final Separator, Vent | 12"-FLG-20-123-B24-N | Flare/Vent Gas |  |  | 5 |  | 100 | bar g | °C | 50 |  | T | 2484
S-01722 | TI-2493 | P21 | Outlet E 2027 Water Cooler | 12"-CWR-20-101-B24-N | Cooling Water Return | 1.5 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 2493
S-01722 | TI-2536 | U01 | Purge Gas to Mixing Point | 24"-PG-30-104-B24-N | Purge Gas | 3.6 | 47 | 7 |  | 100 | bar g | °C | 50 |  | T | 2536
S-01722 | TI-2540 | U01 | Fuel Gas to Mixing Point | 24"-NG-20-108-B24-N | Natural Gas | 2 | 35 | 7 |  | 85 | bar g | °C | 50 |  | T | 2540
S-01722 | TI-2553 | U01 | Outlet Static Fuel Gas Mixer | 28"-FG-20-101-B24-H | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 50 |  | T | 2553
S-01722 | TI-2572 | U02 | Start-up N2 from D 2005 | 10"-N-20-110-B24-N | Nitrogen Gas | 6 | 40 | 10.5 |  | 75 | bar g | °C | 50 |  | T | 2572
S-01722 | TI-2579 | U02 | Outlet C 2001 Start-up Nitrogen Compressor | 10"-N-20-104-B24-P | Nitrogen Gas | 8 | 84 | 10.5 |  | 110 | bar g | °C | 50 |  | T | 2579
S-01722 | TI-2601 | U17 | Import H2 | 3"-HG-20-102-D24-N | Hydrogen Gas | 25 | 40 | 28 |  | 85 | bar g | °C | 50 |  | T | 2601
S-01722 | TI-2607 | U17 | Recycle Hydrogen from Loop | 3"-SG-30-128-G24-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | T | 2607
S-01722 | TI-3045 | P23 | MP Steam from Header | 4"-MPS-70-118-F24-H | Medium Pressure Steam | 33.7 | 242 | 45 |  | 300 | bar g | °C | 50 |  | T | 3045
S-01722 | TI-3072 | P24 | R 3001 1 Methanol Reactor | R 3001 1 | Make-up / Recycle Gas | 89.1 | 230 | 99 |  | 300 | bar g | °C | 50 |  | T | 3072
S-01722 | TI-3073 | P24 | Outlet R 3001 1 Methanol Reactor | 24"-SG-30-111-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | T | 3073
S-01722 | TI-3076 | P24 | R 3001 2 Methanol Reactor | R 3001 2 | Make-up / Recycle Gas | 89.1 | 230 | 99 |  | 300 | bar g | °C | 50 |  | T | 3076
S-01722 | TI-3077 | P24 | Outlet R 3001 2 Methanol Reactor | 24"-SG-30-108-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | T | 3077
S-01722 | TI-3080 | P24 | R 3001 3 Methanol Reactor | R 3001 3 | Make-up / Recycle Gas | 89.1 | 230 | 99 |  | 300 | bar g | °C | 50 |  | T | 3080
S-01722 | TI-3081 | P24 | Outlet R 3001 3 Methanol Reactor | 24"-SG-30-120-H40-H | Synthesis Gas | 77.8 | 246 | 99 |  | 290 | bar g | °C | 50 |  | T | 3081
S-01722 | TI-3084 | P24 | MP Steam for heating of R 3001 1/2/3 | 12"-MPS-70-120-F24-H | Medium Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | T | 3084
S-01722 | TI-3111 | P25 | Inlet E 3001 1/2/3 Feed/Effluent Exchanger | 32"-SG-30-103-G40-N | Synthesis Gas | 80 | 74 | 99 |  | 120 | bar g | °C | 50 |  | T | 3111
S-01722 | TI-3119 | P25 | Outlet E 3001 1 Feed/Effluent Exchanger | 20"-SG-30-110-H40-P | Synthesis Gas | 77.3 | 125 | 99 |  | 150 | bar g | °C | 50 |  | T | 3119
S-01722 | TI-3120 | P25 | Outlet E 3001 2 Feed/Effluent Exchanger | 20"-SG-30-109-H40-P | Synthesis Gas | 77.3 | 125 | 99 |  | 150 | bar g | °C | 50 |  | T | 3120
S-01722 | TI-3121 | P25 | Outlet E 3001 3 Feed/Effluent Exchanger | 20"-SG-30-121-H40-P | Synthesis Gas | 77.3 | 125 | 99 |  | 150 | bar g | °C | 50 |  | T | 3121
S-01722 | TI-3142 | P26 | Outlet AE 3001 2 Loop Air Cooler | 24"-SG-30-122-G40-P | Synthesis Gas | 76.8 | 65 | 99 |  | 120 | bar g | °C | 50 |  | T | 3142
S-01722 | TI-3145 | P26 | Outlet AE 3002 2 Loop Air Cooler | 24"-SG-30-123-G40-P | Synthesis Gas | 76.8 | 65 | 99 |  | 120 | bar g | °C | 50 |  | T | 3145
S-01722 | TI-3148 | P26 | Outlet AE 3002 3 Loop Air Cooler | 24"-SG-30-124-G40-P | Synthesis Gas | 76.8 | 65 | 99 |  | 120 | bar g | °C | 50 |  | T | 3148
S-01722 | TI-3164 | P27 | Outlet D 3001 HP Separator | 30"-SG-30-118-G40-N | Synthesis Gas | 76.2 | 48 | 99 |  | 100 | bar g | °C | 50 |  | T | 3164
S-01722 | TI-3194 | P28 | Outlet D 3002 LP Separator | 8"-PG-30-102-B40-N | Purge Gas | 4 | 48 | 7 |  | 100 | bar g | °C | 50 |  | T | 3194
S-01722 | TI-3198 | P28 | Outlet D 3002 LP Separator | 10"-PMC-30-111-B40-N | Crude Methanol | 4 | 48 | 8 |  | 100 | bar g | °C | 50 |  | T | 3198
S-01722 | TI-5020 | P29 | Wash Water to T 5004 Vent Wash Column | 2"-PMW-50-101-B24-N | Methanol Water | 4 | 48 | 7.5 |  | 100 | bar g | °C | 50 |  | T | 5020
S-01722 | TI-5039 | P30 | Outlet E 2024 1 Stabilizer Column Reboiler | RFG-50 | Reformed Gas | 24.8 | 138 | 29 |  | 200 | bar g | °C | 50 |  | T | 5039
S-01722 | TI-5040 | P30 | Outlet E 2024 2 Stabilizer Column Reboiler | 34"-RFG-50-101-D40-H | Reformed Gas | 24.8 | 138 | 29 |  | 200 | bar g | °C | 50 |  | T | 5040
S-01722 | TI-5045 | P30 | Outlet T 5001 Stabilizer Column | 16"-PMC-50-130-B24-H | Crude Methanol | 1 | 88 | 10 |  | 160 | bar g | °C | 50 |  | T | 5045
S-01722 | TI-5052 | P30 | T 5001 Stabilizer Column | T 5001 Top | Methanol Water Gas/Liquid | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5052
S-01722 | TI-5053 | P30 | T 5001 Stabilizer Column | T 5001 Top | Methanol Water Gas/Liquid | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5053
S-01722 | TI-5054 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5054
S-01722 | TI-5056 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5056
S-01722 | TI-5057 | P30 | T 5001 Stabilizer Column | T 5001 Middle | Methanol Water Gas/Liquid | 0.7 | 84-86 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5057
S-01722 | TI-5059 | P30 | Outlet T 5001 Stabilizer Column | 42"-PMV-50-110-B24-P | Methanol Vapour | 0.7 | 78 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5059
S-01722 | TI-5060 | P30 | Outlet T 5001 Stabilizer Column | 20"-PMC-50-110-B24-H | Crude Methanol | 1 | 87 | 5 |  | 160 | bar g | °C | 50 |  | T | 5060
S-01722 | TI-5062 | P30 | Inlet T 5001 Stabilizer Column | 34"-PMV-50-120-B24-H | Methanol Vapour | 1 | 88 | 5 |  | 160 | bar g | °C | 50 |  | T | 5062
S-01722 | TI-5067 | P30 | Outlet E 2024 2 Stabilizer Column Reboiler | 34"-PMW-50-122-B24-H | Methanol Water | 1 | 88 | 5 |  | 160 | bar g | °C | 50 |  | T | 5067
S-01722 | TI-5074 | P31 | Outlet D 5009 Steam Condensate K.O. Drum for E 5001 | 8"-LPC-50-110-D24-H | Low Pressure Steam Condensate | 2.4 | 138 | 18 |  | 190 | bar g | °C | 50 |  | T | 5074
S-01722 | TI-5097 | P32 | Outlet D 5001 Stabilizer Column OH Accumulator | 10"-PMC-50-121-B24 | Crude Methanol | 0.6 | 65 | 13 |  | 150 | bar g | °C | 50 |  | T | 5097
S-01722 | TI-5110 | P32 | Outlet E 5010 OH Gas Condenser, Vent | 6"-FLG-50-131-B24-N | Flare/Vent Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 50 |  | T | 5110
S-01722 | TI-5111 | P32 | Outlet E 5010 OH Gas Condenser | 6"-PG-50-101-B24-N | Purge Gas | 0.6 | 48 | 3.5 |  | 75 | bar g | °C | 50 |  | T | 5111
S-01722 | TI-5165 | P34 | Outlet T 5002 LP Methanol Column | 10"-PMC-50-150-D24-H | Crude Methanol | 0.7 | 86 | 16 |  | 160 | bar g | °C | 50 |  | T | 5165
S-01722 | TI-5167 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5167
S-01722 | TI-5171 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5171
S-01722 | TI-5173 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5173
S-01722 | TI-5174 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5174
S-01722 | TI-5175 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5175
S-01722 | TI-5177 | P34 | Outlet T 5002 LP Methanol Column | 72"PMV-50-130-B24-P | Methanol Vapour | 0.1 | 67 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5177
S-01722 | TI-5180 | P34 | T 5002 LP Methanol Column | T 5002 | Methanol Water Gas/Liquid | 0.1-0.7 | 67-88 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5180
S-01722 | TI-5181 | P34 | Outlet T 5002 LP Methanol Column | 24"-PMC-50-140-B24-H | Crude Methanol | 0.7 | 83 | 5 |  | 160 | bar g | °C | 50 |  | T | 5181
S-01722 | TI-5184 | P34 | Inlet T 5002 LP Methanol Column | 16"-PMC-50-147-B24-H | Crude Methanol | 0.7 | 86 | 5 |  | 160 | bar g | °C | 50 |  | T | 5184
S-01722 | TI-5208 | P36 | Outlet AE 5005 LP Column OH Condenser | 24"-PMP-50-101-B24-P | Rich Methanol Liquid | 0 | 65 | 3.5 |  | 150 | bar g | °C | 50 |  | T | 5208
S-01722 | TI-5209 | P36 | Outlet D 5002 LP Column OH Accumulator | 20"-PMP-50-102-B24-H | Methanol Product | 0 | 65 | 13 |  | 150 | bar g | °C | 50 |  | T | 5209
S-01722 | TI-5219 | P36 | Inlet E 5008 Methanol Product Cooler No. 1 | 6"-PMP-50-110-B24-P | Methanol Product | 4 | 65 | 13 |  | 150 | bar g | °C | 50 |  | T | 5219
S-01722 | TI-5221 | P36 | Outlet E 5008 Methanol Product Cooler No. 1 | 6"-PMP-50-111-D24-N | Methanol Product | 3.5 | 48 | 19 |  | 75 | bar g | °C | 50 |  | T | 5221
S-01722 | TI-5261 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5261
S-01722 | TI-5262 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5262
S-01722 | TI-5263 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5263
S-01722 | TI-5264 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5264
S-01722 | TI-5265 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5265
S-01722 | TI-5269 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5269
S-01722 | TI-5273 | P38 | Outlet T 5003 MP Methanol Column | 10"-PMW-50-120-D24-H | Methanol Water | 3.6 | 149 | 15 |  | 175 | bar g | °C | 50 |  | T | 5273
S-01722 | TI-5280 | P38 | Outlet T 5003 MP Methanol Column | 56"-PMV-50-150-B24-H | Methanol Vapour | 2.7 | 102 | 6 |  | 165 | bar g | °C | 50 |  | T | 5280
S-01722 | TI-5307 | P39 | Outlet E 5003 1/2/3 MP Column Reboiler No. 1 | 16"-LPC-50-115-B24-H | Low Pressure Steam Condensate | 6.5 | 168 | 10.5 |  | 190 | bar g | °C | 50 |  | T | 5307
S-01722 | TI-5325 | P40 | Outlet D 5003 MP Cooling OH Accumulator | 24"-PMP-50-130-B24-H | Methanol Product | 2.6 | 101 | 7 |  | 165 | bar g | °C | 50 |  | T | 5325
S-01722 | TI-5335 | P40 | Outlet P 5006 A/B MP Column Reflux Pump | 6"-PMP-50-140-D24-H | Methanol Product | 6 | 101 | 19 |  | 165 | bar g | °C | 50 |  | T | 5335
S-01722 | TI-5340 | P40 | Outlet E 5012 Methanol Product Cooler No. 2 | 6"-PMP-50-141-D24-N | Methanol Product | 5.7 | 48 | 19 |  | 75 | bar g | °C | 50 |  | T | 5340
S-01722 | TI-5369 | P41 | Outlet AE 5006 Wash Water Air Cooler | 2"-PMW-50-125-B24-P | Methanol Water | 4.3 | 65 | 7.5 |  | 120 | bar g | °C | 50 |  | T | 5369
S-01722 | TI-5381 | P42 | Inlet X 5001 Product Polisher Unit | 10"-PMP-50-142-B24-N | Methanol Product | 3 | 48 | 19 |  | 75 | bar g | °C | 50 |  | T | 5381
S-01722 | TI-5441 | P45 | Liquid Off-stream from T 5003 | 2"-LOS-50-110-B24-P | Liquid Off-stream | 3.4 | 115 | 7.5 |  | 175 | bar g | °C | 50 |  | T | 5441
S-01722 | TI-5442 | P45 | Inlet E 5011 Liquid Off-stream Cooler | 2"-LOS-50-113-B24-P | Liquid Off-stream | 2.5 | 115 | 7.5 |  | 175 | bar g | °C | 50 |  | T | 5442
S-01722 | TI-5443 | P45 | Outlet E 5011 Liquid Off-stream Cooler | 2"-LOS-50-114-B24-N | Liquid Off-stream | 2 | 48 | 7.5 |  | 75 | bar g | °C | 50 |  | T | 5443
S-01722 | TI-6001 | P05 | Inlet P 6002 A/B Steam Condensate Return Pump | 18"-MPC-60-101-F24-H | Medium Pressure Steam Condensate | 32.5 | 240 | 73 |  | 260 | bar g | °C | 50 |  | T | 6001
S-01722 | TI-6024 | P06 | Inlet T 6001 Saturator | 12"-PRC-60-101-G40-H | Process Condensate | 44 | 225 | 57 |  | 280 | bar g | °C | 50 |  | T | 6024
S-01722 | TI-6026 | P06 | MP Steam to T 6001 Saturator | 24"-MPS-60-102-F24-H | Medium Pressure Steam | 32.2 | 240 | 45 |  | 300 | MPa g | °C | 50 |  | T | 6026
S-01722 | TI-6031 | P06 | Outlet X 6001 A/B Particle Filter | 8"-PRC-60-102-G40-H | Process Condensate | 44 | 119 | 71 |  | 180 | bar g | °C | 50 |  | T | 6031
S-01722 | TI-6034 | P06 | Outlet X 6001 A/B Particle Filter | 8"-PRC-60-102-G40-H | Process Condensate | 44 | 119 | 71 |  | 180 | bar g | °C | 50 |  | T | 6034
S-01722 | TI-6054 | P07 | Outlet D 6001 Feed Gas Separator | 24"-PRG-60-103-F24-H | Process Gas | 42.8 | 226 | 55 |  | 290 | bar g | °C | 50 |  | T | 6054
S-01722 | TI-6056 | P07 | Outlet E 6001 Saturator Feed/Effluent Exchanger | 16"-PRG-60-102-F24-H | Process Gas | 43.3 | 265 | 55 |  | 290 | bar g | °C | 50 |  | T | 6056
S-01722 | TI-6058 | P07 | Outlet D 6001 Feed Gas Separator | 16"-PRC-60-110-G40-H | Process Condensate | 43 | 225 | 56 |  | 290 | bar g | °C | 50 |  | T | 6058
S-01722 | TI-6081 | P08 | Outlet E 6002 Process Condensate Preheater | 4"-PRC-60-108-G40-H | Process Condensate | 45 | 63 | 63 |  | 150 | bar g | °C | 50 |  | T | 6081
S-01722 | TI-6084 | P08 | Outlet E 6002 Process Condensate Preheater | 4"-BD-60-109-G40-P | Boiler Blow-down | 44 | 78 | 57 |  | 260 | bar g | °C | 50 |  | T | 6084
S-01722 | TI-7001 | U03 | HP Extraction Steam from FT 7001 1/2 | 16"-HPS-30-129-F24-H | High Pressure Steam | 45 | 355 | 52 |  | 410 | bar g | °C | 50 |  | T | 7001
S-01722 | TI-7007 | U03 | HP Steam Header | 28"-HPS-70-116-F24-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 50 |  | T | 7007
S-01722 | TI-7021 | U04 | HP Steam Export/Import | 24"-HPS-70-107-F34-H | High Pressure Steam | 43 | 410 | 52 |  | 470 | bar g | °C | 50 |  | T | 7021
S-01722 | TI-7031 | U05 | MP Steam Header | 24"-MPS-30-115-F24-H | Medium Pressure Steam | 32.7 | 240 | 45 |  | 300 | bar g | °C | 50 |  | T | 7031
S-01722 | TI-7056 | U06 | LP Steam | 32"-LPS-70-108-D24-H | Low Pressure Steam | 7 | 189 | 9.5 |  | 340 | bar g | °C | 50 |  | T | 7056
S-01722 | TI-7097 | U09 | D 7001 Deaerator | D 7001 | Boiler Water | 1 | 120 | 3.5 |  | 200 | bar g | °C | 50 |  | T | 7097
S-01722 | TI-7098 | U09 | D 7001 Deaerator, Vent | 24"-VA-70-161-B24-P | Steam | 0 | 120 | 3.5 |  | 340 | bar g | °C | 50 |  | T | 7098
S-01722 | TI-8001 | U21 | Inlet Flare KO Drum | 72"-FLG-80-144-B24-P | Flare gas | 1.5 | 390 | 5 |  | 410 | bar g | °C | 50 |  | T | 8001
S-01722 | TIC-2220 | P13 | Outlet E 2004 2nd Natural Gas Feed Preheat Coil | 16"-PRG-20-101-F24-H | Process Gas | 48.8 | 380 | 55 |  | 410 | bar g | °C | 50 |  | T | 2220
S-01722 | TIC-2232 | P13 | Process Gas to E 2002 Prereformer Feed Preheat Coil | 24"-PRG-20-112-F24-H | Process Gas | 42.1 | 267 | 46 |  | 410 | bar g | °C | 50 |  | T | 2232
S-01722 | TIC-2253 | P14 | Inlet R 2003 Prereformer | 30"-PRG-20-113-G36-H | Process Gas | 38.4 | 496 | 46 |  | 550 | bar g | °C | 50 |  | T | 2253
S-01722 | TIC-2335 | P16B | Outlet E 2020 1 Waste Heat Boiler | E 2020 1 | Reformed Gas | 26.7 | 544 | 31 |  | 575 | bar g | °C | 50 |  | T | 2335
S-01722 | TIC-2336 | P16B | Outlet E 2020 2 Waste Heat Boiler | E 2020 2 | Reformed Gas | 26.7 | 544 | 31 |  | 575 | bar g | °C | 50 |  | T | 2336
S-01722 | TIC-2360 | P17 | Outlet E 2021 1&2 Steam Superheater | 24"-HHPS-20-115-H34-H | High High Pressure Steam | 100 | 460 | 112 |  | 490 | bar g | °C | 50 |  | T | 2360
S-01722 | TIC-2457 | P20 | Outlet E 2025 DMW Preheater | 10"-DMW-20-104-B50-H | Demineralized Water | 4.5 | 72 | 14 |  | 110 | bar g | °C | 50 |  | T | 2457
S-01722 | TIC-3113 | P25 | Outlet E 3001 1 Feed/Effluent Exchanger | 24"-SG-30-135-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | T | 3113
S-01722 | TIC-3116 | P25 | Outlet E 3001 2 Feed/Effluent Exchanger | 24"-SG-30-107-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | T | 3116
S-01722 | TIC-3118 | P25 | Outlet E 3001 3 Feed/Effluent Exchanger | 24"-SG-30-119-H40-H | Synthesis Gas | 79.5 | 210 | 99 |  | 260 | bar g | °C | 50 |  | T | 3118
S-01722 | TIC-5064 | P30 | Outlet E 2024 1 Stabilizer Column Reboiler | 34"-RFG-50-101-D40-H | Reformed Gas | 24.8 | 138 | 29 |  | 200 | bar g | °C | 50 |  | T | 5064
S-01722 | TIC-5266 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5266
S-01722 | TIC-5267 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5267
S-01722 | TIC-5268 | P38 | T 5003 MP Methanol Column | T 5003 | Methanol Water Gas/Liquid | 2.7-3.6 | 102-149 | 6 |  | 165 | bar g | °C | 50 |  | T | 5268
S-01722 | TIC-5277 | P38 | Outlet E 2023 MP Column Reboiler No. 2 | 34"-RFG-20-121-D40-H | Reformed Gas | 25.3 | 159 | 29 |  | 200 | bar g | °C | 50 |  | T | 5277
S-01722 | TIC-7002 | U03 | HP Steam Header | 12"-HPS-70-105-H34-H | High Pressure Steam | 44 | 345 | 112 |  | 410 | bar g | °C | 50 |  | T | 7002
S-01722 | TIC-7003 | U03 | HP Steam Header | 28"-HPS-70-104-H34-H | High Pressure Steam | 44 | 345 | 112 |  | 410 | bar g | °C | 50 |  | T | 7003
S-01722 | TIC-7004 | U03 | HP Steam Header | 28"-HPS-70-106-H34-H | High Pressure Steam | 44 | 345 | 112 |  | 410 | bar g | °C | 50 |  | T | 7004
S-01722 | TIC-7025 | U04 | HP Import Steam to Header | 24"-HPS-70-133-F34-H | High Pressure Steam | 42.5 | 345 | 52 |  | 470 | bar g | °C | 50 |  | T | 7025
S-01722 | TIC-7026 | U04 | HP Steam Header | 24"-HPS-70-1873-H34-H | High Pressure Steam | 43 | 410 | 112 |  | 470 | bar g | °C | 50 |  | T | 7026
S-01722 | TIC-7027 | U04 | HP Steam Header | 24"-HPS-70-1862-H34-H | High Pressure Steam | 43 | 410 | 112 |  | 470 | bar g | °C | 50 |  | T | 7027
S-01722 | TIC-7032 | U05 | MP Steam Header | 18"-MPS-70-128-D24-H | Medium Pressure Steam | 34 | 280 | 45 |  | 300 | bar g | °C | 50 |  | T | 7032
S-01722 | TIC-7033 | U05 | MP Steam Header | 18"-MPS-70-129-D24-H | Medium Pressure Steam | 34 | 280 | 45 |  | 300 | bar g | °C | 50 |  | T | 7033
S-01722 | TIC-7052 | U06 | LP Steam Header | 24"-LPS-70-116-F24-H | Low Pressure Steam | 7.5 | 200 | 52 |  | 340 | bar g | °C | 50 |  | T | 7052
S-01722 | TIC-7053 | U06 | LP Steam Header | 24"-LPS-70-117-F24-H | Low Pressure Steam | 7.5 | 200 | 52 |  | 340 | bar g | °C | 50 |  | T | 7053
S-01722 | TIC-7071 | U07 | HP Steam to E 2008 | 6"-HPS-70-126-F24-H | High Pressure Steam | 44 | 272 | 52 |  | 310 | bar g | °C | 50 |  | T | 7071
S-01722 | TV-2220 | P12 | Bypass E 2006 1st Natural Gas Feed Preheat Coil | 8"-NG-10-106-F24-N | Natural Gas | 50 | 40 | 55 |  | 85 | bar g | °C | 243 |  | T | 2220
S-01722 | TV-2457 | P20 | Bypass E 2025 DMW Preheater | 16"-RFG-20-127-D40-P | Reformed Gas | 24.8 | 138 | 29 |  | 200 | bar g | °C | 243 |  | T | 2457
S-01722 | TV-3113 | P25 | Bypass E 3001 1 Feed/Effluent Exchanger | 10"-SG-30-926-H40-H | Synthesis Gas | 80 | 74 | 99 |  | 260 | bar g | °C | 243 |  | T | 3113
S-01722 | TV-3116 | P25 | Bypass E 3001 2 Feed/Effluent Exchanger | 10"-SG-30-931-H40-H | Synthesis Gas | 80 | 74 | 99 |  | 260 | bar g | °C | 243 |  | T | 3116
S-01722 | TV-3118 | P25 | Bypass E 3001 3 Feed/Effluent Exchanger | 10"-SG-30-937-H40-H | Synthesis Gas | 80 | 74 | 99 |  | 260 | bar g | °C | 243 |  | T | 3118
S-01722 | TV-5064 | P30 | Bypass E 2024 1/2 Stabilizer Column Reboiler | 16"-RFG-50-103-D40-H | Reformed Gas | 25.3 | 159 | 29 |  | 200 | bar g | °C | 243 |  | T | 5064
S-01722 | TV-5277 | P38 | Bypass E 2023 MP Column Reboiler No. 2 | 18"-RFG-50-125-D40-H | Reformed Gas | 25.8 | 165 | 29 |  | 200 | bar g | °C | 243 |  | T | 5277
S-01722 | TV-7002 | U03 | BFW to Quench of HHP-HP Steam | 2"-BFW-70-104-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | T | 7002
S-01722 | TV-7003 | U03 | BFW to Quench of HHP-HP Steam | 3"-BFW-70-143-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | T | 7003
S-01722 | TV-7004 | U03 | BFW to Quench of HHP-HP Steam | 3"-BFW-70-141-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | T | 7004
S-01722 | TV-7025/A | U04 | BFW to Quench of HP Steam Import | 2"-BFW-70-152-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7025 | A
S-01722 | TV-7025/B | U04 | BFW to Quench of HP Steam Import | 2"-BFW-70-154-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7025 | B
S-01722 | TV-7026 | U04 | BFW to Quench of HHP-HP Steam Export | 2"-BFW-70-112-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | T | 7026
S-01722 | TV-7027 | U04 | BFW to Quench of HHP-HP Steam Export | 2"-BFW-70-156-H24-H | Boiler Feed Water | 120 | 122 | 170 |  | 160 | bar g | °C | 243 |  | T | 7027
S-01722 | TV-7032 | U05 | BFW to Quench of HP-MP Steam | 2"-BFW-70-115-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7032
S-01722 | TV-7033 | U05 | HP BFW to Quench of HP-MP Steam | 2"-BFW-70-108-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7033
S-01722 | TV-7052 | U06 | HP BFW to Quench of HP-LP Steam | 2"-BFW-70-121-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7052
S-01722 | TV-7053 | U06 | HP BFW to Quench of HP-LP Steam | 2"-BFW-70-119-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7053
S-01722 | TV-7071/A | U07 | BFW from Header | 2"-BFW-70-124-F24-H | Boiler Feed Water | 50 | 122 | 80 |  | 160 | bar g | °C | 243 |  | T | 7071 | A
S-01722 | TV-7071/B | U07 | BFW from Header | 2"-BFW-70-145-F24-H | Boiler Feed Water | 50 | 121 | 80 |  | 160 | bar g | °C | 243 |  | T | 7071 | B
S-01722 | TZ-7025 | U04 | HP Import Steam to Header | 24"-HPS-70-133-F34-H | High Pressure Steam | 42.5 | 345 | 52 |  | 470 | bar g | °C | 243 |  | T | 7025
S-01722 | USV-1001 | P01 | D 1001 Natural Gas K.O. Drum Drain | 2"-OW-10-103-F24-N | Oily Water | 52 | 40 | 60 |  | 85 | bar g | °C | 243 |  | U | 1001
S-01722 | USV-2010 | P02 | Stop Process Oxygen to E 2008 Oxygen Preheater | 12"-PO-20-102-F70-N | Process Oxygen | 35 | 35 | 47 |  | 85 | bar g | °C | 243 |  | U | 2010
S-01722 | USV-2021 | P02 | Stop HP Steam from Header | 6"-HPS-70-126-F24-H | High Pressure Steam | 44 | 272 | 52 |  | 310 | bar g | °C | 243 |  | U | 2021
S-01722 | USV-2038 | P03 | Stop HP Steam to Mixing Point | 4"-HPS-20-106-F44-H | High Pressure Steam | 44 | 345 | 52 |  | 410 | bar g | °C | 243 |  | U | 2038
S-01722 | USV-2043 | P03 | Bleed Process Oxygen to Mixing Point | 3"-PO-20-103-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 243 |  | U | 2043
S-01722 | USV-2045 | P03 | Block Process Oxygen to Mixing Point | 16"-PO-20-114-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 243 |  | U | 2045
S-01722 | USV-2048 | P03 | Block Process Oxygen to Mixing Point | 16"-PO-20-114-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 243 |  | U | 2048
S-01722 | USV-2049 | P03 | Bleed Oxygen to Mixing Point | 1 1/2"-PO-20-109-F70-H | Process Oxygen | 34 | 230 | 47 |  | 255 | bar g | °C | 243 |  | U | 2049
S-01722 | USV-2092 | P10 | Block Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-20-108-F24-H | Process Gas | 42.1 | 262 | 55 |  | 290 | bar g | °C | 243 |  | U | 2092
S-01722 | USV-2093 | P10 | Block Saturated Natural Gas to Steam/NG Mixture | 24"-PRG-20-108-F24-H | Process Gas | 42.1 | 262 | 55 |  | 290 | bar g | °C | 243 |  | U | 2093
S-01722 | USV-2094 | P10 | Bleed Saturated Natural Gas to Steam/NG Mixture | 2"-PRG-20-109-F24-H | Process Gas | 41.1 | 262 | 55 |  | 290 | bar g | °C | 243 |  | U | 2094
S-01722 | USV-2117 | P11 | Stop HP Steam to FT 2002 Steam Turbine for F 2002 | 8"-HPS-70-101-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 243 |  | U | 2117
S-01722 | USV-2166 | P12 | Stop HP Steam to FT 2001 Steam Turbine for F 2001 | 6"-HPS-70-111-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 243 |  | U | 2166
S-01722 | USV-2381 | P18 | Stop Continuous Blow Down from D 2001 HHP Steam Drum | 2"-CBD-20-102-G24-P | Continuous Blow Down | 103 | 313 | 113 |  | 330 | bar g | °C | 243 |  | U | 2381
S-01722 | USV-2482 | P21 | Outlet D 2005 Final Separator, Depressurisation | 12"-SG-20-106-D40-N | Synthesis Gas | 24 | 48 | 29 |  | 100 | bar g | °C | 243 |  | U | 2482
S-01722 | USV-2541 | U01 | Block Fuel Gas to H 2001 | 28"-FG-20-126-B24-N | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 243 |  | U | 2541
S-01722 | USV-2542 | U01 | Block Fuel Gas to H 2001 | 28"-FG-20-127-B24-N | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 243 |  | U | 2542
S-01722 | USV-2543 | U01 | Bleed Fuel Gas to H 2001 | 2"-FG-20-131-B24-N | Fuel Gas | 2 | 45 | 7 |  | 100 | bar g | °C | 243 |  | U | 2543
S-01722 | USV-2544 | U01 | Purge Gas to Mixing Point | 24"-PG-20-125-B24-N | Purge Gas | 2 | 47 | 7 |  | 100 | bar g | °C | 243 |  | U | 2544
S-01722 | USV-2545 | U01 | Bleed Purge Gas to Mixing Point | 2"-PG-20-125-B24-N | Purge Gas | 2 | 47 | 7 |  | 100 | bar g | °C | 243 |  | U | 2545
S-01722 | USV-2547 | U01 | Block Fuel Gas for Burner Tightness Test | 2"-NG-20-113-B24-N | Fuel Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 243 |  | U | 2547
S-01722 | USV-2548 | U01 | Block Fuel Gas for Burner Tightness Test | 2"-NG-20-113-B24-N | Fuel Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 243 |  | U | 2548
S-01722 | USV-2549 | U01 | Bleed Fuel Gas for Burner Tightness Test | 1 1/2"-FG-20-106-B24-N | Fuel Gas | 4 | 35 | 7 |  | 85 | bar g | °C | 243 |  | U | 2549
S-01722 | USV-3018 | P22 | Block reduction/oxidation gases to R 3001 | 3"-SG-30-150-D24-N | Synthesis Gas | 6 | 48 | 29 |  | 100 | bar g | °C | 243 |  | U | 3018
S-01722 | USV-3052 | P23 | Stop Continuous Blow Down from D 3003 MP Steam Drum | 2"-CBD-30-101-F24-P | Boiler Blow-down | 35 | 242 | 47 |  | 265 | bar g | °C | 243 |  | U | 3052
S-01722 | USV-3172 | P27 | Stop Crude Methanol from D 3001 HP Separator | 10"-PMC-30-101-G40-N | Crude Methanol | 76.2 | 48 | 100 |  | 100 | bar g | °C | 243 |  | U | 3172
S-01722 | USV-5302 | P39 | Stop LP Steam to E 5003 1/2/3 MP Column Reboiler No. 1 | 32"-LPS-70-105-D24-H | Low Pressure Steam | 7 | 188 | 9.5 |  | 340 | bar g | °C | 243 |  | U | 5302
S-01722 | USV-5391 | P43 | Stop Methanol Product to TK 5002 1 | 10"-PMP-50-143-D24-N | Methanol Product | 3 | 48 | 19 |  | 75 | bar g | °C | 243 |  | U | 5391
S-01722 | USV-5392 | P43 | Stop Methanol Product to TK 5002 2 | 10"-PMP-50-144-D24-N | Methanol Product | 3 | 48 | 19 |  | 75 | bar g | °C | 243 |  | U | 5392
S-01722 | USV-5393 | P43 | Stop Methanol Product from P 5008 A/B | 3"-PMP-50-158-B24-N | Methanol Product | 1 | 48 | 14 |  | 75 | bar g | °C | 243 |  | U | 5393
S-01722 | USV-5420 | P44 | Stop Methanol Product from T 5002 2 | 10"-PMP-50-152-B24-N | Methanol Product | 1 | 48 | 4.5 |  | 75 | bar g | °C | 243 |  | U | 5420
S-01722 | USV-5421 | P44 | Stop Methanol Product from P 5008 A/B | 3"-PMP-50-156-B24-N | Methanol Product | 1 | 48 | 14 |  | 75 | bar g | °C | 243 |  | U | 5421
S-01722 | USV-5422 | P44 | Stop Methanol Product from T 5002 1 | 10"-PMP-50-150-B24-N | Methanol Product | 1 | 48 | 4.5 |  | 75 | bar g | °C | 243 |  | U | 5422
S-01722 | USV-6081 | P08 | Blowdown to D 6002 Saturator Blowdown Drum | 2"-BD-60-109-G40-P | Blow-down | 1 | 73 | 57 |  | 260 | bar g | °C | 243 |  | U | 6081
S-01722 | USV-6082 | P08 | Blowdown to D 6002 Saturator Blowdown Drum | 4"-BD-60-114-G40-H | Boiler Blow-down | 43 | 225 | 56 |  | 290 | bar g | °C | 243 |  | U | 6082
S-01722 | USV-7130 | U10 | Stop HP Steam to FP 7001 A Steam Turbine for FP 7001 A | 8"-HPS-70-117-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 243 |  | U | 7130
S-01722 | USV-7135 | U10 | Stop HP Steam to FP 7001 B Steam Turbine for FP 7001 B | 8"-HPS-70-118-F24-H | High Pressure Steam | 43 | 345 | 52 |  | 410 | bar g | °C | 243 |  | U | 7135
S-01722 | USY-1001 | P01 | D 1001 Natural Gas K.O. Drum Drain | [9 empty] | 50 |  | U | 1001
S-01722 | USY-2010 | P02 | Stop Process Oxygen to E 2008 Oxygen Preheater | [9 empty] | 50 |  | U | 2010
S-01722 | USY-2021 | P02 | Stop HP Steam from Header | [9 empty] | 50 |  | U | 2021
S-01722 | USY-2038 | P03 | Stop HP Steam to Mixing Point | [9 empty] | 50 |  | U | 2038
S-01722 | USY-2043 | P03 | Bleed Process Oxygen to Mixing Point | [9 empty] | 50 |  | U | 2043
S-01722 | USY-2045 | P03 | Block Process Oxygen to Mixing Point | [9 empty] | 50 |  | U | 2045
S-01722 | USY-2048 | P03 | Block Process Oxygen to Mixing Point | [9 empty] | 50 |  | U | 2048
S-01722 | USY-2049 | P03 | Bleed Process Oxygen to Mixing Point | [9 empty] | 50 |  | U | 2049
S-01722 | USY-2092 | P10 | Block Saturated Natural Gas to Steam/NG Mixture | [9 empty] | 50 |  | U | 2092
S-01722 | USY-2093 | P10 | Block Saturated Natural Gas to Steam/NG Mixture | [9 empty] | 50 |  | U | 2093
S-01722 | USY-2094 | P10 | Bleed Saturated Natural Gas to Steam/NG Mixture | [9 empty] | 50 |  | U | 2094
S-01722 | USY-2117 | P11 | Stop HP Steam to FT 2002 Steam Turbine for F 2002 | [9 empty] | 50 |  | U | 2117
S-01722 | USY-2118 | P11 | FT 2002 Steam Turbine for F 2002 | [9 empty] | 50 |  | U | 2118
S-01722 | USY-2122 | P11 | F 2002 Combustion Air Blower, Stop | [9 empty] | 50 |  | U | 2122
S-01722 | USY-2123 | P11 | F 2002 Combustion Air Blower, Start | [9 empty] | 50 |  | U | 2123
S-01722 | USY-2157 | P12 | F 2001 Flue Gas Blower, Stop | [9 empty] | 50 |  | U | 2157
S-01722 | USY-2158 | P12 | F 2001 Flue Gas Blower, Start | [9 empty] | 50 |  | U | 2158
S-01722 | USY-2166 | P12 | Stop HP Steam to FT 2001 Steam Turbine for F 2001 | [9 empty] | 50 |  | U | 2166
S-01722 | USY-2169 | P12 | FT 2001 Steam Turbine for F 2001 | [9 empty] | 50 |  | U | 2169
S-01722 | USY-2381 | P18 | Stop Continuous Blow Down from D 2001 HHP Steam Drum | [9 empty] | 50 |  | U | 2381
S-01722 | USY-2409 | P19 | P 2001 A Process Condensate Pump No. 1 | [9 empty] | 50 |  | U | 2409
S-01722 | USY-2413 | P19 | P 2001 B Process Condensate Pump No. 1 | [9 empty] | 50 |  | U | 2413
S-01722 | USY-2446 | P20 | P 2002 A Process Condensate Pump No. 2 | [9 empty] | 50 |  | U | 2446
S-01722 | USY-2450 | P20 | P 2002 B Process Condensate Pump No. 2 | [9 empty] | 50 |  | U | 2450
S-01722 | USY-2482 | P21 | Outlet D 2005 Final Separator, Vent | [9 empty] | 50 |  | U | 2482
S-01722 | USY-2486 | P21 | P 2003 A Process Condensate Pump No. 3 | [9 empty] | 50 |  | U | 2486
S-01722 | USY-2490 | P21 | P 2003 B Process Condensate Pump No. 3 | [9 empty] | 50 |  | U | 2490
S-01722 | USY-2541 | U01 | Block Fuel Gas to Mixing Point | [9 empty] | 50 |  | U | 2541
S-01722 | USY-2542 | U01 | Block Fuel Gas to Mixing Point | [9 empty] | 50 |  | U | 2542
S-01722 | USY-2543 | U01 | Bleed Fuel Gas to Mixing Point | [9 empty] | 50 |  | U | 2543
S-01722 | USY-2544 | U01 | Block Fuel Gas to H 2001 | [9 empty] | 50 |  | U | 2544
S-01722 | USY-2545 | U01 | Bleed Fuel Gas to H 2001 | [9 empty] | 50 |  | U | 2545
S-01722 | USY-2547 | U01 | Block Fuel Gas for Burner Tightness Test | [9 empty] | 50 |  | U | 2547
S-01722 | USY-2548 | U01 | Block Fuel Gas for Burner Tightness Test | [9 empty] | 50 |  | U | 2548
S-01722 | USY-2549 | U01 | Bleed Fuel Gas for Burner Tightness Test | [9 empty] | 50 |  | U | 2549
S-01722 | USY-3018 | P22 | [10 empty] | 50 |  | U | 3018
S-01722 | USY-3052 | P23 | Stop Continuous Blow Down from D 3003 MP Steam Drum | [9 empty] | 50 |  | U | 3052
S-01722 | USY-3172 | P27 | Stop Crude Methanol from D 3001 HP Separator | [9 empty] | 50 |  | U | 3172
S-01722 | USY-5012 | P29 | P 5001 A Raw Methanol Pump | [9 empty] | 50 |  | U | 5012
S-01722 | USY-5016 | P29 | P 5001 B Raw Methanol Pump | [9 empty] | 50 |  | U | 5016
S-01722 | USY-5076 | P31 | P 5011 A Steam Condensate Pump | [9 empty] | 50 |  | U | 5076
S-01722 | USY-5080 | P31 | P 5011 B Steam Condensate Pump | [9 empty] | 50 |  | U | 5080
S-01722 | USY-5100 | P32 | P 5003 A Stabilizer Column Reflux Pump | [9 empty] | 50 |  | U | 5100
S-01722 | USY-5104 | P32 | P 5003 B Stabilizer Column Reflux Pump | [9 empty] | 50 |  | U | 5104
S-01722 | USY-5132 | P33 | P 5002 A Stabilizer Methanol Pump | [9 empty] | 50 |  | U | 5132
S-01722 | USY-5136 | P33 | P 5002 B Stabilizer Methanol Pump | [9 empty] | 50 |  | U | 5136
S-01722 | USY-5211 | P36 | P 5004 A LP Column Reflux Pump | [9 empty] | 50 |  | U | 5211
S-01722 | USY-5215 | P36 | P 5004 B LP Column Reflux Pump | [9 empty] | 50 |  | U | 5215
S-01722 | USY-5232 | P37 | P 5005 A MP Column Feed Pump | [9 empty] | 50 |  | U | 5232
S-01722 | USY-5236 | P37 | P 5005 B MP Column Feed Pump | [9 empty] | 50 |  | U | 5236
S-01722 | USY-5302 | P39 | Stop LP Steam to E 5003 1/2/3 MP Column Reboiler No. 1 | [9 empty] | 50 |  | U | 5302
S-01722 | USY-5328 | P40 | P 5006 A MP Column Reflux Pump | [9 empty] | 50 |  | U | 5328
S-01722 | USY-5332 | P40 | P 5006 B MP Column Reflux Pump | [9 empty] | 50 |  | U | 5332
S-01722 | USY-5352 | P41 | P 5007 A MP Column Recycle Pump | [9 empty] | 50 |  | U | 5352
S-01722 | USY-5356 | P41 | P 5007 B MP Column Recycle Pump | [9 empty] | 50 |  | U | 5356
S-01722 | USY-5360 | P41 | P 5010 A Excess Water Pump | [9 empty] | 50 |  | U | 5360
S-01722 | USY-5364 | P41 | P 5010 B Excess Water Pump | [9 empty] | 50 |  | U | 5364
S-01722 | USY-5391 | P43 | Stop Methanol Product to TK 5002 1 | [9 empty] | 50 |  | U | 5391
S-01722 | USY-5392 | P43 | Stop Methanol Product to TK 5002 2 | [9 empty] | 50 |  | U | 5392
S-01722 | USY-5393 | P43 | Stop Methanol Product from PK 5008 A/B | [9 empty] | 50 |  | U | 5393
S-01722 | USY-5403 | P43 | P 5012 Methanol Start-up Pump | [9 empty] | 50 |  | U | 5403
S-01722 | USY-5420 | P44 | Stop Methanol Product from T 5002 2 | [9 empty] | 50 |  | U | 5420
S-01722 | USY-5421 | P44 | Stop Methanol Product from P 5008 A/B | [9 empty] | 50 |  | U | 5421
S-01722 | USY-5422 | P44 | Stop Methanol Product from T 5002 1 | [9 empty] | 50 |  | U | 5422
S-01722 | USY-5424 | P44 | P 5008 A Methanol Product Pump | [9 empty] | 50 |  | U | 5424
S-01722 | USY-5428 | P44 | P 5008 B Methanol Product Pump | [9 empty] | 50 |  | U | 5428
S-01722 | USY-5454 | P45 | P 5009 A Liquid Off-stream Pump | [9 empty] | 50 |  | U | 5454
S-01722 | USY-5458 | P45 | P 5009 B Liquid Off-stream Pump | [9 empty] | 50 |  | U | 5458
S-01722 | USY-6003 | P05 | P 6002 A Steam Condensate Return Pump | [9 empty] | 50 |  | U | 6003
S-01722 | USY-6007 | P05 | P 6002 B Steam Condensate Return Pump | [9 empty] | 50 |  | U | 6007
S-01722 | USY-6061 | P07 | P 6001 A Saturator Circulation Pump | [9 empty] | 50 |  | U | 6061
S-01722 | USY-6065 | P07 | P 6001 B Saturator Circulation Pump | [9 empty] | 50 |  | U | 6065
S-01722 | USY-6081 | P08 | Blowdown to D 6002 Saturator Blowdown Drum | [9 empty] | 50 |  | U | 6081
S-01722 | USY-6082 | P08 | Blowdown to D 6002 Saturator Blowdown Drum | [9 empty] | 50 |  | U | 6082
S-01722 | USY-7130 | U10 | Stop HP Steam to FP 7001 A Steam Turbine for FP 7001 A | [9 empty] | 50 |  | U | 7130
S-01722 | USY-7135 | U10 | Stop HP Steam to FP 7001 B Steam Turbine for FP 7001 B | [9 empty] | 50 |  | U | 7135
S-01722 | UV-2125 | P11 | Stop Vent Gas to Air Intake | 24"-VG-50-101-B40-N | Vent Gas | 0 | 45 | 3.5 |  | 100 | bar g | °C | 243 |  | U | 2125
S-01722 | UV-2233 | P13 | Quench of Process Gas | 3"-PRC-20-102-G40-N | Process Condensate | 52 | 49 | 80 |  | 106 | bar g | °C | 243 |  | U | 2233
S-01722 | UV-5021 | P29 | Outlet T 5004 Vent Wash Column, Vent | 24"-VA-50-140-B40-N | Vent to Atmosphere | 0 | 45 | 3.5 |  | 100 | bar g | °C | 243 |  | U | 5021
S-01722 | UV-6035 | P06 | Outlet X 6001 A/B Particle Filter | 8"-PRC-60-102-G40-H | Process Condensate | 44 | 119 | 71 |  | 180 | bar g | °C | 243 |  | U | 6035
S-01722 | UY-2125 | P11 | Stop Vent Gas to Air Intake | [9 empty] | 50 |  | U | 2125
S-01722 | UY-2233 | P13 | Quench of Process Gas | [9 empty] | 50 |  | U | 2233
S-01722 | UY-2576 | U02 | C 2001 Start-up Nitrogen Compressor | [9 empty] | 50 |  | U | 2576
S-01722 | UY-5021 | P29 | Outlet T 5004 Vent Wash Column, Vent | [9 empty] | 50 |  | U | 5021
S-01722 | UY-6035 | P06 | Outlet X 6001 A/B Particle Filter | [9 empty] | 50 |  | U | 6035
S-01722 | UY-6083 | P08 | P 7003 A Excess Process Condensate Pump | [9 empty] | 50 |  | U | 6083
S-01722 | UY-6084 | P08 | P 7003 B Excess Process Condensate Pump | [9 empty] | 50 |  | U | 6084
S-01722 | UY-7101 | U22 | P 7004 A Excess Process Condensate Pump | [9 empty] | 50 |  | U | 7101
S-01722 | UY-7103 | U22 | P 7004 B Excess Process Condensate Pump | [9 empty] | 50 |  | U | 7103
S-01722 | UY-7121 | U10 | P 7001 C BFW Pump | [9 empty] | 50 |  | U | 7121
S-01722 | XA-2124 | P11 | F 2002 Combustion Air Blower | [9 empty] | 50 |  | X | 2124
S-01722 | XA-2159 | P12 | F 2001 Flue Gas Blower | [9 empty] | 50 |  | X | 2159
S-01722 | XA-2410 | P19 | P 2001 A Process Condensate Pump No. 1 | [9 empty] | 50 |  | X | 2410
S-01722 | XA-2414 | P19 | P 2001 B Process Condensate Pump No. 1 | [9 empty] | 50 |  | X | 2414
S-01722 | XA-2447 | P20 | P 2002 A Process Condensate Pump No. 2 | [9 empty] | 50 |  | X | 2447
S-01722 | XA-2451 | P20 | P 2002 B Process Condensate Pump No. 2 | [9 empty] | 50 |  | X | 2451
S-01722 | XA-2487 | P21 | P 2003 A Process Condensate Pump No. 3 | [9 empty] | 50 |  | X | 2487
S-01722 | XA-2491 | P21 | P 2003 B Process Condensate Pump No. 3 | [9 empty] | 50 |  | X | 2491
S-01722 | XA-2577 | U02 | C 2001 Start-up Nitrogen Compressor | [9 empty] | 50 |  | X | 2577
S-01722 | XA-3141 | P26 | AE 3002 1 Loop Air Cooler | [9 empty] | 50 |  | X | 3141
S-01722 | XA-3144 | P26 | AE 3002 2 Loop Air Cooler | [9 empty] | 50 |  | X | 3144
S-01722 | XA-3147 | P26 | AE 3002 3 Loop Air Cooler | [9 empty] | 50 |  | X | 3147
S-01722 | XA-5013 | P29 | P 5001 A Raw Methanol Pump | [9 empty] | 50 |  | X | 5013
S-01722 | XA-5017 | P29 | P 5001 B Raw Methanol Pump | [9 empty] | 50 |  | X | 5017
S-01722 | XA-5077 | P31 | P 5011 A Steam Condensate Pump | [9 empty] | 50 |  | X | 5077
S-01722 | XA-5081 | P31 | P 5011 B Steam Condensate Pump | [9 empty] | 50 |  | X | 5081
S-01722 | XA-5092 | P32 | AE 5004 Stabilizer Column OH Condenser | [9 empty] | 50 |  | X | 5092
S-01722 | XA-5101 | P32 | P 5003 A Stabilizer Column Reflux Pump | [9 empty] | 50 |  | X | 5101
S-01722 | XA-5105 | P32 | P 5003 B Stabilizer Column Reflux Pump | [9 empty] | 50 |  | X | 5105
S-01722 | XA-5133 | P33 | P 5002 A Stabilizer Methanol Pump | [9 empty] | 50 |  | X | 5133
S-01722 | XA-5137 | P33 | P 5002 B Stabilizer Methanol Pump | [9 empty] | 50 |  | X | 5137
S-01722 | XA-5201 | P36 | AE 5005 LP Column OH Condenser | [9 empty] | 50 |  | X | 5201
S-01722 | XA-5212 | P36 | P 5004 A LP Column Reflux Pump | [9 empty] | 50 |  | X | 5212
S-01722 | XA-5216 | P36 | P 5004 B LP Column Reflux Pump | [9 empty] | 50 |  | X | 5216
S-01722 | XA-5232 | U15 | P 5080 A Morpholine Dosing Pump | [9 empty] | 50 |  | X | 5232
S-01722 | XA-5233 | P37 | P 5005 A MP Column Feed Pump | [9 empty] | 50 |  | X | 5233
S-01722 | XA-5236 | U15 | P 5080 B Morpholine Dosing Pump | [9 empty] | 50 |  | X | 5236
S-01722 | XA-5237 | P37 | P 5005 B MP Column Feed Pump | [9 empty] | 50 |  | X | 5237
S-01722 | XA-5329 | P40 | P 5006 A MP Column Reflux Pump | [9 empty] | 50 |  | X | 5329
S-01722 | XA-5333 | P40 | P 5006 B MP Column Reflux Pump | [9 empty] | 50 |  | X | 5333
S-01722 | XA-5353 | P41 | P 5007 A MP Column Recycle Pump | [9 empty] | 50 |  | X | 5353
S-01722 | XA-5357 | P41 | P 5007 B MP Column Recycle Pump | [9 empty] | 50 |  | X | 5357
S-01722 | XA-5361 | P41 | P 5010 A Excess Water Pump | [9 empty] | 50 |  | X | 5361
S-01722 | XA-5365 | P41 | P 5010 B Excess Water Pump | [9 empty] | 50 |  | X | 5365
S-01722 | XA-5368 | P41 | AE 5006 Wash Water Air Cooler | [9 empty] | 50 |  | X | 5368
S-01722 | XA-5425 | P44 | P 5008 A Methanol Product Pump | [9 empty] | 50 |  | X | 5425
S-01722 | XA-5429 | P44 | P 5008 B Methanol Product Pump | [9 empty] | 50 |  | X | 5429
S-01722 | XA-5455 | P45 | P 5009 A Liquid Off-stream Pump | [9 empty] | 50 |  | X | 5455
S-01722 | XA-5459 | P45 | P 5009 B Liquid Off-stream Pump | [9 empty] | 50 |  | X | 5459
S-01722 | XA-5511 | U24 | P 5070 A NaOH Solution Dosing Pump (optional) | [9 empty] | 50 |  | X | 5511
S-01722 | XA-5512 | U24 | P 5070 B NaOH Solution Dosing Pump (optional) | [9 empty] | 50 |  | X | 5512
S-01722 | XA-6004 | P05 | P 6002 A Steam Condensate Return Pump | [9 empty] | 50 |  | X | 6004
S-01722 | XA-6008 | P05 | P 6002 B Steam Condensate Return Pump | [9 empty] | 50 |  | X | 6008
S-01722 | XA-6062 | P07 | P 6001 A Saturator Circulation Pump | [9 empty] | 50 |  | X | 6062
S-01722 | XA-6066 | P07 | P 6001 B Saturator Circulation Pump | [9 empty] | 50 |  | X | 6066
S-01722 | XA-7005 | U18 | P 7002 A Demineralized Water Pump | [9 empty] | 50 |  | X | 7005
S-01722 | XA-7006 | U18 | P 7002 B Demineralized Water Pump | [9 empty] | 50 |  | X | 7006
S-01722 | XA-7101 | U22 | P 7004 A Excess Process Condensate Pump | [9 empty] | 50 |  | X | 7101
S-01722 | XA-7103 | U22 | P 7004 B Excess Process Condensate Pump | [9 empty] | 50 |  | X | 7103
S-01722 | XA-7122 | U10 | P 7001 C BFW Pump | [9 empty] | 50 |  | X | 7122
S-01722 | XA-7163 | U12 | P 7051 A Phosphate Dosing Pump | [9 empty] | 50 |  | X | 7163
S-01722 | XA-7166 | U12 | P 7051 B Phosphate Dosing Pump | [9 empty] | 50 |  | X | 7166
S-01722 | XA-7169 | U12 | P 7052 A Phosphate Dosing Pump | [9 empty] | 50 |  | X | 7169
S-01722 | XA-7172 | U12 | P 7052 B Phosphate Dosing Pump | [9 empty] | 50 |  | X | 7172
S-01722 | XA-7193 | U13 | P 7060 A Ammonia Dosing Pump | [9 empty] | 50 |  | X | 7193
S-01722 | XA-7196 | U13 | P 7060 B Ammonia Dosing Pump | [9 empty] | 50 |  | X | 7196
S-01722 | XA-7213 | U14 | P 7070 A Oxygen Scavenger Dosing Pump | [9 empty] | 50 |  | X | 7213
S-01722 | XA-7216 | U14 | P 7070 B Oxygen Scavenger Dosing Pump | [9 empty] | 50 |  | X | 7216
S-01722 | XAL-2284 | P15 | Hazard Flashers H 2001 Primary Reformer | [9 empty] | 50 |  | X | 2284
S-01722 | YL-2124 | P11 | F 2002 Combustion Air Blower | [9 empty] | 50 |  | Y | 2124
S-01722 | YL-2159 | P12 | F 2001 Flue Gas Blower | [9 empty] | 50 |  | Y | 2159
S-01722 | YL-2410 | P19 | P 2001 A Process Condensate Pump No. 1 | [9 empty] | 50 |  | Y | 2410
S-01722 | YL-2414 | P19 | P 2001 B Process Condensate Pump No. 1 | [9 empty] | 50 |  | Y | 2414
S-01722 | YL-2447 | P20 | P 2002 A Process Condensate Pump No. 2 | [9 empty] | 50 |  | Y | 2447
S-01722 | YL-2451 | P20 | P 2002 B Process Condensate Pump No. 2 | [9 empty] | 50 |  | Y | 2451
S-01722 | YL-2471 | P21 | AE 2026 Air Cooler | [9 empty] | 50 |  | Y | 2471
S-01722 | YL-2487 | P21 | P 2003 A Process Condensate Pump No. 3 | [9 empty] | 50 |  | Y | 2487
S-01722 | YL-2491 | P21 | P 2003 B Process Condensate Pump No. 3 | [9 empty] | 50 |  | Y | 2491
S-01722 | YL-5013 | P29 | P 5001 A Raw Methanol Pump | [9 empty] | 50 |  | Y | 5013
S-01722 | YL-5017 | P29 | P 5001 B Raw Methanol Pump | [9 empty] | 50 |  | Y | 5017
S-01722 | YL-5077 | P31 | P 5011 A Steam Condensate Pump | [9 empty] | 50 |  | Y | 5077
S-01722 | YL-5081 | P31 | P 5011 B Steam Condensate Pump | [9 empty] | 50 |  | Y | 5081
S-01722 | YL-5101 | P32 | P 5003 A Stabilizer Column Reflux Pump | [9 empty] | 50 |  | Y | 5101
S-01722 | YL-5105 | P32 | P 5003 B Stabilizer Column Reflux Pump | [9 empty] | 50 |  | Y | 5105
S-01722 | YL-5133 | P33 | P 5002 A Stabilizer Methanol Pump | [9 empty] | 50 |  | Y | 5133
S-01722 | YL-5137 | P33 | P 5002 B Stabilizer Methanol Pump | [9 empty] | 50 |  | Y | 5137
S-01722 | YL-5212 | P36 | P 5004 A LP Column Reflux Pump | [9 empty] | 50 |  | Y | 5212
S-01722 | YL-5216 | P36 | P 5004 B LP Column Reflux Pump | [9 empty] | 50 |  | Y | 5216
S-01722 | YL-5233 | P37 | P 5005 A MP Column Feed Pump | [9 empty] | 50 |  | Y | 5233
S-01722 | YL-5237 | P37 | P 5005 B MP Column Feed Pump | [9 empty] | 50 |  | Y | 5237
S-01722 | YL-5329 | P40 | P 5006 A MP Column Reflux Pump | [9 empty] | 50 |  | Y | 5329
S-01722 | YL-5333 | P40 | P 5006 B MP Column Reflux Pump | [9 empty] | 50 |  | Y | 5333
S-01722 | YL-5353 | P41 | P 5007 A MP Column Recycle Pump | [9 empty] | 50 |  | Y | 5353
S-01722 | YL-5357 | P41 | P 5007 B MP Column Recycle Pump | [9 empty] | 50 |  | Y | 5357
S-01722 | YL-5361 | P41 | P 5010 A Excess Water Pump | [9 empty] | 50 |  | Y | 5361
S-01722 | YL-5365 | P41 | P 5010 B Excess Water Pump | [9 empty] | 50 |  | Y | 5365
S-01722 | YL-5404 | P43 | P 5012 Methanol Start-up Pump | [9 empty] | 50 |  | Y | 5404
S-01722 | YL-6004 | P05 | P 6002 A Steam Condensate Return Pump | [9 empty] | 50 |  | Y | 6004
S-01722 | YL-6008 | P05 | P 6002 B Steam Condensate Return Pump | [9 empty] | 50 |  | Y | 6008
S-01722 | YL-6062 | P07 | P 6001 A Saturator Circulation Pump | [9 empty] | 50 |  | Y | 6062
S-01722 | YL-6066 | P07 | P 6001 B Saturator Circulation Pump | [9 empty] | 50 |  | Y | 6066
S-01722 | YL-6081 | P08 | P 7003 A Excess Process Condensate Pump | [9 empty] | 50 |  | Y | 6081
S-01722 | YL-6086 | P08 | P 7003 B Excess Process Condensate Pump | [9 empty] | 50 |  | Y | 6086
S-01722 | YL-7005 | U18 | P 7002 A Demineralized Water Pump | [9 empty] | 50 |  | Y | 7005
S-01722 | YL-7006 | U18 | P 7002 B Demineralized Water Pump | [9 empty] | 50 |  | Y | 7006
S-01722 | YL-7122 | U10 | P 7001 C BFW Pump | [9 empty] | 50 |  | Y | 7122
S-01722 | ZIC-6025 | P06 | [10 empty] | 50 |  | Z | 6025

## Component Specifications_d
Job No. | Component Tag No. | J-No. | Component Description | Qty_Rem | P&I Diagram | Y-X | Equipment/Pipe | Operating Flow | Flow Unit | Design Pressure | Operating Pressure | Pressure Unit | Minimum Temperature | Operating Temperature | Design Temperature | Temperature Unit | Property 1 | Property 2 | Property 3 | Property 4 | Property 5 | Property 6 | Property 7 | Property 8 | Property 9 | Property 10 | Property 11 | Property 12 | Property 13 | Property 14 | Property 15 | Property 16 | Property 17 | Property 18 | Property 19 | Property 20 | Property 21 | Property 22 | Property 23 | Property 24 | Property 25 | Property 26 | Property 27 | Property 28 | Property 29 | Property 30 | Un | Type | Serial | Sub | Loop No.
S-02115 | FE-1006 | 201 | Orifice Plate Assembly | COUNTIF(Remarks!$B$2:$B$49988,'Component Specifications'!B2) | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 210000 Nm3/h | 59454 Nm3/h | 178361 Nm3/h |  |  | Gas | 52 bar g | 40 °C | 36.8 kg/m3 | 0.013 cP | 0.93 | 1.28 | 16.74 kg/kmol | 5000 mmWG | 317.5 (14", Sch.80) mm | 0.66 | AISI 316 |  |  | 14", Class 600, RF | [11 empty] | F | 1006 |  | FI-1006
S-02115 | FE-2007 | 201 | Orifice Plate Assembly |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 78000 Nm3/h | 21923 Nm3/h | 65769 Nm3/h |  |  | Gas | 40 bar g | 35 °C | 52.5 kg/m3 | 0.022 cP | 0.98 | 1.39 | 32.01 kg/kmol | 2500 mmWG | 257.5 (10", Sch.30) mm | 0.73 | Monel |  |  | 10", Class 600, RF | [11 empty] | F | 2007 |  | FIC-2007
S-02115 | FE-2009 | 201 | Orifice Plate Assembly |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 24000 Nm3/h | 6567 Nm3/h | 19700 Nm3/h |  |  | Gas | 40 bar g | 35 °C | 52.5 kg/m3 | 0.022 cP | 0.98 | 1.39 | 32.01 kg/kmol | 2500 mmWG | 146.3 (6", Sch.80S) mm | 0.71 | Monel |  |  | 6", Class 600, RF | [11 empty] | F | 2009 |  | FIC-2009
S-02115 | FE-2040 | 201 | Orifice Plate Assembly |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 9500 kg/h | 1529 kg/h | 4588 kg/h |  |  | Steam | 44 bar g | 345 °C | 17.2 kg/m3 | 0.022 cP | 0.91 | 1.19 | 18.02 kg/kmol | 2500 mmWG | 97.2 (4", Sch.80S) mm | 0.73 | AISI 410 |  |  | 4", Class 600, RF | [11 empty] | F | 2040 |  | FIC-2040
S-02115 | FE-2061 | 201 | Orifice Plate Assembly |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 500000 Nm3/h | 141316 Nm3/h | 423949 Nm3/h |  |  | Gas | 42.3 bar g | 262 °C | 18.1 kg/m3 | 0.019 cP | 0.94 | 1.19 | 17.47 kg/kmol | 5000 mmWG | 547.7 (24", Sch.80) mm | 0.71 | AISI 316 |  |  | 24", Class 600, RF | [11 empty] | F | 2061 |  | FIC-2061
S-02115 | FE-2072 | 201 | Orifice Plate Assembly |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 85000 kg/h | 10942 kg/h | 32826 kg/h |  |  | Steam | 44 bar g | 345 °C | 17.3 kg/m3 | 0.022 cP | 0.91 | 1.19 | 18.02 kg/kmol | 2500 mmWG | 288.9 (12", Sch.80) mm | 0.74 | AISI 410 |  |  | 12", Class 600, RF | [11 empty] | F | 2072 |  | FIC-2072
S-02115 | FE-2079 | 201 | Orifice Plate Assembly |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 6500 Nm3/h | 1688 Nm3/h | 5063 Nm3/h |  |  | Gas | 50.4 bar g | 48 °C | 17.80 kg/m3 | 0.015 cP | 1.01 | 1.39 | 9.4 kg/kmol | 2500 mmWG | 73.7 (3", Sch.80) mm | 0.55 | AISI 316 |  |  | 3", Class 600, RF | [11 empty] | F | 2079 |  | FIC-2079
S-02115 | FE-2091 | 201 | Orifice Plate Assembly |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 150000 Nm3/h | 42333 Nm3/h | 127000 Nm3/h |  |  | Gas | 42.3 bar g | 262 °C | 18.1 kg/m3 | 0.019 cP | 0.94 | 1.19 | 17.47 kg/kmol | 5000 mmWG | 288.9 (12", Sch.80) mm | 0.73 | AISI 316 |  |  | 12", Class 600, RF | [11 empty] | F | 2091 |  | FIC-2091
S-02115 | FE-2115 | 201 | Orifice Plate Assembly |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 29000 kg/h | 8172 kg/h | 24517 kg/h |  |  | Steam | 43 bar g | 345 °C | 16.9 kg/m3 | 0.022 cP | 0.91 | 1.19 | 18.02 kg/kmol | 2500 mmWG | 193.6 (8", Sch.80) mm | 0.67 | AISI 410 |  |  | 8", Class 600, RF | [11 empty] | F | 2115 |  | FI-2115
S-02115 | FE-2150 | 201 | Orifice Plate Assembly |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 6500 Nm3/h | 1548 Nm3/h | 4644 Nm3/h |  |  | Gas | 50.4 bar g | 48 °C | 17.8 kg/m3 | 0.015 cP | 1.01 | 1.39 | 9.37 kg/kmol | 2500 mmWG | 73.7 (3", Sch.80) mm | 0.55 | AISI 316 |  |  | 3", Class 600, RF | [11 empty] | F | 2150 |  | FIC-2150
S-02115 | FE-2151 | 201 | Orifice Plate Assembly |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 195000 Nm3/h | 54991 Nm3/h | 164973 Nm3/h |  |  | Gas | 50 bar g | 40 °C | 35.3 kg/m3 | 0.013 cP | 0.93 | 1.28 | 16.74 kg/kmol | 2500 mmWG | 317.5 (14", Sch.80) mm | 0.74 | AISI 316 |  |  | 14", Class 600, RF | [11 empty] | F | 2151 |  | FI-2151
S-02115 | FE-2165 | 201 | Orifice Plate Assembly |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 21000 kg/h | 5891 kg/h | 17674 kg/h |  |  | Steam | 43 bar g | 345 °C | 16.9 kg/m3 | 0.022 cP | 0.91 | 1.19 | 18.02 kg/kmol | 5000 mmWG | 146.3 (6", Sch.80) mm | 0.64 | AISI 410 |  |  | 6", Class 600, RF | [11 empty] | F | 2165 |  | FI-2165
S-02115 | FE-2233 | 201 | Orifice Plate Assembly |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 17000 kg/h |  | 0 kg/h |  |  | Liquid | 52 bar g | 49 °C | 944 kg/m3 | 0.23 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 77.9 (3", Sch.40S) mm | 0.48 | AISI 316 |  |  | 3", Class 900, RTJ | [11 empty] | F | 2233 |  | FIC-2233
S-02115 | FE-2417 | 201 | Orifice Plate Assembly |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 460000 kg/h | 130766 kg/h | 392298 kg/h |  |  | Liquid | 120 bar g | 122 °C | 947 kg/m3 | 0.23 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 273.1 (12", Sch.120) mm | 0.68 | AISI 316 |  |  | 12", Class 1500, RTJ | [11 empty] | F | 2417 |  | FIC-2417
S-02115 | FE-2476 | 201 | Orifice Plate Assembly |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 650000 Nm3/h | 184064 Nm3/h | 552191 Nm3/h |  |  | Gas | 24 bar g | 48 °C | 10.3 kg/m3 | 0.016 cP | 1.01 | 1.39 | 11.14 kg/kmol | 2500 mmWG | 686.0 (28", Sch.20) mm | 0.7 | AISI 316 |  |  | 32", Class 300,RF | [11 empty] | F | 2476 |  | FI-2476
S-02115 | FE-2536 | 201 | Orifice Plate Assembly |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 80000 Nm3/h | 22259 Nm3/h | 66777 Nm3/h |  |  | Gas | 3.6 bar g | 47 °C | 1.85 kg/m3 | 0.015 cP | 1 | 1.37 | 10.64 kg/kmol | 2500 mmWG | 590.6 (24", Sch.20) mm | 0.46 | AISI 316 |  |  | 24", Class 300, RF | [11 empty] | F | 2536 |  | FIC-2536
S-02115 | FE-2607 | 201 | Orifice Plate Assembly |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 6500 Nm3/h | 1548 Nm3/h | 5061 Nm3/h |  |  | Gas | 84 bar g | 48 °C | 28.8 kg/m3 | 0.016 cP | 1.04 | 1.38 | 9.37 kg/kmol | 2500 mmWG | 73.7 (3", Sch.80) mm | 0.49 | AISI 316 |  |  | 3", Class 900, RTJ | [11 empty] | F | 2607 |  | FI-2607
S-02115 | FE-3041 | 201 | Orifice Plate Assembly |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | 330000 kg/h | 94780 kg/h | 284348 kg/h |  |  | Liquid | 40.8 bar g | 230 °C | 828.7 kg/m3 | 0.12 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 242.9 (10", Sch.80) mm | 0.68 | AISI 316 |  |  | 10", Class 600, RF | [11 empty] | F | 3041 |  | FIC-3041
S-02115 | FE-3169 | 201 | Orifice Plate Assembly |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 80000 Nm3/h | 20758 Nm3/h | 62275 Nm3/h |  |  | Gas | 84 bar g | 48 °C | 28.8 kg/m3 | 0.016 cP | 1.04 | 1.38 | 9.37 kg/kmol | 5000 mmWG | 146.3 (6", Sch.80) mm | 0.69 | AISI 316 |  |  | 6", Class 900, RTJ | [11 empty] | F | 3169 |  | FIC-3169
S-02115 | FE-3171 | 201 | Orifice Plate Assembly |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 80000 Nm3/h | 20760 Nm3/h | 62275 Nm3/h |  |  | Gas | 84 bar g | 48 °C | 28.8 kg/m3 | 0.016 cP | 1.03 | 1.38 | 9.37 kg/kmol | 5000 mmWG | 146.3 (6", Sch.80) mm | 0.69 | AISI 316 |  |  | 6", Class 900, RTJ | [11 empty] | F | 3171 |  | FIC-3171
S-02115 | FE-3194 | 201 | Orifice Plate Assembly |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 6000 Nm3/h | 1308 Nm3/h | 3925 Nm3/h |  |  | Gas | 4 bar g | 48 °C | 4.92 kg/m3 | 0.016 cP | 0.99 | 1.3 | 25.95 kg/kmol | 2500 mmWG | 211.6 (8", Sch.10S) mm | 0.45 | AISI 316 |  |  | 8", Class 300, RF | [11 empty] | F | 3194 |  | FI-3194
S-02115 | FE-5020 | 201 | Orifice Plate Assembly |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 10000 kg/h | 2732 kg/h | 8197 kg/h |  |  | Liquid | 4 bar g | 48 °C | 989 kg/m3 | 0.57 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 52.5 (2", Sch.40) mm | 0.54 | AISI 316 |  |  | 2", Class 300, RF | [11 empty] | F | 5020 |  | FIC-5020
S-02115 | FE-5041 | 201 | Orifice Plate Assembly |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 290000 kg/h | 81846 kg/h | 245539 kg/h |  |  | Liquid | 5 bar g | 47 °C | 792 kg/m3 | 0.44 cP |  |  | 28.94 kg/kmol | 2500 mmWG | 264.7 (10", Sch.10S) mm | 0.6 | AISI 316 |  |  | 10", Class 300, RF | [11 empty] | F | 5041 |  | FIC-5041
S-02115 | FE-5068 | 201 | Orifice Plate Assembly |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 40000 kg/h | 11372 kg/h | 34117 kg/h |  |  | Steam | 7 bar g | 188 °C | 3.97 kg/m3 | 0.016 cP | 0.95 | 1.23 | 18.02 kg/kmol | 2500 mmWG | 333.4 (14", Sch.40) mm | 0.66 | AISI 316 |  |  | 14", Class 300, RF | [11 empty] | F | 5068 |  | FI-5068
S-02115 | FE-5093 | 201 | Orifice Plate Assembly |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 135000 kg/h | 37068 kg/h | 111205 kg/h |  |  | Liquid | 3.8 bar g | 65 °C | 752 kg/m3 | 0.33 cP |  |  | 32.47 kg/kmol | 2500 mmWG | 211.6 (8", Sch.10) mm | 0.53 | AISI 316 |  |  | 8", Class 300, RF | [11 empty] | F | 5093 |  | FIC-5093
S-02115 | FE-5107 | 201 | Orifice Plate Assembly |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 1200 kg/h | 333 kg/h | 1000 kg/h |  |  | Liquid | 3.8 bar g | 65 °C | 752 kg/m3 | 0.33 cP |  |  | 32.48 kg/kmol | 2500 mmWG | 52.5 (2", Sch.40) mm | 0.21 | AISI 316 |  |  | 2", Class 300, RF | [11 empty] | F | 5107 |  | FIC-5107
S-02115 | FE-5111 | 201 | Orifice Plate Assembly |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 700 Nm3/h | 192 Nm3/h | 577 Nm3/h |  |  | Gas | 0.6 bar g | 48 °C | 2.02 kg/m3 | 0.012 cP | 0.99 | 1.2 | 43.68 kg/kmol | 2500 mmWG | 161.5 (6", Sch.10) mm | 0.32 | AISI 316 |  |  | 6", Class 300, RF | [11 empty] | F | 5111 |  | FI-5111
S-02115 | FE-5161 | 201 | Orifice Plate Assembly |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 290000 kg/h | 81473 kg/h | 244420 kg/h |  |  | Liquid | 2.5 bar g | 88 °C | 753 kg/m3 | 0.27 cP |  |  | 28.9 kg/kmol | 2500 mmWG | 260.4 (10", Sch.20) mm | 0.62 | AISI 316 |  |  | 10", Class 300, RF | [11 empty] | F | 5161 |  | FIC-5161
S-02115 | FE-5203 | 201 | Orifice Plate Assembly |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 340000 kg/h | 93895 kg/h | 281685 kg/h |  |  | Liquid | 4 bar g | 65 °C | 750 kg/m3 | 0.33 cP |  |  | 32.04 kg/kmol | 2500 mmWG | 311.2 (12", Sch.20) mm | 0.57 | AISI 316 |  |  | 12", Class 300, RF | [11 empty] | F | 5203 |  | FIC-5203
S-02115 | FE-5239 | 201 | Orifice Plate Assembly |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 140000 kg/h | 39738 kg/h | 118412 kg/h |  |  | Liquid | 6.5 bar g | 86 °C | 785 kg/m3 | 0.29 cP |  |  | 26.2 kg/kmol | 2500 mmWG | 206.3 (8", Sch.20) mm | 0.54 | AISI 316 |  |  | 8", Class 300, RF | [11 empty] | F | 5239 |  | FIC-5239
S-02115 | FE-5301 | 201 | Orifice Plate Assembly |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 230000 kg/h | 63468 kg/h | 190404 kg/h |  |  | Steam | 7 bar g | 188 °C | 3.97 kg/m3 | 0.016 cP | 0.95 | 1.23 | 18.02 kg/kmol | 2500 mmWG | 768.0.(32", t=22.5 mm) mm | 0.68 | AISI 316 |  |  | 32", Class 300, RF | [11 empty] | F | 5301 |  | FIC-5301
S-02115 | FE-5321 | 201 | Orifice Plate Assembly |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 420000 kg/h | 115585 kg/h | 346756 kg/h |  |  | Liquid | 6 bar g | 101 °C | 711 kg/m3 | 0.23 cP |  |  | 32.04 kg/kmol | 2500 mmWG | 303.2 (12", Sch.40) mm | 0.64 | AISI 316 |  |  | 12", Class 300, RF | [11 empty] | F | 5321 |  | FIC-5321
S-02115 | FE-5367 | 201 | Orifice Plate Assembly |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 32000 kg/h | 8799 kg/h | 26938 kg/h |  |  | Liquid | 50 bar g | 150 °C | 920 kg/m3 | 0.19 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 73.7 (3", Sch.80) mm | 0.67 | AISI 316 |  |  | 3", Class 600, RF | [11 empty] | F | 5367 |  | FIC-5367
S-02115 | FE-5383 | 201 | Orifice Plate Assembly |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | 8000 kg/h | 2000 kg/h | 0 kg/h |  |  | Liquid | 5 bar g | 35 °C | 994 kg/m3 | 0.72 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 54.8 (2", Sch.10S) mm | 0.47 | AISI 316 |  |  | 2", Class 300, RF | [11 empty] | F | 5383 |  | FIC-5383
S-02115 | FE-5407 | 201 | Orifice Plate Assembly |  | P43 |  | 3"-PMP-50-161-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | 10000 kg/h | 2400 kg/h | 7200 kg/h |  |  | Liquid | 48 bar g | 48 °C | 766 kg/m3 | 0.40 cP |  |  |  | 2500 mmWG | 77.9 (3", Sch.40) mm | 0.4 | AISI 316 |  |  | 3", Class 300, RF | [11 empty] | F | 5407 |  | FI-5407
S-02115 | FE-5441 | 201 | Orifice Plate Assembly |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 2900 kg/h | 822 kg/h | 2465 kg/h |  |  | Liquid | 3.4 bar g | 115 °C | 747 kg/m3 | 0.22 cP |  |  | 27.23 kg/kmol | 2500 mmWG | 54.8 (2", Sch.10) mm | 0.31 | AISI 316 |  |  | 2", Class 300, RF | [11 empty] | F | 5441 |  | FIC-5441
S-02115 | FE-5501 | 201 | Orifice Plate Assembly |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | 32000 kg/h | 8799 kg/h | 27742 kg/h |  |  | Liquid | 3.6 bar g | 149 °C | 918 kg/m3 | 0.19 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 73.7 (3", Sch.80) mm | 0.67 | AISI 316 |  |  | ", Class 300, RF | [11 empty] | F | 5501 |  | FIC-5501
S-02115 | FE-6031 | 201 | Orifice Plate Assembly |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 245000 kg/h | 69680 kg/h | 209041 kg/h |  |  | Liquid | 44 bar g | 119 °C | 945 kg/m3 | 0.24 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 193.6 (8", Sch.80S) mm | 0.7 | AISI 316 |  |  | 8", Class 900, RTJ | [11 empty] | F | 6031 |  | FIC-6031
S-02115 | FE-6032 | 201 | Orifice Plate Assembly |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 60000 kg/h |  | 0 kg/h |  |  | Liquid | 50 bar g | 122 °C | 944 kg/m3 | 0.23 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 97.2 (4", Sch.80) mm | 0.69 | AISI 316 |  |  | 4", Class 600, RF | [11 empty] | F | 6032 |  | FI-6032
S-02115 | FE-6057 | 201 | Orifice Plate Assembly |  | P07 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 5500 kg/h | 822 kg/h | 2465 kg/h |  |  | Liquid | 50 bar g | 50 °C | 813 kg/m3 | 0.46 cP |  |  | 27.23 kg/kmol | 2500 mmWG | 49.3 (2", Sch.80) mm | 0.45 | AISI 316 |  |  | 2", Class 600, RF |  | Yes | [9 empty] | F | 6057 |  | FI-6057
S-02115 | FE-6068 | 201 | Orifice Plate Assembly |  | P07 |  | 10"-PRC-60-111-G40-H |  |  | 72 | 44 | bar g |  | 225 | 290 | °C | 310000 kg/h | 87083 kg/h | 261250 kg/h |  |  | Liquid | 44 bar g | 225 °C | 834 kg/m3 | 0.12 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 242.9 (10", Sch.80) mm | 0.66 | AISI 316 |  |  | 10", Class 900, RTJ | [11 empty] | F | 6068 |  | FI-6068
S-02115 | FE-6070 | 201 | Orifice Plate Assembly |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 200000 Nm3/h | 57215 Nm3/h | 171646 Nm3/h |  |  | Gas | 43.8 bar g | 358 °C | 14.2 kg/m3 | 0.021 cP | 1.01 | 1.19 | 16.66 kg/kmol | 2500 mmWG | 363.6 (16", Sch.80) mm | 0.7 | AISI 410 |  |  | 16", Class 600, RF | [11 empty] | F | 6070 |  | FIC-6070
S-02115 | FE-6081 | 201 | Orifice Plate Assembly |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 8000 kg/h | 2100 kg/h | 6179 kg/h |  |  | Liquid | 44 bar g | 57 °C | 975 kg/m3 | 0.36 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 52.5 (2", Sch.40S) mm | 0.49 | AISI 316 |  |  | 4", Class 900, RTJ | [11 empty] | F | 6081 |  | FIC-6081
S-02115 | FE-6082 | 201 | Orifice Plate Assembly |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | 8000 kg/h | 2100 kg/h | 6179 kg/h |  |  | Liquid | 2.5 bar g | 65 °C | 980 kg/m3 | 0.43 cP |  |  |  | 2500 mmWG | 54.8 (2", Sch.10S) mm | 0.47 | AISI 316 | [14 empty] | F | 6082 |  | FIC-6082
S-02115 | FE-6086 | 201 | Orifice Plate Assembly |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 60000 kg/h | 20000 kg/h | 0 kg/h |  |  | Liquid | 43 bar g | 225 °C | 834 kg/m3 | 0.12 cP |  |  | 18.02 kg/kmol | 2500 mmWG | 102.2 (4", Sch.40S) mm | 0.68 | AISI 316 |  |  | 3", Class 900, RTJ | [11 empty] | F | 6086 |  | FIC-6086
S-02115 | FE-7001 | 201 | Orifice Plate Assembly |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 175000 kg/h | 49100 kg/h | 147277 kg/h |  |  | Steam | 45 bar g | 355 °C | 17.3 kg/m3 | 0.023 cP | 0.91 | 1.2 | 18.02 kg/kmol | 5000 mmWG | 363.6 (16", Sch.80) mm | 0.72 | AISI 410 |  |  | 16", Class 600, RF | [11 empty] | F | 7001 |  | FI-7001
S-02115 | FE-7029 | 201 | Orifice Plate Assembly |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 250000 kg/h | 38250 kg/h | 97820 kg/h |  |  | Steam | 43 bar g | 410 °C | 33 kg/m3 | 0.027 cP | 0.89 | 1.18 | 18.02 kg/kmol | 2500 mmWG | 547.7 (24", Sch.80) mm | 0.6 | AISI 410 |  |  | 24", Class 600, RF | [11 empty] | F | 7029 |  | FI-7029
S-02115 | FE-7030 | 201 | Orifice Plate Assembly |  | U04 |  | 24"-HPS-70-136-F34-H |  |  | 52 | 42 | bar g |  | 410 | 470 | °C | 225000 kg/h | 55000 kg/h | 0 kg/h |  |  | Steam | 42 bar g | 410 °C | 14.5 kg/m3 | 0.025 cP | 0.94 | 1.23 | 18.02 kg/kmol | 2500 mmWG | 547.7 (24", Sch.80) mm | 0.68 | AISI 410 |  |  | 24", Class 600, RF | [11 empty] | F | 7030 |  | FI-7030
S-02115 | FE-7091 | 201 | Orifice Plate Assembly |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 400000 kg/h | 72775 kg/h | 218326 kg/h |  |  | Liquid | 4.5 bar g | 69 °C | 977 kg/m3 | 0.39 cP |  |  | 18.02 kg/kmol | 4000 mmWG | 211.6 (8", Sch.10S) mm | 0.72 | AISI 316 |  |  | 8", Class 300, RF | [11 empty] | F | 7091 |  | FIC-7091
S-02115 | FE-7101 | 201 | Orifice Plate Assembly |  | U22 |  | 2"-PRC-70-141-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | 6000 kg/h | 3000 kg/h | 5000 kg/h |  |  | Liquid | 46 bar g | 65 °C | 980 kg/m3 | 0.43 cP |  |  |  | 2500 mmWG | 52.5 (2", Sch.40S) mm | 0.43 | AISI 316 |  |  | 2", Class 900, RTJ | [11 empty] | F | 7101 |  | FI-7101
S-02115 | FE-7129 | 201 | Orifice Plate Assembly |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 16000 kg/h | 4406 kg/h | 13217 kg/h |  |  | Steam | 43 bar g | 345 °C | 16.9 kg/m3 | 0.022 cP | 0.91 | 1.19 | 18.02 kg/kmol | 2500 mmWG | 193.6 (8", Sch.80) mm | 0.51 | AISI 410 |  |  | 8", Class 600, RF | [11 empty] | F | 7129 |  | FI-7129
S-02115 | FE-7134 | 201 | Orifice Plate Assembly |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 16000 kg/h | 4406 kg/h | 13217 kg/h |  |  | Steam | 43 bar g | 345 °C | 16.9 kg/m3 | 0.022 cP | 0.91 | 1.19 | 18.02 kg/kmol | 2500 mmWG | 193.6 (8", Sch.80) mm | 0.51 | AISI 410 |  |  | 8", Class 600, RF | [11 empty] | F | 7134 |  | FI-7134
S-02115 | FE-7141 | 201 | Orifice Plate Assembly |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 300000 kg/h |  | 0 kg/h |  |  | Liquid | 120 bar g | 122 °C | 947 kg/m3 | 0.23 cP |  |  | 18.02 kg/kmol | 5000 mmWG | 182.6 (8", Sch.120) mm | 0.69 | AISI 316 |  |  | 8", Class 1500, RTJ | [11 empty] | F | 7141 |  | FIC-7141
S-02115 | FE-2372 | 201.1 | ISA 1932 Flow Nozzle |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 460000 kg/h | 129458 kg/h | 388375 kg/h |  |  | Steam | 102 bar g | 313 °C | 57.5 kg/m3 | 0.022 cP | 0.66 | 1.05 | 18.02 kg/kmol | 2500 mmWG | 398 (18", Sch.100) mm | 0.74 | AISI 316 |  |  | 18", Class 900, RTJ | [11 empty] | F | 2372 |  | FI-2372
S-02115 | FE-3020 | 201.1 | ISA 1932 Flow Nozzle |  | P22 |  | 18"-SG-30-101-H40-H |  |  | 99 | 80 | bar g |  | 122 | 165 | °C | 650000 Nm3/h | 183490 Nm3/h | 550469 Nm3/h |  |  | Gas | 90 bar g | 131 °C | 29.0 kg/m3 | 0.02 cP | 1.04 | 1.39 | 11.12 kg/kmol | 2500 mmWG | 410 (18", Sch.80) mm | 0.72 | AISI 316 |  |  | 18", Class 1500, RTJ | [11 empty] | F | 3020 |  | FI-3020
S-02115 | FE-3050 | 201.1 | ISA 1932 Flow Nozzle |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 330000 kg/h | 93830 kg/h | 281504 kg/h |  |  | Steam | 40.8 bar g | 253 °C | 21.1 kg/m3 | 0.019 cP | 0.82 | 1.11 | 18.02 kg/kmol | 2500 mmWG | 548 (24", Sch.80) mm | 0.6 | AISI 316 |  |  | 24", Class 600, RF | [11 empty] | F | 3050 |  | FI-3050
S-02115 | FE-3167 | 201.1 | ISA 1932 Flow Nozzle |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 2000000 Nm3/h | 549650 Nm3/h | 1648950 Nm3/h |  |  | Gas | 84 bar g | 48 °C | 28.8 kg/m3 | 0.016 cP | 1.04 | 1.38 | 9.37 kg/kmol | 2500 mmWG | 698 mm | 0.69 | AISI 316 |  |  | 30", Class 900, RTJ | [11 empty] | F | 3167 |  | FI-3167
S-02115 | FE-2111 | 201.2 | Venturi |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 420000 Nm3/h | 334601 Nm3/h | Gas | 1.034 bar a | 54 °C | 1.04 kg/m3 | 0.019 cP | 1 | 1.4 | 28.05 kg/kmol |  | By Comb. Air Blower Vendor mm | By Comb. Air Blower Vendor | By Comb. Air Blower Vendor |  |  | By vendor, Class 150,By vendor | 140083 Nm3/h | [13 empty] | F | 2111 |  | FIC-2111
S-02115 | TE-2234 | 202 | Thermocouple |  | P13 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | K | [30 empty] | T | 2234 |  | TI-2234
S-02115 | TE-2253 | 202 | Thermocouple |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | K | [30 empty] | T | 2253 |  | TIC-2253
S-02115 | TE-2254 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2254 |  | TI-2254
S-02115 | TE-2255 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2255 |  | TI-2255
S-02115 | TE-2256 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2256 |  | TI-2256
S-02115 | TE-2257 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2257 |  | TI-2257
S-02115 | TE-2258 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2258 |  | TI-2258
S-02115 | TE-2259 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2259 |  | TI-2259
S-02115 | TE-2260 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2260 |  | TI-2260
S-02115 | TE-2261 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2261 |  | TI-2261
S-02115 | TE-2262 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2262 |  | TI-2262
S-02115 | TE-2263 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2263 |  | TI-2263
S-02115 | TE-2264 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2264 |  | TI-2264
S-02115 | TE-2265 | 202 | Thermocouple |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | K | [30 empty] | T | 2265 |  | TI-2265
S-02115 | TE-2268 | 202 | Thermocouple |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | K | [30 empty] | T | 2268 |  | TI-2268
S-02115 | TE-2353 | 202 | Thermocouple |  | P17 |  | 24"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | K | [30 empty] | T | 2353 |  | TI-2353
S-02115 | TE-2354 | 202 | Thermocouple |  | P17 |  | 42"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | K | [30 empty] | T | 2354 |  | TI-2354
S-02115 | TE-2355 | 202 | Thermocouple |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | K | [30 empty] | T | 2355 |  | TI-2355
S-02115 | TE-2356 | 202 | Thermocouple |  | P17 |  | 24"-HHPS-20-117-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | K | [30 empty] | T | 2356 |  | TI-2356
S-02115 | TSE/A-2360 | 202 | Thermocouple |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | K | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TSE/B-2360 | 202 | Thermocouple |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | K | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TSE/C-2360 | 202 | Thermocouple |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | K | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TE-3084 | 202 | Thermocouple |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | K | [30 empty] | T | 3084 |  | TI-3084
S-02115 | TE-7021 | 202 | Thermocouple |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | K | [30 empty] | T | 7021 |  | TI-7021
S-02115 | TE-7026 | 202 | Thermocouple |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | K | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | TE-7027 | 202 | Thermocouple |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | K | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | TE-2154 | 203 | Thermocouple Assembly |  | P12 |  | WHS | [6 empty] | 236.3 |  | °C | N | J-203.1 | [29 empty] | T | 2154 |  | TI-2154
S-02115 | TE-2155 | 203 | Thermocouple Assembly |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | N | J-203.1 | [29 empty] | T | 2155 |  | TI-2155
S-02115 | TSE/A-2221 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | N | J-203.1 | [29 empty] | T | 2221 |  | TI-2221
S-02115 | TSE/B-2221 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | N | J-203.1 | [29 empty] | T | 2221 |  | TI-2221
S-02115 | TSE/C-2221 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | N | J-203.1 | [29 empty] | T | 2221 |  | TI-2221
S-02115 | TE-2226 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 1093 |  | °C | N | J-203.1 | [29 empty] | T | 2226 |  | TI-2226
S-02115 | TE-2227 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 794 |  | °C | N | J-203.1 | [29 empty] | T | 2227 |  | TI-2227
S-02115 | TE-2228 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | -0.02 | bar g |  | 439 |  | °C | N | J-203.1 | [29 empty] | T | 2228 |  | TI-2228
S-02115 | TE-2229 | 203 | Thermocouple Assembly |  | P13 |  | WHS |  |  |  | 0.05 | bar g |  | 350 |  | °C | N | J-203.1 | [29 empty] | T | 2229 |  | TI-2229
S-02115 | TE-2295 | 203 | Thermocouple Assembly |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | N | J-203.1 | [29 empty] | T | 2295 |  | TI-2295
S-02115 | TE-2297 | 203 | Thermocouple Assembly |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | N | J-203.1 | [29 empty] | T | 2297 |  | TI-2297
S-02115 | TE-2303 | 203 | Thermocouple Assembly |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | N | J-203.3 | [29 empty] | T | 2303 |  | TI-2303
S-02115 | TE-2304 | 203 | Thermocouple Assembly |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | N | J-203.3 | [29 empty] | T | 2304 |  | TI-2304
S-02115 | TSE/A-2305 | 203 | Thermocouple Assembly |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | N | J-203.3 | [29 empty] | T | 2305 |  | TI-2305
S-02115 | TSE/B-2305 | 203 | Thermocouple Assembly |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | N | J-203.3 | [29 empty] | T | 2305 |  | TI-2305
S-02115 | TSE/C-2305 | 203 | Thermocouple Assembly |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | N | J-203.3 | [29 empty] | T | 2305 |  | TI-2305
S-02115 | TSE/A-2325 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2325 |  | TI-2325
S-02115 | TSE/B-2325 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2325 |  | TI-2325
S-02115 | TSE/C-2325 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2325 |  | TI-2325
S-02115 | TSE/A-2329 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | K | J-203.7 | [29 empty] | T | 2329 |  | TI-2329
S-02115 | TSE/B-2329 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | K | J-203.7 | [29 empty] | T | 2329 |  | TI-2329
S-02115 | TSE/C-2329 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | K | J-203.2 | [29 empty] | T | 2329 |  | TI-2329
S-02115 | TSE/A-2333 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2333 |  | TI-2333
S-02115 | TSE/B-2333 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2333 |  | TI-2333
S-02115 | TSE/C-2333 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2333 |  | TI-2333
S-02115 | TSE/A-2334 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2334 |  | TI-2334
S-02115 | TSE/B-2334 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2334 |  | TI-2334
S-02115 | TSE/C-2334 | 203 | Thermocouple Assembly |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | N | J-203.7 | [29 empty] | T | 2334 |  | TI-2334
S-02115 | TSE/A-2335 | 203 | Thermocouple Assembly |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | K | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TSE/B-2335 | 203 | Thermocouple Assembly |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | K | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TSE/C-2335 | 203 | Thermocouple Assembly |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | K | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TSE/A-2336 | 203 | Thermocouple Assembly |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | K | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TSE/B-2336 | 203 | Thermocouple Assembly |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | K | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TSE/C-2336 | 203 | Thermocouple Assembly |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | K | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TE-1001 | 204 | Resistance Temperature Sensor |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Pt 100 | [30 empty] | T | 1001 |  | TI-1001
S-02115 | TE-1010 | 204 | Resistance Temperature Sensor |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Pt 100 | [30 empty] | T | 1010 |  | TI-1010
S-02115 | TE-1012 | 204 | Resistance Temperature Sensor |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Pt 100 | [30 empty] | T | 1012 |  | TI-1012
S-02115 | TE-1034 | 204 | Resistance Temperature Sensor |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Pt 100 | [30 empty] | T | 1034 |  | TI-1034
S-02115 | TE-1035 | 204 | Resistance Temperature Sensor |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Pt 100 | [30 empty] | T | 1035 |  | TI-1035
S-02115 | TE-1037 | 204 | Resistance Temperature Sensor |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | Pt 100 | [30 empty] | T | 1037 |  | TI-1037
S-02115 | TE-1041 | 204 | Resistance Temperature Sensor |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | Pt 100 | [30 empty] | T | 1041 |  | TI-1041
S-02115 | TE-1042 | 204 | Resistance Temperature Sensor |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | Pt 100 | [30 empty] | T | 1042 |  | TI-1042
S-02115 | TE-1045 | 204 | Resistance Temperature Sensor |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Pt 100 | [30 empty] | T | 1045 |  | TI-1045
S-02115 | TE-1047 | 204 | Resistance Temperature Sensor |  | P04 |  | 8"-FLG-10-113-B24-P |  |  | 5 |  | bar g |  |  | 410 | °C | Pt 100 | [30 empty] | T | 1047 |  | TI-1047
S-02115 | TE-2001 | 204 | Resistance Temperature Sensor |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Pt 100 | [30 empty] | T | 2001 |  | TI-2001
S-02115 | TE-2003 | 204 | Resistance Temperature Sensor |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | Pt 100 | [30 empty] | T | 2003 |  | TI-2003
S-02115 | TE-2039 | 204 | Resistance Temperature Sensor |  | P03 |  | 4"-HPS-20-109-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Pt 100 | [30 empty] | T | 2039 |  | TI-2039
S-02115 | TE-2044 | 204 | Resistance Temperature Sensor |  | P03 |  | 6"-VA-20-104-F70-P |  |  | 45 |  | bar g |  |  | 255 | °C | Pt 100 | [30 empty] | T | 2044 |  | TI-2044
S-02115 | TE-2046 | 204 | Resistance Temperature Sensor |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | Pt 100 | [30 empty] | T | 2046 |  | TI-2046
S-02115 | TSE/A-2047 | 204 | Resistance Temperature Sensor |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Pt 100 | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TSE/B-2047 | 204 | Resistance Temperature Sensor |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Pt 100 | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TSE/C-2047 | 204 | Resistance Temperature Sensor |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Pt 100 | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TE-2050 | 204 | Resistance Temperature Sensor |  | P03 |  | 2"-VA-20-101-F70-P |  |  | 4.5 |  | bar g |  |  | 255 | °C | Pt 100 | [30 empty] | T | 2050 |  | TI-2050
S-02115 | TE-2061 | 204 | Resistance Temperature Sensor |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Pt 100 | [30 empty] | T | 2061 |  | TI-2061
S-02115 | TE-2074 | 204 | Resistance Temperature Sensor |  | P09 |  | 24"-FLG-20-107-B24-P |  |  | 5 |  | bar g |  |  | 290 | °C | Pt 100 | [30 empty] | T | 2074 |  | TI-2074
S-02115 | TE-2111 | 204 | Resistance Temperature Sensor |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | Pt 100 | [30 empty] | T | 2111 |  | TI-2111
S-02115 | TE-2112 | 204 | Resistance Temperature Sensor |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | Pt 100 | [30 empty] | T | 2112 |  | TI-2112
S-02115 | TE-2148 | 204 | Resistance Temperature Sensor |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | Pt 100 | [30 empty] | T | 2148 |  | TI-2148
S-02115 | TE-2149 | 204 | Resistance Temperature Sensor |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | Pt 100 | [30 empty] | T | 2149 |  | TI-2149
S-02115 | TE-2150 | 204 | Resistance Temperature Sensor |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Pt 100 | [30 empty] | T | 2150 |  | TI-2150
S-02115 | TE-2151 | 204 | Resistance Temperature Sensor |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Pt 100 | [30 empty] | T | 2151 |  | TI-2151
S-02115 | TE-2161 | 204 | Resistance Temperature Sensor |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | Pt 100 | [30 empty] | T | 2161 |  | TI-2161
S-02115 | TE-2162 | 204 | Resistance Temperature Sensor |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | Pt 100 | [30 empty] | T | 2162 |  | TI-2162
S-02115 | TE-2220 | 204 | Resistance Temperature Sensor |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Pt 100 | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | TE-2232 | 204 | Resistance Temperature Sensor |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | Pt 100 | [30 empty] | T | 2232 |  | TIC-2232
S-02115 | TE-2285 | 204 | Resistance Temperature Sensor |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | Pt 100 | [30 empty] | T | 2285 |  | TI-2285
S-02115 | TE-2326 | 204 | Resistance Temperature Sensor |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | Pt 100 | [30 empty] | T | 2326 |  | TI-2326
S-02115 | TE-2327 | 204 | Resistance Temperature Sensor |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | Pt 100 | [30 empty] | T | 2327 |  | TI-2327
S-02115 | TE-2328 | 204 | Resistance Temperature Sensor |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | Pt 100 | [30 empty] | T | 2328 |  | TI-2328
S-02115 | TE-2330 | 204 | Resistance Temperature Sensor |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | Pt 100 | [30 empty] | T | 2330 |  | TI-2330
S-02115 | TE-2331 | 204 | Resistance Temperature Sensor |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | Pt 100 | [30 empty] | T | 2331 |  | TI-2331
S-02115 | TE-2332 | 204 | Resistance Temperature Sensor |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | Pt 100 | [30 empty] | T | 2332 |  | TI-2332
S-02115 | TE-2351 | 204 | Resistance Temperature Sensor |  | P17 |  | 24"-RFG-20-110-D34-H |  |  | 30 | 26.3 | bar g |  | 360 | 390 | °C | Pt 100 | [30 empty] | T | 2351 |  | TI-2351
S-02115 | TE-2352 | 204 | Resistance Temperature Sensor |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Pt 100 | [30 empty] | T | 2352 |  | TI-2352
S-02115 | TE-2359 | 204 | Resistance Temperature Sensor |  | P17 |  | 20"-HHPS-20-103-H24-H |  |  | 112 | 101 | bar g |  | 338 | 370 | °C | Pt 100 | [30 empty] | T | 2359 |  | TI-2359
S-02115 | TE-2371 | 204 | Resistance Temperature Sensor |  | P18 |  | 12"-BFW-20-102-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | Pt 100 | [30 empty] | T | 2371 |  | TI-2371
S-02115 | TE-2402 | 204 | Resistance Temperature Sensor |  | P19 |  | 34"-RFG-20-117-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Pt 100 | [30 empty] | T | 2402 |  | TI-2402
S-02115 | TE-2407 | 204 | Resistance Temperature Sensor |  | P19 |  | 16"-FLG-20-120-B40-P |  |  | 5 |  | bar g |  |  | 200 | °C | Pt 100 | [30 empty] | T | 2407 |  | TI-2407
S-02115 | TE-2418 | 204 | Resistance Temperature Sensor |  | P19 |  | 12"-BFW-20-104-G24 |  |  | 113 | 104 | bar g |  | 122 | 160 | °C | Pt 100 | [30 empty] | T | 2418 |  | TI-2418
S-02115 | TE-2421 | 204 | Resistance Temperature Sensor |  | P19 |  | 34"-RFG-20-122-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Pt 100 | [30 empty] | T | 2421 |  | TI-2421
S-02115 | TE-2444 | 204 | Resistance Temperature Sensor |  | P20 |  | 34"-RFG-20-124-D40-P |  |  | 29 | 24.4 | bar g |  | 132 | 200 | °C | Pt 100 | [30 empty] | T | 2444 |  | TI-2444
S-02115 | TE-2455 | 204 | Resistance Temperature Sensor |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | Pt 100 | [30 empty] | T | 2455 |  | TI-2455
S-02115 | TE-2457 | 204 | Resistance Temperature Sensor |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | Pt 100 | [30 empty] | T | 2457 |  | TIC-2457
S-02115 | TE-2472 | 204 | Resistance Temperature Sensor |  | P21 |  | 34"-RFG-20-125-D40-P |  |  | 29 | 24.2 | bar g |  | 65 | 120 | °C | Pt 100 | [30 empty] | T | 2472 |  | TI-2472
S-02115 | TE-2476 | 204 | Resistance Temperature Sensor |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 2476 |  | TI-2476
S-02115 | TE-2484 | 204 | Resistance Temperature Sensor |  | P21 |  | 12"-FLG-20-123-B24-N |  |  | 5 |  | bar g |  |  | 100 | °C | Pt 100 | [30 empty] | T | 2484 |  | TI-2484
S-02115 | TE-2493 | 204 | Resistance Temperature Sensor |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 2493 |  | TI-2493
S-02115 | TE-2536 | 204 | Resistance Temperature Sensor |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Pt 100 | [30 empty] | T | 2536 |  | TI-2536
S-02115 | TE-2540 | 204 | Resistance Temperature Sensor |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | Pt 100 | [30 empty] | T | 2540 |  | TI-2540
S-02115 | TE-2553 | 204 | Resistance Temperature Sensor |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Pt 100 | [30 empty] | T | 2553 |  | TI-2553
S-02115 | TE-2572 | 204 | Resistance Temperature Sensor |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Pt 100 | [30 empty] | T | 2572 |  | TI-2572
S-02115 | TE-2579 | 204 | Resistance Temperature Sensor |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | Pt 100 | [30 empty] | T | 2579 |  | TI-2579
S-02115 | TE-2601 | 204 | Resistance Temperature Sensor |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | Pt 100 | [30 empty] | T | 2601 |  | TI-2601
S-02115 | TE-2607 | 204 | Resistance Temperature Sensor |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 2607 |  | TI-2607
S-02115 | TE-3045 | 204 | Resistance Temperature Sensor |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Pt 100 | [30 empty] | T | 3045 |  | TI-3045
S-02115 | TSE/A-3072 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TSE/B-3072 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TSE/C-3072 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TE-3073 | 204 | Resistance Temperature Sensor |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | Pt 100 | [30 empty] | T | 3073 |  | TI-3073
S-02115 | TSE/A-3076 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TSE/B-3076 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TSE/C-3076 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TE-3077 | 204 | Resistance Temperature Sensor |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | Pt 100 | [30 empty] | T | 3077 |  | TI-3077
S-02115 | TSE/A-3080 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TSE/B-3080 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TSE/C-3080 | 204 | Resistance Temperature Sensor |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | Pt 100 | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TE-3081 | 204 | Resistance Temperature Sensor |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | Pt 100 | [30 empty] | T | 3081 |  | TI-3081
S-02115 | TE-3111 | 204 | Resistance Temperature Sensor |  | P25 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | Pt 100 | [30 empty] | T | 3111 |  | TI-3111
S-02115 | TE-3113 | 204 | Resistance Temperature Sensor |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | Pt 100 | [30 empty] | T | 3113 |  | TIC-3113
S-02115 | TE-3116 | 204 | Resistance Temperature Sensor |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | Pt 100 | [30 empty] | T | 3116 |  | TIC-3116
S-02115 | TE-3118 | 204 | Resistance Temperature Sensor |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | Pt 100 | [30 empty] | T | 3118 |  | TIC-3118
S-02115 | TE-3119 | 204 | Resistance Temperature Sensor |  | P25 |  | 20"-SG-30-110-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | Pt 100 | [30 empty] | T | 3119 |  | TI-3119
S-02115 | TE-3120 | 204 | Resistance Temperature Sensor |  | P25 |  | 20"-SG-30-109-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | Pt 100 | [30 empty] | T | 3120 |  | TI-3120
S-02115 | TE-3121 | 204 | Resistance Temperature Sensor |  | P25 |  | 20"-SG-30-121-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | Pt 100 | [30 empty] | T | 3121 |  | TI-3121
S-02115 | TE-3142 | 204 | Resistance Temperature Sensor |  | P26 |  | 24"-SG-30-122-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | Pt 100 | [30 empty] | T | 3142 |  | TI-3142
S-02115 | TE-3145 | 204 | Resistance Temperature Sensor |  | P26 |  | 24"-SG-30-123-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | Pt 100 | [30 empty] | T | 3145 |  | TI-3145
S-02115 | TE-3148 | 204 | Resistance Temperature Sensor |  | P26 |  | 24"-SG-30-124-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | Pt 100 | [30 empty] | T | 3148 |  | TI-3148
S-02115 | TE-3164 | 204 | Resistance Temperature Sensor |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 3164 |  | TI-3164
S-02115 | TE-3194 | 204 | Resistance Temperature Sensor |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 3194 |  | TI-3194
S-02115 | TE-3198 | 204 | Resistance Temperature Sensor |  | P28 |  | 10"-PMC-30-111-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 3198 |  | TI-3198
S-02115 | TE-5020 | 204 | Resistance Temperature Sensor |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | Pt 100 | [30 empty] | T | 5020 |  | TI-5020
S-02115 | TE-5039 | 204 | Resistance Temperature Sensor |  | P30 |  | RFG-50 |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | Pt 100 | [30 empty] | T | 5039 |  | TI-5039
S-02115 | TE-5040 | 204 | Resistance Temperature Sensor |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | Pt 100 | [30 empty] | T | 5040 |  | TI-5040
S-02115 | TE-5045 | 204 | Resistance Temperature Sensor |  | P30 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | Pt 100 | [30 empty] | T | 5045 |  | TI-5045
S-02115 | TE-5052 | 204 | Resistance Temperature Sensor |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Pt 100 | [30 empty] | T | 5052 |  | TI-5052
S-02115 | TE-5053 | 204 | Resistance Temperature Sensor |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Pt 100 | [30 empty] | T | 5053 |  | TI-5053
S-02115 | TE-5054 | 204 | Resistance Temperature Sensor |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | Pt 100 | [30 empty] | T | 5054 |  | TI-5054
S-02115 | TE-5056 | 204 | Resistance Temperature Sensor |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | Pt 100 | [30 empty] | T | 5056 |  | TI-5056
S-02115 | TE-5057 | 204 | Resistance Temperature Sensor |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | Pt 100 | [30 empty] | T | 5057 |  | TI-5057
S-02115 | TE-5059 | 204 | Resistance Temperature Sensor |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Pt 100 | [30 empty] | T | 5059 |  | TI-5059
S-02115 | TE-5060 | 204 | Resistance Temperature Sensor |  | P30 |  | 20"-PMC-50-110-B24-H |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | Pt 100 | [30 empty] | T | 5060 |  | TI-5060
S-02115 | TE-5062 | 204 | Resistance Temperature Sensor |  | P30 |  | 34"-PMV-50-120-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | Pt 100 | [30 empty] | T | 5062 |  | TI-5062
S-02115 | TE-5064 | 204 | Resistance Temperature Sensor |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | Pt 100 | [30 empty] | T | 5064 |  | TIC-5064
S-02115 | TE-5067 | 204 | Resistance Temperature Sensor |  | P30 |  | 34"-PMW-50-122-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | Pt 100 | [30 empty] | T | 5067 |  | TI-5067
S-02115 | TE-5074 | 204 | Resistance Temperature Sensor |  | P31 |  | 8"-LPC-50-110-D24-H |  |  | 18 | 2.4 | bar g |  | 138 | 190 | °C | Pt 100 | [30 empty] | T | 5074 |  | TI-5074
S-02115 | TE-5097 | 204 | Resistance Temperature Sensor |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | Pt 100 | [30 empty] | T | 5097 |  | TI-5097
S-02115 | TE-5110 | 204 | Resistance Temperature Sensor |  | P32 |  | 6"-FLG-50-131-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | Pt 100 | [30 empty] | T | 5110 |  | TI-5110
S-02115 | TE-5111 | 204 | Resistance Temperature Sensor |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | Pt 100 | [30 empty] | T | 5111 |  | TI-5111
S-02115 | TE-5165 | 204 | Resistance Temperature Sensor |  | P34 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | Pt 100 | [30 empty] | T | 5165 |  | TI-5165
S-02115 | TE-5167 | 204 | Resistance Temperature Sensor |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | Pt 100 | [30 empty] | T | 5167 |  | TI-5167
S-02115 | TE-5171 | 204 | Resistance Temperature Sensor |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | Pt 100 | [30 empty] | T | 5171 |  | TI-5171
S-02115 | TE-5173 | 204 | Resistance Temperature Sensor |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | Pt 100 | [30 empty] | T | 5173 |  | TI-5173
S-02115 | TE-5174 | 204 | Resistance Temperature Sensor |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | Pt 100 | [30 empty] | T | 5174 |  | TI-5174
S-02115 | TE-5175 | 204 | Resistance Temperature Sensor |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | Pt 100 | [30 empty] | T | 5175 |  | TI-5175
S-02115 | TE-5177 | 204 | Resistance Temperature Sensor |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | Pt 100 | [30 empty] | T | 5177 |  | TI-5177
S-02115 | TE-5180 | 204 | Resistance Temperature Sensor |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | Pt 100 | [30 empty] | T | 5180 |  | TI-5180
S-02115 | TE-5181 | 204 | Resistance Temperature Sensor |  | P34 |  | 24"-PMC-50-140-B24-H |  |  | 5 | 0.7 | bar g |  | 83 | 160 | °C | Pt 100 | [30 empty] | T | 5181 |  | TI-5181
S-02115 | TE-5184 | 204 | Resistance Temperature Sensor |  | P34 |  | 16"-PMC-50-147-B24-H |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | Pt 100 | [30 empty] | T | 5184 |  | TI-5184
S-02115 | TE-5208 | 204 | Resistance Temperature Sensor |  | P36 |  | 24"-PMP-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Pt 100 | [30 empty] | T | 5208 |  | TI-5208
S-02115 | TE-5209 | 204 | Resistance Temperature Sensor |  | P36 |  | 20"-PMP-50-102-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | Pt 100 | [30 empty] | T | 5209 |  | TI-5209
S-02115 | TE-5219 | 204 | Resistance Temperature Sensor |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | Pt 100 | [30 empty] | T | 5219 |  | TI-5219
S-02115 | TE-5221 | 204 | Resistance Temperature Sensor |  | P36 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Pt 100 | [30 empty] | T | 5221 |  | TI-5221
S-02115 | TE-5261 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5261 |  | TI-5261
S-02115 | TE-5262 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5262 |  | TI-5262
S-02115 | TE-5263 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5263 |  | TI-5263
S-02115 | TE-5264 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5264 |  | TI-5264
S-02115 | TE-5265 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5265 |  | TI-5265
S-02115 | TE-5266 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5266 |  | TIC-5266
S-02115 | TE-5267 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5267 |  | TIC-5267
S-02115 | TE-5268 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5268 |  | TIC-5268
S-02115 | TE-5269 | 204 | Resistance Temperature Sensor |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Pt 100 | [30 empty] | T | 5269 |  | TI-5269
S-02115 | TE-5273 | 204 | Resistance Temperature Sensor |  | P38 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | Pt 100 | [30 empty] | T | 5273 |  | TI-5273
S-02115 | TE-5277 | 204 | Resistance Temperature Sensor |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Pt 100 | [30 empty] | T | 5277 |  | TIC-5277
S-02115 | TE-5280 | 204 | Resistance Temperature Sensor |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | Pt 100 | [30 empty] | T | 5280 |  | TI-5280
S-02115 | TE-5307 | 204 | Resistance Temperature Sensor |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | Pt 100 | [30 empty] | T | 5307 |  | TI-5307
S-02115 | TE-5325 | 204 | Resistance Temperature Sensor |  | P40 |  | 24"-PMP-50-130-B24-H |  |  | 7 | 2.6 | bar g |  | 101 | 165 | °C | Pt 100 | [30 empty] | T | 5325 |  | TI-5325
S-02115 | TE-5335 | 204 | Resistance Temperature Sensor |  | P40 |  | 6"-PMP-50-140-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | Pt 100 | [30 empty] | T | 5335 |  | TI-5335
S-02115 | TE-5340 | 204 | Resistance Temperature Sensor |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Pt 100 | [30 empty] | T | 5340 |  | TI-5340
S-02115 | TE-5369 | 204 | Resistance Temperature Sensor |  | P41 |  | 2"-PMW-50-125-B24-P |  |  | 7.5 | 4.3 | bar g |  | 65 | 120 | °C | Pt 100 | [30 empty] | T | 5369 |  | TI-5369
S-02115 | TE-5381 | 204 | Resistance Temperature Sensor |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Pt 100 | [30 empty] | T | 5381 |  | TI-5381
S-02115 | TE-5441 | 204 | Resistance Temperature Sensor |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | Pt 100 | [30 empty] | T | 5441 |  | TI-5441
S-02115 | TE-5442 | 204 | Resistance Temperature Sensor |  | P45 |  | 2"-LOS-50-113-B24-P |  |  | 7.5 | 2.5 | bar g |  | 115 | 175 | °C | Pt 100 | [30 empty] | T | 5442 |  | TI-5442
S-02115 | TE-5443 | 204 | Resistance Temperature Sensor |  | P45 |  | 2"-LOS-50-114-B24-N |  |  | 7.5 | 2 | bar g |  | 48 | 75 | °C | Pt 100 | [30 empty] | T | 5443 |  | TI-5443
S-02115 | TE-6001 | 204 | Resistance Temperature Sensor |  | P05 |  | 18"-MPC-60-101-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | Pt 100 | [30 empty] | T | 6001 |  | TI-6001
S-02115 | TE-6024 | 204 | Resistance Temperature Sensor |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 290 | °C | Pt 100 | [30 empty] | T | 6024 |  | TI-6024
S-02115 | TE-6026 | 204 | Resistance Temperature Sensor |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | Pt 100 | [30 empty] | T | 6026 |  | TI-6026
S-02115 | TE-6031 | 204 | Resistance Temperature Sensor |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Pt 100 | [30 empty] | T | 6031 |  | TI-6031
S-02115 | TE-6034 | 204 | Resistance Temperature Sensor |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Pt 100 | [30 empty] | T | 6034 |  | TI-6034
S-02115 | TE-6054 | 204 | Resistance Temperature Sensor |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | Pt 100 | [30 empty] | T | 6054 |  | TI-6054
S-02115 | TE-6056 | 204 | Resistance Temperature Sensor |  | P07 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | Pt 100 | [30 empty] | T | 6056 |  | TI-6056
S-02115 | TE-6058 | 204 | Resistance Temperature Sensor |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | Pt 100 | [30 empty] | T | 6058 |  | TI-6058
S-02115 | TE-6081 | 204 | Resistance Temperature Sensor |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | Pt 100 | [30 empty] | T | 6081 |  | TI-6081
S-02115 | TE-6084 | 204 | Resistance Temperature Sensor |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | Pt 100 | [30 empty] | T | 6084 |  | TI-6084
S-02115 | TE-7001 | 204 | Resistance Temperature Sensor |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | Pt 100 | [30 empty] | T | 7001 |  | TI-7001
S-02115 | TE-7002 | 204 | Resistance Temperature Sensor |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | Pt 100 | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | TE-7003 | 204 | Resistance Temperature Sensor |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | Pt 100 | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | TE-7004 | 204 | Resistance Temperature Sensor |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | Pt 100 | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | TE-7007 | 204 | Resistance Temperature Sensor |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Pt 100 | [30 empty] | T | 7007 |  | TI-7007
S-02115 | TE-7025 | 204 | Resistance Temperature Sensor |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | Pt 100 | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | TE-7031 | 204 | Resistance Temperature Sensor |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Pt 100 | [30 empty] | T | 7031 |  | TI-7031
S-02115 | TE-7032 | 204 | Resistance Temperature Sensor |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | Pt 100 | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | TE-7033 | 204 | Resistance Temperature Sensor |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | Pt 100 | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | TE-7052 | 204 | Resistance Temperature Sensor |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | Pt 100 | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | TE-7053 | 204 | Resistance Temperature Sensor |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | Pt 100 | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | TE-7056 | 204 | Resistance Temperature Sensor |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | Pt 100 | [30 empty] | T | 7056 |  | TI-7056
S-02115 | TSE/A-7071 | 204 | Resistance Temperature Sensor |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Pt 100 | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TSE/B-7071 | 204 | Resistance Temperature Sensor |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Pt 100 | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TSE/C-7071 | 204 | Resistance Temperature Sensor |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Pt 100 | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TE-7097 | 204 | Resistance Temperature Sensor |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | Pt 100 | [30 empty] | T | 7097 |  | TI-7097
S-02115 | TE-7098 | 204 | Resistance Temperature Sensor |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 0 | bar g |  | 120 | 340 | °C | Pt 100 | [30 empty] | T | 7098 |  | TI-7098
S-02115 | TE-8001 | 204 | Resistance Temperature Sensor |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | Pt 100 | [30 empty] | T | 8001 |  | TI-8001
S-02115 | FE-2582 | 206 | Pitot Tube |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 35000 Nm3/h | 31208 Nm3/h | Gas | 8 bar g | 84 °C | 8.50 kg/m3 | 0.02 cP | 1 | 1.41 | 28.01 | By vendor mmWG | 260.4 (Sch. 20) mm | AISI 316 |  | 10400 Nm3/h | [16 empty] | F | 2582 |  | FI-2582
S-02115 | AST/A-1001 | 209 | Gas Analyzer |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0.5-0.7 SG | Specific gravity | Vibrating cylinder |  |  |  |  | Lean Gas/Rich Gas | [20 empty] | 16.74/18.57 kg/kmol |  |  | A | 1001 |  | AI-1001
S-02115 | AST/B-1001 | 209 | Gas Analyzer |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0.5-0.7 SG | Specific gravity | Vibrating cylinder |  |  |  |  | Lean Gas/Rich Gas | [20 empty] | 16.74/18.57 kg/kmol |  |  | A | 1001 |  | AI-1001
S-02115 | AST/C-1001 | 209 | Gas Analyzer |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0.5-0.7 SG | Specific gravity | Vibrating cylinder |  |  |  |  | Lean Gas/Rich Gas | [20 empty] | 16.74/18.57 kg/kmol |  |  | A | 1001 |  | AI-1001
S-02115 | AT-1035 | 209 | Gas Analyzer |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-40 wt ppm | Total Sulphur | Lead acetate |  |  |  |  | C1/2040 | 0.01 mol % | 0.43 mol % | 0.22 mol % |  |  | 92.53 mol % | 0.11 mol % | 0.49 mol % | 2.01 mol % | 4.17 mol % | [13 empty] | A | 1035 |  | AI-1035
S-02115 | AT-1045 | 209 | Gas Analyzer |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-1 wt ppm | Total Sulphur | Lead acetate |  |  |  |  | C1/2040 | 0.01 mol % | 0.43 mol % | 0.22 mol % |  |  | 92.53 mol % | 0.11 mol % | 0.49 mol % | 2.01 mol % | 4.17 mol % | [13 empty] | A | 1045 |  | AI-1045
S-02115 | AT-2223 | 209 | Gas Analyzer |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-10 Vol % / 0-2000 ppm | O2/Combustibles | See note 1 |  |  |  |  | SOR lean gas; SOR rich gas | 0.79; 0.78 mol % | [6 empty] | 6.64; 7.81 mol % |  | 64.39; 64.37 mol % |  | 1.53; 1.52 mol % | 26.65; 25.52 mol % | [10 empty] | A | 2223 |  | AI-2223
S-02115 | AT-2224 | 209 | Gas Analyzer |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-10 Vol % | O2 | Zirconium oxide |  |  |  |  | SOR lean gas; SOR rich gas | 0.79; 0.78 mol % | [6 empty] | 6.64; 7.81 mol % |  | 64.39; 64.37 mol % |  | 1.53; 1.52 mol % | 26.65; 25.52 mol % | [10 empty] | A | 2224 |  | AI-2224
S-02115 | AT-2479 | 209 | Gas Analyzer |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-10 Vol % | CH4 | Infrared |  |  | 1 |  | SOR Lean gas; SOR rich gas | 0.03; 0.24 mol % |  |  |  |  | 0.65; 5.77 mol % | 21.40; 2.0 mol % | 7.27; 5.62 mol % | 68.90; 73.27 mol % | 1.30; 12.29 mol % |  |  | 0.45; 0.05 mol % |  | 0; 0.72 mol % |  |  | AT-2479 | With sample probe |  |  |  |  | A | 2479 |  | AI-2479
S-02115 | AT-2531 | 209 | Gas Analyzer |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-50 MJ/Nm3 | O2 | LHV |  |  |  |  | C1/2000 |  | 0.44 mol % | 0.23 mol % |  |  | 95 mol % |  | 0.33 mol % |  | 4 mol % | [13 empty] | A | 2531 |  | AI-2531
S-02115 | AT-2532 | 209 | Gas Analyzer |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-20 MJ/Nm3 | O2 | LHV |  |  |  |  | C1/3355 | 0.19 mol % |  |  |  |  | 4.98 mol % | 3.9 mol % | 8.82 mol % | 70.51 mol % | 9.87 mol % |  |  | 0.08 mol % | 0.19 mol % | 1.38 mol % | 0.09 mol % | 0.18 mol % | [6 empty] | A | 2532 |  | AI-2532
S-02115 | AT-3001 | 209 | Gas Analyzer |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 50-95 Vol % | H2 | Thermal conductivity |  |  | 2 | See note 2 | SOR LeanG 1 | 0.03; 0.24 / 0.03; 0.25 mol % |  |  |  |  | 0.65; 5.77 /0.63; 5.83 mol % | 21.40; 2.0 / 21.88; 3.0 mol % | 7.27; 5.62 / 7.56; 8.91 mol % | 68.90; 73.27 / 67.92; 66.16 mol % | 1.30; 12.29 / 1.53; 15.02 mol % |  |  | 0.45; 0.05 / 0.45; 0.05 mol % |  | 0; 0.72/ 0; 0.76 mol % |  |  | AT-3001, AT-3002 & AT-3003 | With sample probe |  |  |  |  | A | 3001 |  | AI-3001
S-02115 | AT-3002 | 209 | Gas Analyzer |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-40 Vol % | CO | Infrared |  |  | 2 | See note 2 | SOR LeanG 1 | 0.03; 0.24 / 0.03; 0.25 mol % |  |  |  |  | 0.65; 5.77 /0.63; 5.83 mol % | 21.40; 2.0 / 21.88; 3.0 mol % | 7.27; 5.62 / 7.56; 8.91 mol % | 68.90; 73.27 / 67.92; 66.16 mol % | 1.30; 12.29 / 1.53; 15.02 mol % |  |  | 0.45; 0.05 / 0.45; 0.05 mol % |  | 0; 0.72/ 0; 0.76 mol % |  |  | AT-3001, AT-3002 & AT-3003 | With sample probe |  |  |  |  | A | 3002 |  | AI-3002
S-02115 | AT-3003 | 209 | Gas Analyzer |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-15 Vol % | CO2 | Infrared |  |  | 2 | See note 2 | SOR LeanG 1 | 0.03; 0.24 / 0.03; 0.25 mol % |  |  |  |  | 0.65; 5.77 /0.63; 5.83 mol % | 21.40; 2.0 / 21.88; 3.0 mol % | 7.27; 5.62 / 7.56; 8.91 mol % | 68.90; 73.27 / 67.92; 66.16 mol % | 1.30; 12.29 / 1.53; 15.02 mol % |  |  | 0.45; 0.05 / 0.45; 0.05 mol % |  | 0; 0.72/ 0; 0.76 mol % |  |  | AT-3001, AT-3002 & AT-3003 | With sample probe |  |  |  |  | A | 3003 |  | AI-3003
S-02115 | AT-2382 | 210 | pH Transmitter |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 2-14 pH | Yes | [29 empty] | A | 2382 |  | AI-2382
S-02115 | AT-3053 | 210 | pH Transmitter |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 2-14 pH | [30 empty] | A | 3053 |  | AI-3053
S-02115 | AT-7099 | 210 | pH Transmitter |  | U09 |  | 18"-BFW-70-129-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 2-12 pH | [30 empty] | A | 7099 |  | AIC-7099
S-02115 | AT-2379 | 211 | Conductivity Transmitter |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-1 µS/cm | [30 empty] | A | 2379 |  | AI-2379
S-02115 | AT-2384 | 211 | Conductivity Transmitter |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 0-100 µS/cm | [30 empty] | A | 2384 |  | AI-2384
S-02115 | AT-3055 | 211 | Conductivity Transmitter |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 0-100 µS/cm | [30 empty] | A | 3055 |  | AI-3055
S-02115 | FT-3198 | 212.1 | Flow Transmitter, Mass Coriolis |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 280000 kg/h | 80222 kg/h | 240667 kg/h |  |  | Liquid | 4 bar g | 48 °C | 785 kg/m3 | 0.43 cP |  |  | 29.46 kg/kmol | 6" | AISI 316 | 6", Class 150, RF |  | <0.2 bar | [13 empty] | F | 3198 |  | FI-3198
S-02115 | FT-5336 | 212.1 | Flow Transmitter, Mass Coriolis |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 100000 kg/h | 27443 kg/h | 82329 kg/h |  |  | Liquid | 5.7 bar g | 48 °C | 766 kg/m3 | 0.40 cP |  |  | 32.04 kg/kmol | 4" | AISI 316 | 4", Class 300, RF |  | <0.2 bar | [13 empty] | F | 5336 |  | FIC-5336
S-02115 | FT-5337 | 212.1 | Flow Transmitter, Mass Coriolis |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 150000 kg/h | 42003 kg/h | 126008 kg/h |  |  | Liquid | 3.5 bar g | 48 °C | 766 kg/m3 | 0.40 cP |  |  | 32.04 kg/kmol | 6" | AISI 316 | 6", Class 150, RF |  | <0.1 bar | [13 empty] | F | 5337 |  | FIC-5337
S-02115 | FT-5421 | 212.1 | Flow Transmitter, Mass Coriolis |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 240000 kg/h | 69500 kg/h | 208337 kg/h |  |  | Liquid | 5 bar g | 48 °C | 766 kg/m3 | 0.40 cP |  |  | 32.04 kg/kmol | 6" | AISI 316 | 6", Class 150, RF |  | <0.2 bar | [13 empty] | F | 5421 |  | FI-5421
S-02115 | FT/1-2531 | 212.5 | Flow Transmitter, Vortex |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 10000 Nm3/h | 2800 Nm3/h | 8400 Nm3/h |  |  | Gas | 4 bar g | 35 °C | 3.30 kg/m3 | 0.012 cP | 0.99 | 1.3 | 16.74 | 6 " | AISI 316 | 6", Class 150, RF | [15 empty] | F | 2531 |  | FIC-2531
S-02115 | FT/2-2531 | 212.5 | Flow Transmitter, Vortex |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 30000 Nm3/h | 5000 Nm3/h | 13389 Nm3/h |  |  | Gas | 4 bar g | 35 °C | 3.30 kg/m3 | 0.012 cP | 0.99 | 1.3 | 16.74 | 10 " | AISI 316 | 10", Class 150, RF | [15 empty] | F | 2531 |  | FIC-2531
S-02115 | FT-1006 | 213 | Flow Transmitter, d/P |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-5000 mmWG | [30 empty] | F | 1006 |  | FI-1006
S-02115 | FST/A-2007 | 213 | Flow Transmitter, d/P |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-2500 mmWG | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FST/B-2007 | 213 | Flow Transmitter, d/P |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-2500 mmWG | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FST/C-2007 | 213 | Flow Transmitter, d/P |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-2500 mmWG | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FT-2009 | 213 | Flow Transmitter, d/P |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-2500 mmWG | [30 empty] | F | 2009 |  | FIC-2009
S-02115 | FST/A-2040 | 213 | Flow Transmitter, d/P |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FST/B-2040 | 213 | Flow Transmitter, d/P |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FST/C-2040 | 213 | Flow Transmitter, d/P |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FST/A-2061 | 213 | Flow Transmitter, d/P |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-5000 mmWG | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FST/B-2061 | 213 | Flow Transmitter, d/P |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-5000 mmWG | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FST/C-2061 | 213 | Flow Transmitter, d/P |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-5000 mmWG | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FST/A-2072 | 213 | Flow Transmitter, d/P |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FST/B-2072 | 213 | Flow Transmitter, d/P |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FST/C-2072 | 213 | Flow Transmitter, d/P |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FT-2079 | 213 | Flow Transmitter, d/P |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-2500 mmWG | [30 empty] | F | 2079 |  | FIC-2079
S-02115 | FT-2091 | 213 | Flow Transmitter, d/P |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-5000 mmWG | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | FT-2111 | 213 | Flow Transmitter, d/P |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | By Vendor mmWG | [30 empty] | F | 2111 |  | FIC-2111
S-02115 | FT-2115 | 213 | Flow Transmitter, d/P |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 2115 |  | FI-2115
S-02115 | FT-2150 | 213 | Flow Transmitter, d/P |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-2500 mmWG | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FT-2151 | 213 | Flow Transmitter, d/P |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-2500 mmWG | [30 empty] | F | 2151 |  | FI-2151
S-02115 | FT-2165 | 213 | Flow Transmitter, d/P |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-5000 mmWG | [30 empty] | F | 2165 |  | FI-2165
S-02115 | FST/A-2233 | 213 | Flow Transmitter, d/P |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 0-2500 mmWG | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FST/B-2233 | 213 | Flow Transmitter, d/P |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 0-2500 mmWG | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FST/C-2233 | 213 | Flow Transmitter, d/P |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 0-2500 mmWG | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FT-2372 | 213 | Flow Transmitter, d/P |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-2500 mmWG | [30 empty] | F | 2372 |  | FI-2372
S-02115 | FT-2417 | 213 | Flow Transmitter, d/P |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-2500 mmWG | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | FT-2476 | 213 | Flow Transmitter, d/P |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 2476 |  | FI-2476
S-02115 | FT-2536 | 213 | Flow Transmitter, d/P |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | FST-2582 | 213 | Flow Transmitter, d/P |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | By avg. pitot tube vendor mmWG | [30 empty] | F | 2582 |  | FI-2582
S-02115 | FT-2607 | 213 | Flow Transmitter, d/P |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 2607 |  | FI-2607
S-02115 | FT-3020 | 213 | Flow Transmitter, d/P |  | P22 |  | 18"-SG-30-101-H40-H |  |  | 99 | 80 | bar g |  | 122 | 165 | °C | 0-2500 mmWG | [30 empty] | F | 3020 |  | FI-3020
S-02115 | FT-3041 | 213 | Flow Transmitter, d/P |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | 0-2500 mmWG | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | FT-3050 | 213 | Flow Transmitter, d/P |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 0-2500 mmWG | [30 empty] | F | 3050 |  | FI-3050
S-02115 | FT-3167 | 213 | Flow Transmitter, d/P |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 3167 |  | FI-3167
S-02115 | FT-3169 | 213 | Flow Transmitter, d/P |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-5000 mmWG | [30 empty] | F | 3169 |  | FIC-3169
S-02115 | FT-3171 | 213 | Flow Transmitter, d/P |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-5000 mmWG | [30 empty] | F | 3171 |  | FIC-3171
S-02115 | FT-3194 | 213 | Flow Transmitter, d/P |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 3194 |  | FI-3194
S-02115 | FT-5020 | 213 | Flow Transmitter, d/P |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | FT-5041 | 213 | Flow Transmitter, d/P |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 5041 |  | FIC-5041
S-02115 | FT-5068 | 213 | Flow Transmitter, d/P |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 0-2500 mmWG | [30 empty] | F | 5068 |  | FI-5068
S-02115 | FT-5093 | 213 | Flow Transmitter, d/P |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-2500 mmWG | [30 empty] | F | 5093 |  | FIC-5093
S-02115 | FT-5107 | 213 | Flow Transmitter, d/P |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-2500 mmWG | [30 empty] | F | 5107 |  | FIC-5107
S-02115 | FT-5111 | 213 | Flow Transmitter, d/P |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-2500 mmWG | [30 empty] | F | 5111 |  | FI-5111
S-02115 | FT-5161 | 213 | Flow Transmitter, d/P |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 0-2500 mmWG | [30 empty] | F | 5161 |  | FIC-5161
S-02115 | FT-5203 | 213 | Flow Transmitter, d/P |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-2500 mmWG | [30 empty] | F | 5203 |  | FIC-5203
S-02115 | FT-5239 | 213 | Flow Transmitter, d/P |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 0-2500 mmWG | [30 empty] | F | 5239 |  | FIC-5239
S-02115 | FT-5301 | 213 | Flow Transmitter, d/P |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 0-2500 mmWG | [30 empty] | F | 5301 |  | FIC-5301
S-02115 | FT-5321 | 213 | Flow Transmitter, d/P |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 0-2500 mmWG | [30 empty] | F | 5321 |  | FIC-5321
S-02115 | FT-5367 | 213 | Flow Transmitter, d/P |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 0-2500 mmWG | [30 empty] | F | 5367 |  | FIC-5367
S-02115 | FT-5383 | 213 | Flow Transmitter, d/P |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | 0-2500 mmWG | [30 empty] | F | 5383 |  | FIC-5383
S-02115 | FT-5407 | 213 | Flow Transmitter, d/P |  | P43 |  | 3"-PMP-50-161-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | 0-2500 mmWG | [30 empty] | F | 5407 |  | FI-5407
S-02115 | FT-5441 | 213 | Flow Transmitter, d/P |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 0-2500 mmWG | [30 empty] | F | 5441 |  | FIC-5441
S-02115 | FT-5501 | 213 | Flow Transmitter, d/P |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | 0-2500 mmWG | [30 empty] | F | 5501 |  | FIC-5501
S-02115 | FT-6031 | 213 | Flow Transmitter, d/P |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-2500 mmWG | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | FT-6032 | 213 | Flow Transmitter, d/P |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 0-2500 mmWG | [30 empty] | F | 6032 |  | FI-6032
S-02115 | FT-6057 | 213 | Flow Transmitter, d/P |  | P07 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 0-2500 mmWG | [30 empty] | F | 6057 |  | FI-6057
S-02115 | FT-6068 | 213 | Flow Transmitter, d/P |  | P07 |  | 10"-PRC-60-111-G40-H |  |  | 72 | 44 | bar g |  | 225 | 290 | °C | 0-2500 mmWG | [30 empty] | F | 6068 |  | FI-6068
S-02115 | FST/A-6070 | 213 | Flow Transmitter, d/P |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 0-5000 mmWG | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FST/B-6070 | 213 | Flow Transmitter, d/P |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 0-5000 mmWG | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FST/C-6070 | 213 | Flow Transmitter, d/P |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 0-5000 mmWG | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FT-6081 | 213 | Flow Transmitter, d/P |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 0-2500 mmWG | [30 empty] | F | 6081 |  | FIC-6081
S-02115 | FT-6082 | 213 | Flow Transmitter, d/P |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | 0-2500 mmWG | [30 empty] | F | 6082 |  | FIC-6082
S-02115 | FT-6086 | 213 | Flow Transmitter, d/P |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 0-2500 mmWG | [30 empty] | F | 6086 |  | FIC-6086
S-02115 | FT-7001 | 213 | Flow Transmitter, d/P |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-5000 mmWG | [30 empty] | F | 7001 |  | FI-7001
S-02115 | FT-7029 | 213 | Flow Transmitter, d/P |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-2500 mmWG | [30 empty] | F | 7029 |  | FI-7029
S-02115 | FT-7030 | 213 | Flow Transmitter, d/P |  | U04 |  | 24"-HPS-70-136-F34-H |  |  | 52 | 42 | bar g |  | 410 | 470 | °C | 0-2500 mmWG | [30 empty] | F | 7030 |  | FI-7030
S-02115 | FT-7091 | 213 | Flow Transmitter, d/P |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 0-4000 mmWG | [30 empty] | F | 7091 |  | FIC-7091
S-02115 | FT-7101 | 213 | Flow Transmitter, d/P |  | U22 |  | 2"-PRC-70-141-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | 0-2500 mmWG | [30 empty] | F | 7101 |  | FI-7101
S-02115 | FT-7129 | 213 | Flow Transmitter, d/P |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 7129 |  | FI-7129
S-02115 | FT-7134 | 213 | Flow Transmitter, d/P |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-2500 mmWG | [30 empty] | F | 7134 |  | FI-7134
S-02115 | FT-7141 | 213 | Flow Transmitter, d/P |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-5000 mmWG | [30 empty] | F | 7141 |  | FIC-7141
S-02115 | LST/A-1004 | 214 | Level Transmitter, d/P |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | By Detail Engineer |  | By Detail Engineer |  | 36.8 kg/m3 | 995 kg/m3 | [25 empty] | L | 1004 |  | LI-1004
S-02115 | LST/B-1004 | 214 | Level Transmitter, d/P |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | By Detail Engineer |  | By Detail Engineer |  | 36.8 kg/m3 | 995 kg/m3 | [25 empty] | L | 1004 |  | LI-1004
S-02115 | LST/C-1004 | 214 | Level Transmitter, d/P |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | By Detail Engineer |  | By Detail Engineer |  | 36.8 kg/m3 | 995 kg/m3 | [25 empty] | L | 1004 |  | LI-1004
S-02115 | LT-2016 | 214 | Level Transmitter, d/P |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 789 kg/m3 | [25 empty] | L | 2016 |  | LIC-2016
S-02115 | LST/A-2372 | 214 | Level Transmitter, d/P |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | By Detail Engineer |  | By Detail Engineer |  | 57.5 kg/m3 | 683 kg/m3 | [25 empty] | L | 2372 |  | LIC-2372
S-02115 | LST/B-2372 | 214 | Level Transmitter, d/P |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | By Detail Engineer |  | By Detail Engineer |  | 57.5 kg/m3 | 683 kg/m3 | [25 empty] | L | 2372 |  | LIC-2372
S-02115 | LST/C-2372 | 214 | Level Transmitter, d/P |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | By Detail Engineer |  | By Detail Engineer |  | 57.5 kg/m3 | 683 kg/m3 | [25 empty] | L | 2372 |  | LIC-2372
S-02115 | LT-2403 | 214 | Level Transmitter, d/P |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 9.78 kg/m3 | 903 kg/m3 | [25 empty] | L | 2403 |  | LIC-2403
S-02115 | LST-2404 | 214 | Level Transmitter, d/P |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 9.78 kg/m3 | 903 kg/m3 | [25 empty] | L | 2404 |  | LI-2404
S-02115 | LT-2419 | 214 | Level Transmitter, d/P |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 9.54 kg/m3 | 909 kg/m3 | [25 empty] | L | 2419 |  | LIC-2419
S-02115 | LT-2441 | 214 | Level Transmitter, d/P |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 9.39 kg/m3 | 929 kg/m3 | [25 empty] | L | 2441 |  | LIC-2441
S-02115 | LST-2442 | 214 | Level Transmitter, d/P |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 9.39 kg/m3 | 929 kg/m3 | [25 empty] | L | 2442 |  | LI-2442
S-02115 | LST/A-2474 | 214 | Level Transmitter, d/P |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 10.7 kg/m3 | 989 kg/m3 | [25 empty] | L | 2474 |  | LIC-2474
S-02115 | LST/B-2474 | 214 | Level Transmitter, d/P |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 10.7 kg/m3 | 989 kg/m3 | [25 empty] | L | 2474 |  | LIC-2474
S-02115 | LST/C-2474 | 214 | Level Transmitter, d/P |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 10.7 kg/m3 | 989 kg/m3 | [25 empty] | L | 2474 |  | LIC-2474
S-02115 | LST/A-3042 | 214 | Level Transmitter, d/P |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  | 17.4 kg/m3 | 811 kg/m3 | [25 empty] | L | 3042 |  | LIC-3042
S-02115 | LST/B-3042 | 214 | Level Transmitter, d/P |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  | 17.4 kg/m3 | 811 kg/m3 | [25 empty] | L | 3042 |  | LIC-3042
S-02115 | LST/C-3042 | 214 | Level Transmitter, d/P |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  | 17.4 kg/m3 | 811 kg/m3 | [25 empty] | L | 3042 |  | LIC-3042
S-02115 | LST/A-3161 | 214 | Level Transmitter, d/P |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 35.1 kg/m3 | 757 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 3161 |  | LIC-3161
S-02115 | LST/B-3161 | 214 | Level Transmitter, d/P |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 35.1 kg/m3 | 757 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 3161 |  | LIC-3161
S-02115 | LST/C-3161 | 214 | Level Transmitter, d/P |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 35.1 kg/m3 | 757 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 3161 |  | LIC-3161
S-02115 | LST/A-3192 | 214 | Level Transmitter, d/P |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 5.69 kg/m3 | 781 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 3192 |  | LIC-3192
S-02115 | LST/B-3192 | 214 | Level Transmitter, d/P |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 5.69 kg/m3 | 781 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 3192 |  | LIC-3192
S-02115 | LST/C-3192 | 214 | Level Transmitter, d/P |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  | 5.69 kg/m3 | 781 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 3192 |  | LIC-3192
S-02115 | LT-5041 | 214 | Level Transmitter, d/P |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.96 kg/m3 | 753 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5041 |  | LIC-5041
S-02115 | LST-5042 | 214 | Level Transmitter, d/P |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.96 kg/m3 | 753 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5042 |  | LI-5042
S-02115 | LT-5065 | 214 | Level Transmitter, d/P |  | P30 |  | E 2024 2 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | By Detail Engineer |  | By Detail Engineer |  | 2.17 kg/m3 | 748 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5065 |  | LI-5065
S-02115 | LT-5070 | 214 | Level Transmitter, d/P |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 928 kg/m3 | [25 empty] | L | 5070 |  | LIC-5070
S-02115 | LST-5071 | 214 | Level Transmitter, d/P |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 928 kg/m3 | [25 empty] | L | 5071 |  | LI-5071
S-02115 | LT-5093 | 214 | Level Transmitter, d/P |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  | 2.26 kg/m3 | 752 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5093 |  | LIC-5093
S-02115 | LST-5094 | 214 | Level Transmitter, d/P |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  | 2.26 kg/m3 | 752 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5094 |  | LI-5094
S-02115 | LT-5161 | 214 | Level Transmitter, d/P |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.29 kg/m3 | 786 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5161 |  | LIC-5161
S-02115 | LST-5162 | 214 | Level Transmitter, d/P |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.29 kg/m3 | 786 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5162 |  | LI-5162
S-02115 | LT-5182 | 214 | Level Transmitter, d/P |  | P34 |  | E 5002 4 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.73 kg/m3 | 786 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5182 |  | LI-5182
S-02115 | LT-5203 | 214 | Level Transmitter, d/P |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 750 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5203 |  | LIC-5203
S-02115 | LST-5204 | 214 | Level Transmitter, d/P |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 750 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5204 |  | LI-5204
S-02115 | LT-5270 | 214 | Level Transmitter, d/P |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | By Detail Engineer |  | By Detail Engineer |  | 4.07 kg/m3 | 918 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5270 |  | LIC-5270
S-02115 | LST-5271 | 214 | Level Transmitter, d/P |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | By Detail Engineer |  | By Detail Engineer |  | 4.07 kg/m3 | 918 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5271 |  | LI-5271
S-02115 | LT-5278 | 214 | Level Transmitter, d/P |  | P39 |  | E 5003 2 Shell |  |  | 7.5 | 3.6 |  |  | 149 | 175 | °C | By Detail Engineer |  | By Detail Engineer |  | 2.42 kg/m3 | 918 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5278 |  | LI-5278
S-02115 | LT-5308 | 214 | Level Transmitter, d/P |  | P39 |  | E 5003 1 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 340 | °C | By Detail Engineer |  | By Detail Engineer |  | 3.71 kg/m3 | 899 kg/m3 | [25 empty] | L | 5308 |  | LI-5308
S-02115 | LT-5310 | 214 | Level Transmitter, d/P |  | P39 |  | E 5003 2 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 175 | °C | By Detail Engineer |  | By Detail Engineer |  | 3.71 kg/m3 | 899 kg/m3 | [25 empty] | L | 5310 |  | LI-5310
S-02115 | LT-5321 | 214 | Level Transmitter, d/P |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 711 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5321 |  | LIC-5321
S-02115 | LST-5322 | 214 | Level Transmitter, d/P |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 711 kg/m3 |  | 3" to 1½" reducing flange | [23 empty] | L | 5322 |  | LI-5322
S-02115 | LST/A-5501 | 214 | Level Transmitter, d/P |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 991 kg/m3 | [25 empty] | L | 5501 |  | LIC-5501
S-02115 | LST/B-5501 | 214 | Level Transmitter, d/P |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 991 kg/m3 | [25 empty] | L | 5501 |  | LIC-5501
S-02115 | LST/C-5501 | 214 | Level Transmitter, d/P |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | By Detail Engineer |  | By Detail Engineer |  |  | 991 kg/m3 | [25 empty] | L | 5501 |  | LIC-5501
S-02115 | LT-6021 | 214 | Level Transmitter, d/P |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | By Detail Engineer |  | By Detail Engineer |  | 20 kg/m3 | 834 kg/m3 | [25 empty] | L | 6021 |  | LIC-6021
S-02115 | LST-6022/1 | 214 | Level Transmitter, d/P |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | By Detail Engineer |  | By Detail Engineer |  | 20 kg/m3 | 834 kg/m3 | [25 empty] | L | 6022 | 1 | LI-6022/1
S-02115 | LST-6022/2 | 214 | Level Transmitter, d/P |  | P06 |  | T 6001 2 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | By Detail Engineer |  | By Detail Engineer |  | 20 kg/m3 | 834 kg/m3 | [25 empty] | L | 6022 | 2 | LI-6022/2
S-02115 | LST/A-6051 | 214 | Level Transmitter, d/P |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  | 22.6 kg/m3 | 827 kg/m3 | [25 empty] | L | 6051 |  | LIC-6051
S-02115 | LST/B-6051 | 214 | Level Transmitter, d/P |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  | 22.6 kg/m3 | 827 kg/m3 | [25 empty] | L | 6051 |  | LIC-6051
S-02115 | LST/C-6051 | 214 | Level Transmitter, d/P |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | By Detail Engineer |  | By Detail Engineer |  | 22.6 kg/m3 | 827 kg/m3 | [25 empty] | L | 6051 |  | LIC-6051
S-02115 | LT-6082 | 214 | Level Transmitter, d/P |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | By Detail Engineer |  | By Detail Engineer |  | 0.6 kg/m3 | 958 kg/m3 | [25 empty] | L | 6082 |  | LIC-6082
S-02115 | LT-6083 | 214 | Level Transmitter, d/P |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | By Detail Engineer |  | By Detail Engineer |  | 0.6 kg/m3 | 958 kg/m3 | [25 empty] | L | 6083 |  | LI-6083
S-02115 | LST/A-7091 | 214 | Level Transmitter, d/P |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.12 kg/m3 | 943 kg/m3 | [25 empty] | L | 7091 |  | LIC-7091
S-02115 | LST/B-7091 | 214 | Level Transmitter, d/P |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.12 kg/m3 | 943 kg/m3 | [25 empty] | L | 7091 |  | LIC-7091
S-02115 | LST/C-7091 | 214 | Level Transmitter, d/P |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | By Detail Engineer |  | By Detail Engineer |  | 1.12 kg/m3 | 943 kg/m3 | [25 empty] | L | 7091 |  | LIC-7091
S-02115 | LT-7251 | 214 | Level Transmitter, d/P |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | By Detail Engineer |  | By Detail Engineer |  | 4.42 kg/m3 | 894 kg/m3 | [25 empty] | L | 7251 |  | LIC-7251
S-02115 | LT-5001 | 214.2 | Level Transmitter, Radar Type |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | By vendor | By vendor | [29 empty] | L | 5001 |  | LI-5001
S-02115 | LST-5002 | 214.2 | Level Transmitter, Radar Type |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | By vendor | By vendor | [29 empty] | L | 5002 |  | LI-5002
S-02115 | LT-5396 | 214.2 | Level Transmitter, Radar Type |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | By vendor | By vendor | [29 empty] | L | 5396 |  | LI-5396
S-02115 | LST-5397 | 214.2 | Level Transmitter, Radar Type |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | By vendor | By vendor | [29 empty] | L | 5397 |  | LI-5397
S-02115 | LT-5413 | 214.2 | Level Transmitter, Radar Type |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | By vendor | By vendor | [29 empty] | L | 5413 |  | LI-5413
S-02115 | LST-5414 | 214.2 | Level Transmitter, Radar Type |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | By vendor | By vendor | [29 empty] | L | 5414 |  | LI-5414
S-02115 | LT-5446 | 214.2 | Level Transmitter, Radar Type |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | By vendor | By vendor | [29 empty] | L | 5446 |  | LI-5446
S-02115 | LST-5447 | 214.2 | Level Transmitter, Radar Type |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | By vendor | By vendor | [29 empty] | L | 5447 |  | LI-5447
S-02115 | LT-7001 | 214.2 | Level Transmitter, Radar Type |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | By vendor | By vendor | [29 empty] | L | 7001 |  | LI-7001
S-02115 | LT-7002 | 214.2 | Level Transmitter, Radar Type |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | By vendor | By vendor | [29 empty] | L | 7002 |  | LI-7002
S-02115 | LT-7101 | 214.2 | Level Transmitter, Radar Type |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | By vendor | By vendor | [29 empty] | L | 7101 |  | LI-7101
S-02115 | LT-7102 | 214.2 | Level Transmitter, Radar Type |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | By vendor | By vendor | [29 empty] | L | 7102 |  | LI-7102
S-02115 | LT-7060 | 215 | Pressure Transmitter |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | By detailed engineering | [30 empty] | L | 7060 |  | LI-7060
S-02115 | LT-7061 | 215 | Pressure Transmitter |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | By detailed engineering | [30 empty] | L | 7061 |  | LI-7061
S-02115 | PT-1001 | 215 | Pressure Transmitter |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-80 bar g | [30 empty] | P | 1001 |  | PI-1001
S-02115 | PT-1006 | 215 | Pressure Transmitter |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-70 bar g | [30 empty] | P | 1006 |  | PIC-1006
S-02115 | PT-1011 | 215 | Pressure Transmitter |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-10 bar g | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | PT-1045 | 215 | Pressure Transmitter |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-70 bar g | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | PT-2001 | 215 | Pressure Transmitter |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-60 bar g | [30 empty] | P | 2001 |  | PI-2001
S-02115 | PT-2015 | 215 | Pressure Transmitter |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | 0-70 bar g | [30 empty] | P | 2015 |  | PIC-2015
S-02115 | PT-2035 | 215 | Pressure Transmitter |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-70 bar g | [30 empty] | P | 2035 |  | PI-2035
S-02115 | PT-2046 | 215 | Pressure Transmitter |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | 0-60 bar g | [30 empty] | P | 2046 |  | PI-2046
S-02115 | PT-2047 | 215 | Pressure Transmitter |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-60 bar g | [30 empty] | P | 2047 |  | PI-2047
S-02115 | PT-2061 | 215 | Pressure Transmitter |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-70 bar g | [30 empty] | P | 2061 |  | PI-2061
S-02115 | PT-2073 | 215 | Pressure Transmitter |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-70 bar g | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | PT-2077 | 215 | Pressure Transmitter |  | P09 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | 0-70 bar g | [30 empty] | P | 2077 |  | PI-2077
S-02115 | PT-2099 | 215 | Pressure Transmitter |  | P10 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | 0-60 bar g | [30 empty] | P | 2099 |  | PI-2099
S-02115 | PT-2111 | 215 | Pressure Transmitter |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | -25 - 0 mbar g | [30 empty] | P | 2111 |  | PI-2111
S-02115 | PT-2112 | 215 | Pressure Transmitter |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 0-100 mbar g | [30 empty] | P | 2112 |  | PI-2112
S-02115 | PT-2150 | 215 | Pressure Transmitter |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-80 bar g | [30 empty] | P | 2150 |  | PI-2150
S-02115 | PT-2156 | 215 | Pressure Transmitter |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | -100 - 0 mbar g | [30 empty] | P | 2156 |  | PI-2156
S-02115 | PST/A-2163 | 215 | Pressure Transmitter |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-60 mbar g | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PST/B-2163 | 215 | Pressure Transmitter |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-60 mbar g | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PST/C-2163 | 215 | Pressure Transmitter |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-60 mbar g | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PT-2268 | 215 | Pressure Transmitter |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 0-60 bar g | [30 empty] | P | 2268 |  | PI-2268
S-02115 | PT-2282 | 215 | Pressure Transmitter |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-60 bar g | [30 empty] | P | 2282 |  | PI-2282
S-02115 | PT-2307 | 215 | Pressure Transmitter |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-60 bar g | [30 empty] | P | 2307 |  | PI-2307
S-02115 | PT-2322 | 215 | Pressure Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-45 bar g | [30 empty] | P | 2322 |  | PI-2322
S-02115 | PT-2324 | 215 | Pressure Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-40 bar g | [30 empty] | P | 2324 |  | PI-2324
S-02115 | PT-2352 | 215 | Pressure Transmitter |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | 0-35 bar g | [30 empty] | P | 2352 |  | PI-2352
S-02115 | PT-2361 | 215 | Pressure Transmitter |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-140 bar g | [30 empty] | P | 2361 |  | PIC-2361
S-02115 | PT-2363 | 215 | Pressure Transmitter |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-140 bar g | [30 empty] | P | 2363 |  | PIC-2363
S-02115 | PST/A-2372 | 215 | Pressure Transmitter |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-140 bar g | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PST/B-2372 | 215 | Pressure Transmitter |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-140 bar g | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PST/C-2372 | 215 | Pressure Transmitter |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-140 bar g | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PT-2406 | 215 | Pressure Transmitter |  | P19 |  | 34"-RFG-20-120-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 0-40 bar g | [30 empty] | P | 2406 |  | PIC-2406
S-02115 | PT-2416 | 215 | Pressure Transmitter |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | 0-80 bar g | [30 empty] | P | 2416 |  | PI-2416
S-02115 | PT-2453 | 215 | Pressure Transmitter |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | 0-80 bar g | [30 empty] | P | 2453 |  | PI-2453
S-02115 | PT-2455 | 215 | Pressure Transmitter |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-10 bar g | [30 empty] | P | 2455 |  | PI-2455
S-02115 | PT-2481 | 215 | Pressure Transmitter |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-35 bar g | [30 empty] | P | 2481 |  | PIC-2481
S-02115 | PT-2493 | 215 | Pressure Transmitter |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 0-80 bar g | [30 empty] | P | 2493 |  | PI-2493
S-02115 | PT-2536 | 215 | Pressure Transmitter |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-10 bar g | [30 empty] | P | 2536 |  | PIC-2536
S-02115 | PT-2540 | 215 | Pressure Transmitter |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | 0-3 bar g | [30 empty] | P | 2540 |  | PI-2540
S-02115 | PST/A-2554 | 215 | Pressure Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-3 bar g | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PST/B-2554 | 215 | Pressure Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-3 bar g | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PST/C-2554 | 215 | Pressure Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-3 bar g | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PST/A-2556 | 215 | Pressure Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 1) bar g | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PST/B-2556 | 215 | Pressure Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 1) bar g | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PST/C-2556 | 215 | Pressure Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 1) bar g | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PT-2579 | 215 | Pressure Transmitter |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-12 bar g | [30 empty] | P | 2579 |  | PI-2579
S-02115 | PST-2582 | 215 | Pressure Transmitter |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-12 bar g | [30 empty] | P | 2582 |  | PI-2582
S-02115 | PT-2601 | 215 | Pressure Transmitter |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-35 bar g | [30 empty] | P | 2601 |  | PI-2601
S-02115 | PT-2603 | 215 | Pressure Transmitter |  | U17 |  | 3"-HG-20-109-D24-N |  |  | 29 | 25 | bar g |  | 40 | 100 | °C | 0-35 bar g | [30 empty] | P | 2603 |  | PIC-2603
S-02115 | PT-2607 | 215 | Pressure Transmitter |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-120 bar g | [30 empty] | P | 2607 |  | PI-2607
S-02115 | PT-2608 | 215 | Pressure Transmitter |  | U17 |  | 3"-HG-20-108-F24-N |  |  | 55 | 50.4 | bar g |  | 48 | 100 | °C | 0-80 bar g | [30 empty] | P | 2608 |  | PIC-2608
S-02115 | PT-3007 | 215 | Pressure Transmitter |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-35 bar g | [30 empty] | P | 3007 |  | PIC-3007
S-02115 | PT-3023 | 215 | Pressure Transmitter |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 0-120 bar g | [30 empty] | P | 3023 |  | PI-3023
S-02115 | PST/A-3042 | 215 | Pressure Transmitter |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-60 bar g | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PST/B-3042 | 215 | Pressure Transmitter |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-60 bar g | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PST/C-3042 | 215 | Pressure Transmitter |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-60 bar g | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PT-3071 | 215 | Pressure Transmitter |  | P24 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-120 bar g | [30 empty] | P | 3071 |  | PI-3071
S-02115 | PT-3075 | 215 | Pressure Transmitter |  | P24 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-120 bar g | [30 empty] | P | 3075 |  | PI-3075
S-02115 | PT-3079 | 215 | Pressure Transmitter |  | P24 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-120 bar g | [30 empty] | P | 3079 |  | PI-3079
S-02115 | PT-3166 | 215 | Pressure Transmitter |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-120 bar g | [30 empty] | P | 3166 |  | PIC-3166
S-02115 | PT-3194 | 215 | Pressure Transmitter |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 0-10 bar g | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | PT-5004 | 215 | Pressure Transmitter |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | -10 - +30 mbar g | [30 empty] | P | 5004 |  | PI-5004
S-02115 | PT-5022 | 215 | Pressure Transmitter |  | P29 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 0-14 bar g |  |  | Diaphragm seal | [27 empty] | P | 5022 |  | PI-5022
S-02115 | PT-5047 | 215 | Pressure Transmitter |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-1.5 bar g |  | High temp. version | Traced | [27 empty] | P | 5047 |  | PI-5047
S-02115 | PT-5049 | 215 | Pressure Transmitter |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-1.5 bar g |  | High temp. version | Traced | [27 empty] | P | 5049 |  | PI-5049
S-02115 | PT-5051 | 215 | Pressure Transmitter |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-1.5 bar g |  | High temp. version | Traced | [27 empty] | P | 5051 |  | PI-5051
S-02115 | PT-5069 | 215 | Pressure Transmitter |  | P31 |  | 14"-LPS-50-103-D24-H |  |  | 9.5 | 2.4 | bar g |  | 187 | 340 | °C | 0-6 bar g | [30 empty] | P | 5069 |  | PIC-5069
S-02115 | PT-5083 | 215 | Pressure Transmitter |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | 0-10 bar g | [30 empty] | P | 5083 |  | PI-5083
S-02115 | PT-5091 | 215 | Pressure Transmitter |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-1.5 bar g | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | PT-5093 | 215 | Pressure Transmitter |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-12 bar g | [30 empty] | P | 5093 |  | PI-5093
S-02115 | PT-5111 | 215 | Pressure Transmitter |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-4 bar g | [30 empty] | P | 5111 |  | PI-5111
S-02115 | PT-5139 | 215 | Pressure Transmitter |  | P33 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 0-10 bar g |  |  | Diaphragm Seal | [27 empty] | P | 5139 |  | PI-5139
S-02115 | PT-5166 | 215 | Pressure Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1.5 bar g |  | High temp. version | Traced | [27 empty] | P | 5166 |  | PI-5166
S-02115 | PT-5168 | 215 | Pressure Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1 bar g |  | High temp. version | Traced | [27 empty] | P | 5168 |  | PI-5168
S-02115 | PT-5170 | 215 | Pressure Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1 bar g |  | High temp. version | Traced | [27 empty] | P | 5170 |  | PI-5170
S-02115 | PT-5172 | 215 | Pressure Transmitter |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | 0-0.6 bar g |  | High temp. version | Traced | [27 empty] | P | 5172 |  | PI-5172
S-02115 | PT-5176 | 215 | Pressure Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1.5 bar g |  | High temp. version | Traced | [27 empty] | P | 5176 |  | PI-5176
S-02115 | PST/A-5207 | 215 | Pressure Transmitter |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | -0.1 - +0.9 bar g | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PST/B-5207 | 215 | Pressure Transmitter |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | -0.1 - +0.9 bar g | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PST/C-5207 | 215 | Pressure Transmitter |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | -0.1 - +0.9 bar g | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PT-5219 | 215 | Pressure Transmitter |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-12 bar g | [30 empty] | P | 5219 |  | PI-5219
S-02115 | PT-5240 | 215 | Pressure Transmitter |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 0-20 bar g |  |  | Diaphragm Seal | [27 empty] | P | 5240 |  | PI-5240
S-02115 | PT-5252 | 215 | Pressure Transmitter |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | 0-6 bar g |  | High temp. version | Traced | [27 empty] | P | 5252 |  | PI-5252
S-02115 | PT-5254 | 215 | Pressure Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g |  | High temp. version | Traced | [27 empty] | P | 5254 |  | PI-5254
S-02115 | PT-5256 | 215 | Pressure Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g |  | High temp. version | Traced | [27 empty] | P | 5256 |  | PI-5256
S-02115 | PT-5258 | 215 | Pressure Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g |  | High temp. version | Traced | [27 empty] | P | 5258 |  | PI-5258
S-02115 | PT-5260 | 215 | Pressure Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g |  | High temp. version | Traced | [27 empty] | P | 5260 |  | PI-5260
S-02115 | PT-5307 | 215 | Pressure Transmitter |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 0-14 bar g | [30 empty] | P | 5307 |  | PI-5307
S-02115 | PT-5335 | 215 | Pressure Transmitter |  | P40 |  | 6"-PMP-50-140-D24-P |  |  | 19 | 3.6 | bar g |  | 101 | 165 | °C | 0-25 bar g | [30 empty] | P | 5335 |  | PI-5335
S-02115 | PT-5367 | 215 | Pressure Transmitter |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 0-90 bar g |  |  | Diaphragm Seal | [27 empty] | P | 5367 |  | PI-5367
S-02115 | PT-5369 | 215 | Pressure Transmitter |  | P41 |  | 2"-PMW-50-124-B24-P |  |  | 7.5 | 4.5 | bar g |  | 149 | 175 | °C | 0-10 bar g |  |  | Diaphragm Seal | [27 empty] | P | 5369 |  | PI-5369
S-02115 | PT-5387 | 215 | Pressure Transmitter |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-10 bar g | [30 empty] | P | 5387 |  | PI-5387
S-02115 | PT-5398 | 215 | Pressure Transmitter |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | -10 - +30 mbar g | [30 empty] | P | 5398 |  | PI-5398
S-02115 | PT-5415 | 215 | Pressure Transmitter |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | -10 - +30 mbar g | [30 empty] | P | 5415 |  | PI-5415
S-02115 | PT-5421 | 215 | Pressure Transmitter |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 0-10 bar g | [30 empty] | P | 5421 |  | PI-5421
S-02115 | PT-5448 | 215 | Pressure Transmitter |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | -10 - +30 mbar g | [30 empty] | P | 5448 |  | PI-5448
S-02115 | PT-6010 | 215 | Pressure Transmitter |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | 0-90 bar g | [30 empty] | P | 6010 |  | PI-6010
S-02115 | PT-6025 | 215 | Pressure Transmitter |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | 0-60 bar g | [30 empty] | P | 6025 |  | PIC-6025
S-02115 | PT-6031 | 215 | Pressure Transmitter |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-80 bar g | [30 empty] | P | 6031 |  | PI-6031
S-02115 | PT-6054 | 215 | Pressure Transmitter |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | 0-70 bar g | [30 empty] | P | 6054 |  | PI-6054
S-02115 | PT-6088 | 215 | Pressure Transmitter |  | P08 |  | 4"-BD-60-119-B40-P |  |  | 9 | 3 | bar g |  | 78 | 150 | °C | 0-6 bar g | [30 empty] | P | 6088 |  | PI-6088
S-02115 | PT-7001 | 215 | Pressure Transmitter |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-60 bar g | [30 empty] | P | 7001 |  | PIC-7001
S-02115 | PT-7002 | 215 | Pressure Transmitter |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-120 bar g | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PT-7003 | 215 | Pressure Transmitter |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-60 bar g | [30 empty] | P | 7003 |  | PIC-7003
S-02115 | PT-7004 | 215 | Pressure Transmitter |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-60 bar g | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | PT-7021 | 215 | Pressure Transmitter |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-60 bar g | [30 empty] | P | 7021 |  | PI-7021
S-02115 | PT-7025 | 215 | Pressure Transmitter |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-120 bar g | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | PT-7028 | 215 | Pressure Transmitter |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | 0-60 bar g | [30 empty] | P | 7028 |  | PIC-7028
S-02115 | PT-7031 | 215 | Pressure Transmitter |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-60 bar g | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PT-7034 | 215 | Pressure Transmitter |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-60 bar g | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | PT-7051 | 215 | Pressure Transmitter |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-12 bar g | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | PT-7055 | 215 | Pressure Transmitter |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-12 bar g | [30 empty] | P | 7055 |  | PIC-7055
S-02115 | PT-7056 | 215 | Pressure Transmitter |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | 0-12 bar g | [30 empty] | P | 7056 |  | PIC-7056
S-02115 | PT-7094 | 215 | Pressure Transmitter |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-4 bar g | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | PST-7112 | 215 | Pressure Transmitter |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-3 bar g | [30 empty] | P | 7112 |  | PI-7112
S-02115 | PST-7116 | 215 | Pressure Transmitter |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-3 bar g | [30 empty] | P | 7116 |  | PI-7116
S-02115 | PST-7120 | 215 | Pressure Transmitter |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-3 bar g | [30 empty] | P | 7120 |  | PI-7120
S-02115 | PT-7127 | 215 | Pressure Transmitter |  | U10 |  | 12"-BFW-70-140-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-200 bar g | [30 empty] | P | 7127 |  | PI-7127
S-02115 | PT-7141 | 215 | Pressure Transmitter |  | U11 |  | 8"-BFW-70-164-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 0-100 bar g | [30 empty] | P | 7141 |  | PIC-7141
S-02115 | PT-8001 | 215 | Pressure Transmitter |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | 0-3 bar g | [30 empty] | P | 8001 |  | PI-8001
S-02115 | PDT-1032 | 216 | Diff. Press. Transmitter |  | P04 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-1.6 bar |  |  | PRG-10-101 | [27 empty] | P | 1032 |  | PDI-1032
S-02115 | PDT-2004 | 216 | Diff. Press. Transmitter |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-1 bar |  |  | PO-20-107 | [27 empty] | P | 2004 |  | PDI-2004
S-02115 | PDT-2032 | 216 | Diff. Press. Transmitter |  | P03 |  | 4"-HPS-70-103-F34-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-1 bar |  |  | HPS-20-106 | [27 empty] | P | 2032 |  | PDI-2032
S-02115 | PDST/A-2036 | 216 | Diff. Press. Transmitter |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-8 bar |  |  | HPS-20-109 | [27 empty] | P | 2036 |  | PDI-2036
S-02115 | PDST/B-2036 | 216 | Diff. Press. Transmitter |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-8 bar |  |  | HPS-20-109 | [27 empty] | P | 2036 |  | PDI-2036
S-02115 | PDST/C-2036 | 216 | Diff. Press. Transmitter |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-8 bar |  |  | HPS-20-109 | [27 empty] | P | 2036 |  | PDI-2036
S-02115 | PDT-2051 | 216 | Diff. Press. Transmitter |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-4 bar |  |  | PO-20-116 | [27 empty] | P | 2051 |  | PDI-2051
S-02115 | PST/A-2224 | 216 | Diff. Press. Transmitter |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | -40 - +20 mmWG |  |  | Atmospheric | [27 empty] | P | 2224 |  | PIC-2224
S-02115 | PST/B-2224 | 216 | Diff. Press. Transmitter |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | -40 - +20 mmWG |  |  | Atmospheric | [27 empty] | P | 2224 |  | PIC-2224
S-02115 | PST/C-2224 | 216 | Diff. Press. Transmitter |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | -40 - +20 mmWG |  |  | Atmospheric | [27 empty] | P | 2224 |  | PIC-2224
S-02115 | PDT-2252 | 216 | Diff. Press. Transmitter |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | 0-2 bar |  |  | RFG-20-101 | [27 empty] | P | 2252 |  | PDI-2252
S-02115 | PDT-2283 | 216 | Diff. Press. Transmitter |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-8 bar | [30 empty] | P | 2283 |  | PDI-2283
S-02115 | PDT-2321 | 216 | Diff. Press. Transmitter |  | P16A |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-6 bar | [30 empty] | P | 2321 |  | PDI-2321
S-02115 | PDT-2323 | 216 | Diff. Press. Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-1 bar | [30 empty] | P | 2323 |  | PDI-2323
S-02115 | PDT-2417 | 216 | Diff. Press. Transmitter |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-6 bar |  |  | 12"-BFW-20-104-G24-H | [27 empty] | P | 2417 |  | PDIC-2417
S-02115 | PDT-2575 | 216 | Diff. Press. Transmitter |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | By Vendor bar |  |  | N-20-110 | [27 empty] | P | 2575 |  | PDIC-2575
S-02115 | PDT-3024 | 216 | Diff. Press. Transmitter |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 0-10 bar |  |  | SG-30-118 | [27 empty] | P | 3024 |  | PDI-3024
S-02115 | PDT-3112 | 216 | Diff. Press. Transmitter |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-4 bar |  |  | SG-30-111 | [27 empty] | P | 3112 |  | PDI-3112
S-02115 | PDT-3115 | 216 | Diff. Press. Transmitter |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-4 bar |  |  | SG-30-108 | [27 empty] | P | 3115 |  | PDI-3115
S-02115 | PDT-3117 | 216 | Diff. Press. Transmitter |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-4 bar |  |  | SG-30-120 | [27 empty] | P | 3117 |  | PDI-3117
S-02115 | PDT-5385 | 216 | Diff. Press. Transmitter |  | P42 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-0.5 bar | [30 empty] | P | 5385 |  | PDI-5385
S-02115 | PDT-6026 | 216 | Diff. Press. Transmitter |  | P06 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | 0-2.5 bar |  |  | PRG-60-101 | [27 empty] | P | 6026 |  | PDI-6026
S-02115 | PDT-6028 | 216 | Diff. Press. Transmitter |  | P06 |  | 3"-PRC-20-107-G40-H |  |  | 71 | 45 | bar g |  | 115 | 180 | °C | 0-2 bar |  |  | PRC-60-104 | [27 empty] | P | 6028 |  | PDI-6028
S-02115 | TT-1001 | 218 | Temperature Transmitter |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 1001 |  | TI-1001
S-02115 | TT-1010 | 218 | Temperature Transmitter |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 1010 |  | TI-1010
S-02115 | TT-1012 | 218 | Temperature Transmitter |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 1012 |  | TI-1012
S-02115 | TT-1034 | 218 | Temperature Transmitter |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1034 |  | TI-1034
S-02115 | TT-1035 | 218 | Temperature Transmitter |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1035 |  | TI-1035
S-02115 | TT-1037 | 218 | Temperature Transmitter |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1037 |  | TI-1037
S-02115 | TT-1041 | 218 | Temperature Transmitter |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1041 |  | TI-1041
S-02115 | TT-1042 | 218 | Temperature Transmitter |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1042 |  | TI-1042
S-02115 | TT-1045 | 218 | Temperature Transmitter |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1045 |  | TI-1045
S-02115 | TT-1047 | 218 | Temperature Transmitter |  | P04 |  | 8"-FLG-10-113-B24-P |  |  | 5 |  | bar g |  |  | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 1047 |  | TI-1047
S-02115 | TT-2001 | 218 | Temperature Transmitter |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2001 |  | TI-2001
S-02115 | TT-2003 | 218 | Temperature Transmitter |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2003 |  | TI-2003
S-02115 | TT-2039 | 218 | Temperature Transmitter |  | P03 |  | 4"-HPS-20-109-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2039 |  | TI-2039
S-02115 | TT-2044 | 218 | Temperature Transmitter |  | P03 |  | 6"-VA-20-104-F70-P |  |  | 45 |  | bar g |  |  | 255 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2044 |  | TI-2044
S-02115 | TT-2046 | 218 | Temperature Transmitter |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2046 |  | TI-2046
S-02115 | TST/A-2047 | 218 | Temperature Transmitter |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2047 |  | TI-2047
S-02115 | TST/B-2047 | 218 | Temperature Transmitter |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2047 |  | TI-2047
S-02115 | TST/C-2047 | 218 | Temperature Transmitter |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2047 |  | TI-2047
S-02115 | TT-2050 | 218 | Temperature Transmitter |  | P03 |  | 2"-VA-20-101-F70-P |  |  | 4.5 |  | bar g |  |  | 255 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2050 |  | TI-2050
S-02115 | TT-2061 | 218 | Temperature Transmitter |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2061 |  | TI-2061
S-02115 | TT-2074 | 218 | Temperature Transmitter |  | P09 |  | 24"-FLG-20-107-B24-P |  |  | 5 |  | bar g |  |  | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2074 |  | TI-2074
S-02115 | TT-2111 | 218 | Temperature Transmitter |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2111 |  | TI-2111
S-02115 | TT-2112 | 218 | Temperature Transmitter |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2112 |  | TI-2112
S-02115 | TT-2148 | 218 | Temperature Transmitter |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2148 |  | TI-2148
S-02115 | TT-2149 | 218 | Temperature Transmitter |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2149 |  | TI-2149
S-02115 | TT-2150 | 218 | Temperature Transmitter |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2150 |  | TI-2150
S-02115 | TT-2151 | 218 | Temperature Transmitter |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2151 |  | TI-2151
S-02115 | TT-2154 | 218 | Temperature Transmitter |  | P12 |  | WHS | [6 empty] | 236.3 |  | °C | 0-300 °C | N | [29 empty] | T | 2154 |  | TI-2154
S-02115 | TT-2155 | 218 | Temperature Transmitter |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | 0-200 °C | K | [29 empty] | T | 2155 |  | TI-2155
S-02115 | TT-2161 | 218 | Temperature Transmitter |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2161 |  | TI-2161
S-02115 | TT-2162 | 218 | Temperature Transmitter |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2162 |  | TI-2162
S-02115 | TT-2220 | 218 | Temperature Transmitter |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2220 |  | TIC-2220
S-02115 | TST/A-2221 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | N | [29 empty] | T | 2221 |  | TI-2221
S-02115 | TST/B-2221 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | N | [29 empty] | T | 2221 |  | TI-2221
S-02115 | TST/C-2221 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | N | [29 empty] | T | 2221 |  | TI-2221
S-02115 | TT-2226 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 1093 |  | °C | 0-1200 °C | N | [29 empty] | T | 2226 |  | TI-2226
S-02115 | TT-2227 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 794 |  | °C | 0-900 °C | N | [29 empty] | T | 2227 |  | TI-2227
S-02115 | TT-2228 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | -0.02 | bar g |  | 439 |  | °C | 0-500 °C | N | [29 empty] | T | 2228 |  | TI-2228
S-02115 | TT-2229 | 218 | Temperature Transmitter |  | P13 |  | WHS |  |  |  | 0.05 | bar g |  | 350 |  | °C | 0-400 °C | N | [29 empty] | T | 2229 |  | TI-2229
S-02115 | TT-2232 | 218 | Temperature Transmitter |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2232 |  | TIC-2232
S-02115 | TT-2234 | 218 | Temperature Transmitter |  | P13 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-800 °C | K | [29 empty] | T | 2234 |  | TI-2234
S-02115 | TT-2253 | 218 | Temperature Transmitter |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2253 |  | TIC-2253
S-02115 | TT-2254 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2254 |  | TI-2254
S-02115 | TT-2255 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2255 |  | TI-2255
S-02115 | TT-2256 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2256 |  | TI-2256
S-02115 | TT-2257 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2257 |  | TI-2257
S-02115 | TT-2258 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2258 |  | TI-2258
S-02115 | TT-2259 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2259 |  | TI-2259
S-02115 | TT-2260 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2260 |  | TI-2260
S-02115 | TT-2261 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2261 |  | TI-2261
S-02115 | TT-2262 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2262 |  | TI-2262
S-02115 | TT-2263 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2263 |  | TI-2263
S-02115 | TT-2264 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2264 |  | TI-2264
S-02115 | TT-2265 | 218 | Temperature Transmitter |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | K | [29 empty] | T | 2265 |  | TI-2265
S-02115 | TT-2268 | 218 | Temperature Transmitter |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 0-600 °C | K | [29 empty] | T | 2268 |  | TI-2268
S-02115 | TT-2285 | 218 | Temperature Transmitter |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2285 |  | TI-2285
S-02115 | TT-2295 | 218 | Temperature Transmitter |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | N | [29 empty] | T | 2295 |  | TI-2295
S-02115 | TT-2297 | 218 | Temperature Transmitter |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | N | [29 empty] | T | 2297 |  | TI-2297
S-02115 | TT-2303 | 218 | Temperature Transmitter |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | N | [29 empty] | T | 2303 |  | TI-2303
S-02115 | TT-2304 | 218 | Temperature Transmitter |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | N | [29 empty] | T | 2304 |  | TI-2304
S-02115 | TST/A-2305 | 218 | Temperature Transmitter |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | N | [29 empty] | T | 2305 |  | TI-2305
S-02115 | TST/B-2305 | 218 | Temperature Transmitter |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | N | [29 empty] | T | 2305 |  | TI-2305
S-02115 | TST/C-2305 | 218 | Temperature Transmitter |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | N | [29 empty] | T | 2305 |  | TI-2305
S-02115 | TST/A-2325 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2325 |  | TI-2325
S-02115 | TST/B-2325 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2325 |  | TI-2325
S-02115 | TST/C-2325 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2325 |  | TI-2325
S-02115 | TT-2326 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2326 |  | TI-2326
S-02115 | TT-2327 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2327 |  | TI-2327
S-02115 | TT-2328 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2328 |  | TI-2328
S-02115 | TST/A-2329 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 0-700 °C | K | [29 empty] | T | 2329 |  | TI-2329
S-02115 | TST/B-2329 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 0-700 °C | K | [29 empty] | T | 2329 |  | TI-2329
S-02115 | TST/C-2329 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 0-700 °C | K | [29 empty] | T | 2329 |  | TI-2329
S-02115 | TT-2330 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2330 |  | TI-2330
S-02115 | TT-2331 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2331 |  | TI-2331
S-02115 | TT-2332 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2332 |  | TI-2332
S-02115 | TST/A-2333 | 218 | Temperature Transmitter |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2333 |  | TI-2333
S-02115 | TST/B-2333 | 218 | Temperature Transmitter |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2333 |  | TI-2333
S-02115 | TST/C-2333 | 218 | Temperature Transmitter |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2333 |  | TI-2333
S-02115 | TST/A-2334 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2334 |  | TI-2334
S-02115 | TST/B-2334 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2334 |  | TI-2334
S-02115 | TST/C-2334 | 218 | Temperature Transmitter |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | N | [29 empty] | T | 2334 |  | TI-2334
S-02115 | TST/A-2335 | 218 | Temperature Transmitter |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C | K | [29 empty] | T | 2335 |  | TIC-2335
S-02115 | TST/B-2335 | 218 | Temperature Transmitter |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C | K | [29 empty] | T | 2335 |  | TIC-2335
S-02115 | TST/C-2335 | 218 | Temperature Transmitter |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C | K | [29 empty] | T | 2335 |  | TIC-2335
S-02115 | TST/A-2336 | 218 | Temperature Transmitter |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C | K | [29 empty] | T | 2336 |  | TIC-2336
S-02115 | TST/B-2336 | 218 | Temperature Transmitter |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C | K | [29 empty] | T | 2336 |  | TIC-2336
S-02115 | TST/C-2336 | 218 | Temperature Transmitter |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C | K | [29 empty] | T | 2336 |  | TIC-2336
S-02115 | TT-2351 | 218 | Temperature Transmitter |  | P17 |  | 24"-RFG-20-110-D34-H |  |  | 30 | 26.3 | bar g |  | 360 | 390 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2351 |  | TI-2351
S-02115 | TT-2352 | 218 | Temperature Transmitter |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2352 |  | TI-2352
S-02115 | TT-2353 | 218 | Temperature Transmitter |  | P17 |  | 24"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | 0-500 °C | K | [29 empty] | T | 2353 |  | TI-2353
S-02115 | TT-2354 | 218 | Temperature Transmitter |  | P17 |  | 42"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | 0-500 °C | K | [29 empty] | T | 2354 |  | TI-2354
S-02115 | TT-2355 | 218 | Temperature Transmitter |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | K | [29 empty] | T | 2355 |  | TI-2355
S-02115 | TT-2356 | 218 | Temperature Transmitter |  | P17 |  | 24"-HHPS-20-117-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | K | [29 empty] | T | 2356 |  | TI-2356
S-02115 | TT-2359 | 218 | Temperature Transmitter |  | P17 |  | 20"-HHPS-20-103-H24-H |  |  | 112 | 101 | bar g |  | 338 | 370 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 2359 |  | TI-2359
S-02115 | TST/A-2360 | 218 | Temperature Transmitter |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | K | [29 empty] | T | 2360 |  | TIC-2360
S-02115 | TST/B-2360 | 218 | Temperature Transmitter |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | K | [29 empty] | T | 2360 |  | TIC-2360
S-02115 | TST/C-2360 | 218 | Temperature Transmitter |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | K | [29 empty] | T | 2360 |  | TIC-2360
S-02115 | TT-2371 | 218 | Temperature Transmitter |  | P18 |  | 12"-BFW-20-102-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 2371 |  | TI-2371
S-02115 | TT-2402 | 218 | Temperature Transmitter |  | P19 |  | 34"-RFG-20-117-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2402 |  | TI-2402
S-02115 | TT-2407 | 218 | Temperature Transmitter |  | P19 |  | 16"-FLG-20-120-B40-P |  |  | 5 |  | bar g |  |  | 200 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2407 |  | TI-2407
S-02115 | TT-2418 | 218 | Temperature Transmitter |  | P19 |  | 12"-BFW-20-104-G24 |  |  | 113 | 104 | bar g |  | 122 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2418 |  | TI-2418
S-02115 | TT-2421 | 218 | Temperature Transmitter |  | P19 |  | 34"-RFG-20-122-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2421 |  | TI-2421
S-02115 | TT-2444 | 218 | Temperature Transmitter |  | P20 |  | 34"-RFG-20-124-D40-P |  |  | 29 | 24.4 | bar g |  | 132 | 200 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 2444 |  | TI-2444
S-02115 | TT-2455 | 218 | Temperature Transmitter |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2455 |  | TI-2455
S-02115 | TT-2457 | 218 | Temperature Transmitter |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2457 |  | TIC-2457
S-02115 | TT-2472 | 218 | Temperature Transmitter |  | P21 |  | 34"-RFG-20-125-D40-P |  |  | 29 | 24.2 | bar g |  | 65 | 120 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2472 |  | TI-2472
S-02115 | TT-2476 | 218 | Temperature Transmitter |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2476 |  | TI-2476
S-02115 | TT-2484 | 218 | Temperature Transmitter |  | P21 |  | 12"-FLG-20-123-B24-N |  |  | 5 |  | bar g |  |  | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2484 |  | TI-2484
S-02115 | TT-2493 | 218 | Temperature Transmitter |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2493 |  | TI-2493
S-02115 | TT-2536 | 218 | Temperature Transmitter |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2536 |  | TI-2536
S-02115 | TT-2540 | 218 | Temperature Transmitter |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2540 |  | TI-2540
S-02115 | TT-2553 | 218 | Temperature Transmitter |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2553 |  | TI-2553
S-02115 | TT-2572 | 218 | Temperature Transmitter |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2572 |  | TI-2572
S-02115 | TT-2579 | 218 | Temperature Transmitter |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2579 |  | TI-2579
S-02115 | TT-2601 | 218 | Temperature Transmitter |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 2601 |  | TI-2601
S-02115 | TT-2607 | 218 | Temperature Transmitter |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 2607 |  | TI-2607
S-02115 | TT-3045 | 218 | Temperature Transmitter |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3045 |  | TI-3045
S-02115 | TST/A-3072 | 218 | Temperature Transmitter |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3072 |  | TI-3072
S-02115 | TST/B-3072 | 218 | Temperature Transmitter |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3072 |  | TI-3072
S-02115 | TST/C-3072 | 218 | Temperature Transmitter |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3072 |  | TI-3072
S-02115 | TT-3073 | 218 | Temperature Transmitter |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3073 |  | TI-3073
S-02115 | TST/A-3076 | 218 | Temperature Transmitter |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3076 |  | TI-3076
S-02115 | TST/B-3076 | 218 | Temperature Transmitter |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3076 |  | TI-3076
S-02115 | TST/C-3076 | 218 | Temperature Transmitter |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3076 |  | TI-3076
S-02115 | TT-3077 | 218 | Temperature Transmitter |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3077 |  | TI-3077
S-02115 | TST/A-3080 | 218 | Temperature Transmitter |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3080 |  | TI-3080
S-02115 | TST/B-3080 | 218 | Temperature Transmitter |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3080 |  | TI-3080
S-02115 | TST/C-3080 | 218 | Temperature Transmitter |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3080 |  | TI-3080
S-02115 | TT-3081 | 218 | Temperature Transmitter |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 3081 |  | TI-3081
S-02115 | TT-3084 | 218 | Temperature Transmitter |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-500 °C | K | [29 empty] | T | 3084 |  | TI-3084
S-02115 | TT-3111 | 218 | Temperature Transmitter |  | P25 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3111 |  | TI-3111
S-02115 | TT-3113 | 218 | Temperature Transmitter |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 3113 |  | TIC-3113
S-02115 | TT-3116 | 218 | Temperature Transmitter |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 3116 |  | TIC-3116
S-02115 | TT-3118 | 218 | Temperature Transmitter |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 3118 |  | TIC-3118
S-02115 | TT-3119 | 218 | Temperature Transmitter |  | P25 |  | 20"-SG-30-110-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3119 |  | TI-3119
S-02115 | TT-3120 | 218 | Temperature Transmitter |  | P25 |  | 20"-SG-30-109-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3120 |  | TI-3120
S-02115 | TT-3121 | 218 | Temperature Transmitter |  | P25 |  | 20"-SG-30-121-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3121 |  | TI-3121
S-02115 | TT-3142 | 218 | Temperature Transmitter |  | P26 |  | 24"-SG-30-122-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3142 |  | TI-3142
S-02115 | TT-3145 | 218 | Temperature Transmitter |  | P26 |  | 24"-SG-30-123-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3145 |  | TI-3145
S-02115 | TT-3148 | 218 | Temperature Transmitter |  | P26 |  | 24"-SG-30-124-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3148 |  | TI-3148
S-02115 | TT-3164 | 218 | Temperature Transmitter |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3164 |  | TI-3164
S-02115 | TT-3194 | 218 | Temperature Transmitter |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3194 |  | TI-3194
S-02115 | TT-3198 | 218 | Temperature Transmitter |  | P28 |  | 10"-PMC-30-111-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 3198 |  | TI-3198
S-02115 | TT-5020 | 218 | Temperature Transmitter |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5020 |  | TI-5020
S-02115 | TT-5039 | 218 | Temperature Transmitter |  | P30 |  | RFG-50 |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5039 |  | TI-5039
S-02115 | TT-5040 | 218 | Temperature Transmitter |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5040 |  | TI-5040
S-02115 | TT-5045 | 218 | Temperature Transmitter |  | P30 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5045 |  | TI-5045
S-02115 | TT-5052 | 218 | Temperature Transmitter |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5052 |  | TI-5052
S-02115 | TT-5053 | 218 | Temperature Transmitter |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5053 |  | TI-5053
S-02115 | TT-5054 | 218 | Temperature Transmitter |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5054 |  | TI-5054
S-02115 | TT-5056 | 218 | Temperature Transmitter |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5056 |  | TI-5056
S-02115 | TT-5057 | 218 | Temperature Transmitter |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5057 |  | TI-5057
S-02115 | TT-5059 | 218 | Temperature Transmitter |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5059 |  | TI-5059
S-02115 | TT-5060 | 218 | Temperature Transmitter |  | P30 |  | 20"-PMC-50-110-B24-H |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5060 |  | TI-5060
S-02115 | TT-5062 | 218 | Temperature Transmitter |  | P30 |  | 34"-PMV-50-120-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5062 |  | TI-5062
S-02115 | TT-5064 | 218 | Temperature Transmitter |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 5064 |  | TIC-5064
S-02115 | TT-5067 | 218 | Temperature Transmitter |  | P30 |  | 34"-PMW-50-122-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5067 |  | TI-5067
S-02115 | TT-5074 | 218 | Temperature Transmitter |  | P31 |  | 8"-LPC-50-110-D24-H |  |  | 18 | 2.4 | bar g |  | 138 | 190 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 5074 |  | TI-5074
S-02115 | TT-5097 | 218 | Temperature Transmitter |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5097 |  | TI-5097
S-02115 | TT-5110 | 218 | Temperature Transmitter |  | P32 |  | 6"-FLG-50-131-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 5110 |  | TI-5110
S-02115 | TT-5111 | 218 | Temperature Transmitter |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 5111 |  | TI-5111
S-02115 | TT-5165 | 218 | Temperature Transmitter |  | P34 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5165 |  | TI-5165
S-02115 | TT-5167 | 218 | Temperature Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5167 |  | TI-5167
S-02115 | TT-5171 | 218 | Temperature Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5171 |  | TI-5171
S-02115 | TT-5173 | 218 | Temperature Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5173 |  | TI-5173
S-02115 | TT-5174 | 218 | Temperature Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5174 |  | TI-5174
S-02115 | TT-5175 | 218 | Temperature Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5175 |  | TI-5175
S-02115 | TT-5177 | 218 | Temperature Transmitter |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5177 |  | TI-5177
S-02115 | TT-5180 | 218 | Temperature Transmitter |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5180 |  | TI-5180
S-02115 | TT-5181 | 218 | Temperature Transmitter |  | P34 |  | 24"-PMC-50-140-B24-H |  |  | 5 | 0.7 | bar g |  | 83 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5181 |  | TI-5181
S-02115 | TT-5184 | 218 | Temperature Transmitter |  | P34 |  | 16"-PMC-50-147-B24-H |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5184 |  | TI-5184
S-02115 | TT-5208 | 218 | Temperature Transmitter |  | P36 |  | 24"-PMP-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5208 |  | TI-5208
S-02115 | TT-5209 | 218 | Temperature Transmitter |  | P36 |  | 20"-PMP-50-102-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5209 |  | TI-5209
S-02115 | TT-5219 | 218 | Temperature Transmitter |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5219 |  | TI-5219
S-02115 | TT-5221 | 218 | Temperature Transmitter |  | P36 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 5221 |  | TI-5221
S-02115 | TT-5261 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5261 |  | TI-5261
S-02115 | TT-5262 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5262 |  | TI-5262
S-02115 | TT-5263 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5263 |  | TI-5263
S-02115 | TT-5264 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5264 |  | TI-5264
S-02115 | TT-5265 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5265 |  | TI-5265
S-02115 | TT-5266 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5266 |  | TIC-5266
S-02115 | TT-5267 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5267 |  | TIC-5267
S-02115 | TT-5268 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5268 |  | TIC-5268
S-02115 | TT-5269 | 218 | Temperature Transmitter |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5269 |  | TI-5269
S-02115 | TT-5273 | 218 | Temperature Transmitter |  | P38 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5273 |  | TI-5273
S-02115 | TT-5277 | 218 | Temperature Transmitter |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 5277 |  | TIC-5277
S-02115 | TT-5280 | 218 | Temperature Transmitter |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5280 |  | TI-5280
S-02115 | TT-5307 | 218 | Temperature Transmitter |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 5307 |  | TI-5307
S-02115 | TT-5325 | 218 | Temperature Transmitter |  | P40 |  | 24"-PMP-50-130-B24-H |  |  | 7 | 2.6 | bar g |  | 101 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5325 |  | TI-5325
S-02115 | TT-5335 | 218 | Temperature Transmitter |  | P40 |  | 6"-PMP-50-140-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5335 |  | TI-5335
S-02115 | TT-5340 | 218 | Temperature Transmitter |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 5340 |  | TI-5340
S-02115 | TT-5369 | 218 | Temperature Transmitter |  | P41 |  | 2"-PMW-50-125-B24-P |  |  | 7.5 | 4.3 | bar g |  | 65 | 120 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5369 |  | TI-5369
S-02115 | TT-5381 | 218 | Temperature Transmitter |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 5381 |  | TI-5381
S-02115 | TT-5441 | 218 | Temperature Transmitter |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5441 |  | TI-5441
S-02115 | TT-5442 | 218 | Temperature Transmitter |  | P45 |  | 2"-LOS-50-113-B24-P |  |  | 7.5 | 2.5 | bar g |  | 115 | 175 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 5442 |  | TI-5442
S-02115 | TT-5443 | 218 | Temperature Transmitter |  | P45 |  | 2"-LOS-50-114-B24-N |  |  | 7.5 | 2 | bar g |  | 48 | 75 | °C | 0-100 °C | Pt 100 | [29 empty] | T | 5443 |  | TI-5443
S-02115 | TT-6001 | 218 | Temperature Transmitter |  | P05 |  | 18"-MPC-60-101-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 6001 |  | TI-6001
S-02115 | TT-6024 | 218 | Temperature Transmitter |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 290 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 6024 |  | TI-6024
S-02115 | TT-6026 | 218 | Temperature Transmitter |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 6026 |  | TI-6026
S-02115 | TT-6031 | 218 | Temperature Transmitter |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 6031 |  | TI-6031
S-02115 | TT-6034 | 218 | Temperature Transmitter |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 6034 |  | TI-6034
S-02115 | TT-6054 | 218 | Temperature Transmitter |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 6054 |  | TI-6054
S-02115 | TT-6056 | 218 | Temperature Transmitter |  | P07 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 6056 |  | TI-6056
S-02115 | TT-6058 | 218 | Temperature Transmitter |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 6058 |  | TI-6058
S-02115 | TT-6081 | 218 | Temperature Transmitter |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 6081 |  | TI-6081
S-02115 | TT-6084 | 218 | Temperature Transmitter |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 0-300 °C | Pt 100 | [29 empty] | T | 6084 |  | TI-6084
S-02115 | TT-7001 | 218 | Temperature Transmitter |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 7001 |  | TI-7001
S-02115 | TT-7002 | 218 | Temperature Transmitter |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 7002 |  | TIC-7002
S-02115 | TT-7003 | 218 | Temperature Transmitter |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 7003 |  | TIC-7003
S-02115 | TT-7004 | 218 | Temperature Transmitter |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 7004 |  | TIC-7004
S-02115 | TT-7007 | 218 | Temperature Transmitter |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 7007 |  | TI-7007
S-02115 | TT-7021 | 218 | Temperature Transmitter |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | K | [29 empty] | T | 7021 |  | TI-7021
S-02115 | TT-7025 | 218 | Temperature Transmitter |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 7025 |  | TIC-7025
S-02115 | TT-7026 | 218 | Temperature Transmitter |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | K | [29 empty] | T | 7026 |  | TIC-7026
S-02115 | TT-7027 | 218 | Temperature Transmitter |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | K | [29 empty] | T | 7027 |  | TIC-7027
S-02115 | TT-7031 | 218 | Temperature Transmitter |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7031 |  | TI-7031
S-02115 | TT-7032 | 218 | Temperature Transmitter |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7032 |  | TIC-7032
S-02115 | TT-7033 | 218 | Temperature Transmitter |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7033 |  | TIC-7033
S-02115 | TT-7052 | 218 | Temperature Transmitter |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7052 |  | TIC-7052
S-02115 | TT-7053 | 218 | Temperature Transmitter |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7053 |  | TIC-7053
S-02115 | TT-7056 | 218 | Temperature Transmitter |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7056 |  | TI-7056
S-02115 | TST/A-7071 | 218 | Temperature Transmitter |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7071 |  | TIC-7071
S-02115 | TST/B-7071 | 218 | Temperature Transmitter |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7071 |  | TIC-7071
S-02115 | TST/C-7071 | 218 | Temperature Transmitter |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 0-400 °C | Pt 100 | [29 empty] | T | 7071 |  | TIC-7071
S-02115 | TT-7097 | 218 | Temperature Transmitter |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-200 °C | Pt 100 | [29 empty] | T | 7097 |  | TI-7097
S-02115 | TT-7098 | 218 | Temperature Transmitter |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 0 | bar g |  | 120 | 340 | °C | 0-350 °C | Pt 100 | [29 empty] | T | 7098 |  | TI-7098
S-02115 | TT-8001 | 218 | Temperature Transmitter |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | 0-500 °C | Pt 100 | [29 empty] | T | 8001 |  | TI-8001
S-02115 | A_I/A-1001 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | A | 1001 |  | AI-1001
S-02115 | A_I/B-1001 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | A | 1001 |  | AI-1001
S-02115 | A_I/C-1001 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | A | 1001 |  | AI-1001
S-02115 | A_I-1035 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | FF AI | [30 empty] | A | 1035 |  | AI-1035
S-02115 | A_I-1045 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | FF AI | [30 empty] | A | 1045 |  | AI-1045
S-02115 | A_I/1-2223 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | FF AI | [30 empty] | A | 2223 |  | AI-2223
S-02115 | A_I/2-2223 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | FF AI | [30 empty] | A | 2223 |  | AI-2223
S-02115 | A_I-2224 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | FF AI | [30 empty] | A | 2224 |  | AI-2224
S-02115 | A_I-2379 | 227.01 | Analog Input |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | FF AI | [30 empty] | A | 2379 |  | AI-2379
S-02115 | A_I-2382 | 227.01 | Analog Input |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | FF AI | [30 empty] | A | 2382 |  | AI-2382
S-02115 | A_I-2384 | 227.01 | Analog Input |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | FF AI | [30 empty] | A | 2384 |  | AI-2384
S-02115 | A_I-2479 | 227.01 | Analog Input |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | A | 2479 |  | AI-2479
S-02115 | A_I-2531 | 227.01 | Analog Input |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | A | 2531 |  | AI-2531
S-02115 | A_I-2532 | 227.01 | Analog Input |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF AI | [30 empty] | A | 2532 |  | AI-2532
S-02115 | A_I-3001 | 227.01 | Analog Input |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | A | 3001 |  | AI-3001
S-02115 | A_I-3002 | 227.01 | Analog Input |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | A | 3002 |  | AI-3002
S-02115 | A_I-3003 | 227.01 | Analog Input |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | A | 3003 |  | AI-3003
S-02115 | A_I-3053 | 227.01 | Analog Input |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | FF AI | [30 empty] | A | 3053 |  | AI-3053
S-02115 | A_I-3055 | 227.01 | Analog Input |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | FF AI | [30 empty] | A | 3055 |  | AI-3055
S-02115 | A_I-7099 | 227.01 | Analog Input |  | U09 |  | 18"-BFW-70-129-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | FF AI | [30 empty] | A | 7099 |  | AIC-7099
S-02115 | F_I-1006 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | FF AI |  | PI-1001, TI-1001 | [28 empty] | F | 1006 |  | FI-1006
S-02115 | F_I/A-2007 | 227.01 | Analog Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 4-20 mA |  | PI-2001, TI-2001 | [28 empty] | F | 2007 |  | FIC-2007
S-02115 | F_I/B-2007 | 227.01 | Analog Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 4-20 mA |  | PI-2001, TI-2001 | [28 empty] | F | 2007 |  | FIC-2007
S-02115 | F_I/C-2007 | 227.01 | Analog Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 4-20 mA |  | PI-2001, TI-2001 | [28 empty] | F | 2007 |  | FIC-2007
S-02115 | F_I-2009 | 227.01 | Analog Input |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FF AI |  | PI-2001, TI-2001 | [28 empty] | F | 2009 |  | FIC-2009
S-02115 | F_I/A-2040 | 227.01 | Analog Input |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA |  | PIC-7003, TI-7007 | [28 empty] | F | 2040 |  | FIC-2040
S-02115 | F_I/B-2040 | 227.01 | Analog Input |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA |  | PIC-7003, TI-7007 | [28 empty] | F | 2040 |  | FIC-2040
S-02115 | F_I/C-2040 | 227.01 | Analog Input |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA |  | PIC-7003, TI-7007 | [28 empty] | F | 2040 |  | FIC-2040
S-02115 | F_I/A-2061 | 227.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA |  | PI-2061, TI-2061 | [28 empty] | F | 2061 |  | FIC-2061
S-02115 | F_I/B-2061 | 227.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA |  | PI-2061, TI-2061 | [28 empty] | F | 2061 |  | FIC-2061
S-02115 | F_I/C-2061 | 227.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA |  | PI-2061, TI-2061 | [28 empty] | F | 2061 |  | FIC-2061
S-02115 | F_I/A-2072 | 227.01 | Analog Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA |  | PIC-7003, TI-7007 | [28 empty] | F | 2072 |  | FIC-2072
S-02115 | F_I/B-2072 | 227.01 | Analog Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA |  | PIC-7003, TI-7007 | [28 empty] | F | 2072 |  | FIC-2072
S-02115 | F_I/C-2072 | 227.01 | Analog Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA |  | PIC-7003, TI-7007 | [28 empty] | F | 2072 |  | FIC-2072
S-02115 | F_I-2079 | 227.01 | Analog Input |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF AI |  | PI-2150, TI-2150 | [28 empty] | F | 2079 |  | FIC-2079
S-02115 | F_I-2091 | 227.01 | Analog Input |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AI |  | PIC-2073, TI-2061 | [28 empty] | F | 2091 |  | FIC-2091
S-02115 | F_I-2111 | 227.01 | Analog Input |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | FF AI |  | PI-2112, TI-2112 | [28 empty] | F | 2111 |  | FIC-2111
S-02115 | F_I-2115 | 227.01 | Analog Input |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | FF AI |  | PIC-7003, TI-7007 | [28 empty] | F | 2115 |  | FI-2115
S-02115 | F_I-2150 | 227.01 | Analog Input |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF AI |  | PI-2150, TI-2150 | [28 empty] | F | 2150 |  | FIC-2150
S-02115 | F_I-2151 | 227.01 | Analog Input |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF AI |  | PIC-1006, TI-2151 | [28 empty] | F | 2151 |  | FI-2151
S-02115 | F_I-2165 | 227.01 | Analog Input |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | FF AI |  | PIC-7003, TI-7007 | [28 empty] | F | 2165 |  | FI-2165
S-02115 | F_I/A-2233 | 227.01 | Analog Input |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 4-20 mA | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | F_I/B-2233 | 227.01 | Analog Input |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 4-20 mA | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | F_I/C-2233 | 227.01 | Analog Input |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 4-20 mA | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | F_I-2372 | 227.01 | Analog Input |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | FF AI |  | PI-2372 | [28 empty] | F | 2372 |  | FI-2372
S-02115 | F_I-2417 | 227.01 | Analog Input |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF AI | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | F_I-2476 | 227.01 | Analog Input |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI |  | PIC-2481, TI-2476 | [28 empty] | F | 2476 |  | FI-2476
S-02115 | F_I/1-2531 | 227.01 | Analog Input |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AI |  | PIC-1011, TI-1012 | [28 empty] | F | 2531 |  | FIC-2531
S-02115 | F_I/2-2531 | 227.01 | Analog Input |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AI |  | PIC-1011, TI-1012 | [28 empty] | F | 2531 |  | FIC-2531
S-02115 | F_I-2536 | 227.01 | Analog Input |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF AI |  | PIC-2536 A, TI-2536 | [28 empty] | F | 2536 |  | FIC-2536
S-02115 | F_I-2607 | 227.01 | Analog Input |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI |  | PI-2607, TI-2607 | [28 empty] | F | 2607 |  | FI-2607
S-02115 | F_I-3020 | 227.01 | Analog Input |  | P22 |  | 18"-SG-30-101-H40-H |  |  | 99 | 80 | bar g |  | 122 | 165 | °C | FF AI |  | PI-3023, T from compr. vendor | HIC-3020 | [27 empty] | F | 3020 |  | FI-3020
S-02115 | F_I-3041 | 227.01 | Analog Input |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | FF AI | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | F_I-3050 | 227.01 | Analog Input |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | FF AI |  | PIC-3042 | [28 empty] | F | 3050 |  | FI-3050
S-02115 | F_I-3167 | 227.01 | Analog Input |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI |  | PIC-3166 A, TI-3164 | HIC-3167 | [27 empty] | F | 3167 |  | FI-3167
S-02115 | F_I-3169 | 227.01 | Analog Input |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI |  | PIC-3166 A, TI-3164 | [28 empty] | F | 3169 |  | FIC-3169
S-02115 | F_I-3171 | 227.01 | Analog Input |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 4-20 mA |  | PIC-3166 A, TI-3164 | [28 empty] | F | 3171 |  | FIC-3171
S-02115 | F_I-3194 | 227.01 | Analog Input |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | FF AI |  | PIC-3194, TI-3194 | [28 empty] | F | 3194 |  | FI-3194
S-02115 | F_I-3198 | 227.01 | Analog Input |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | F | 3198 |  | FI-3198
S-02115 | F_I-5020 | 227.01 | Analog Input |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | F_I-5041 | 227.01 | Analog Input |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | FF AI | [30 empty] | F | 5041 |  | FIC-5041
S-02115 | F_I-5068 | 227.01 | Analog Input |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FF AI |  | PIC-7056, TI-7056 | [28 empty] | F | 5068 |  | FI-5068
S-02115 | F_I-5093 | 227.01 | Analog Input |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | F | 5093 |  | FIC-5093
S-02115 | F_I-5107 | 227.01 | Analog Input |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | F | 5107 |  | FIC-5107
S-02115 | F_I-5111 | 227.01 | Analog Input |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | FF AI |  | PI-5111, TI-5111 | [28 empty] | F | 5111 |  | FI-5111
S-02115 | F_I-5161 | 227.01 | Analog Input |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | FF AI | [30 empty] | F | 5161 |  | FIC-5161
S-02115 | F_I-5203 | 227.01 | Analog Input |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | F | 5203 |  | FIC-5203
S-02115 | F_I-5239 | 227.01 | Analog Input |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | FF AI | [30 empty] | F | 5239 |  | FIC-5239
S-02115 | F_I-5301 | 227.01 | Analog Input |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FF AI |  | PIC-7056, TI-7056 | [28 empty] | F | 5301 |  | FIC-5301
S-02115 | F_I-5321 | 227.01 | Analog Input |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | FF AI | [30 empty] | F | 5321 |  | FIC-5321
S-02115 | F_I-5336 | 227.01 | Analog Input |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | F_I-5337 | 227.01 | Analog Input |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | F | 5337 |  | FIC-5337
S-02115 | F_I-5367 | 227.01 | Analog Input |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | FF AI | [30 empty] | F | 5367 |  | FIC-5367
S-02115 | F_I-5383 | 227.01 | Analog Input |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | FF AI | [30 empty] | F | 5383 |  | FIC-5383
S-02115 | F_I-5407 | 227.01 | Analog Input |  | P43 |  | 3"-PMP-50-161-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | F | 5407 |  | FI-5407
S-02115 | F_I-5421 | 227.01 | Analog Input |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | F | 5421 |  | FI-5421
S-02115 | F_I-5441 | 227.01 | Analog Input |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | FF AI | [30 empty] | F | 5441 |  | FIC-5441
S-02115 | F_I-5501 | 227.01 | Analog Input |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | FF AI | [30 empty] | F | 5501 |  | FIC-5501
S-02115 | F_I-6031 | 227.01 | Analog Input |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | FF AI | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | F_I-6032 | 227.01 | Analog Input |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF AI | [30 empty] | F | 6032 |  | FI-6032
S-02115 | F_I-6057 | 227.01 | Analog Input |  | P07 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | FF AI | [30 empty] | F | 6057 |  | FI-6057
S-02115 | F_I-6068 | 227.01 | Analog Input |  | P07 |  | 10"-PRC-60-111-G40-H |  |  | 72 | 44 | bar g |  | 225 | 290 | °C | FF AI | [30 empty] | F | 6068 |  | FI-6068
S-02115 | F_I/A-6070 | 227.01 | Analog Input |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 4-20 mA |  | PIC-1045, TI-1045 | [28 empty] | F | 6070 |  | FIC-6070
S-02115 | F_I/B-6070 | 227.01 | Analog Input |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 4-20 mA |  | PIC-1045, TI-1045 | [28 empty] | F | 6070 |  | FIC-6070
S-02115 | F_I/C-6070 | 227.01 | Analog Input |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 4-20 mA |  | PIC-1045, TI-1045 | [28 empty] | F | 6070 |  | FIC-6070
S-02115 | F_I-6081 | 227.01 | Analog Input |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | FF AI | [30 empty] | F | 6081 |  | FIC-6081
S-02115 | F_I-6082 | 227.01 | Analog Input |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | FF AI | [30 empty] | F | 6082 |  | FIC-6082
S-02115 | F_I-6086 | 227.01 | Analog Input |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | FF AI | [30 empty] | F | 6086 |  | FIC-6086
S-02115 | F_I-7001 | 227.01 | Analog Input |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | FF AI |  | PIC-7001, TI-7001 | [28 empty] | F | 7001 |  | FI-7001
S-02115 | F_I-7029 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | FF AI |  | PI-7021, TI-7021 | [28 empty] | F | 7029 |  | FI-7029
S-02115 | F_I-7030 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-136-F34-H |  |  | 52 | 42 | bar g |  | 410 | 470 | °C | FF AI |  | PI-7021, TI-7021 | [28 empty] | F | 7030 |  | FI-7030
S-02115 | F_I-7091 | 227.01 | Analog Input |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | FF AI | [30 empty] | F | 7091 |  | FIC-7091
S-02115 | F_I-7101 | 227.01 | Analog Input |  | U22 |  | 2"-PRC-70-141-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | FF AI | [30 empty] | F | 7101 |  | FI-7101
S-02115 | F_I-7129 | 227.01 | Analog Input |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | FF AI |  | PIC-7003, TI-7007 | [28 empty] | F | 7129 |  | FI-7129
S-02115 | F_I-7134 | 227.01 | Analog Input |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | FF AI |  | PIC-7003, TI-7007 | [28 empty] | F | 7134 |  | FI-7134
S-02115 | F_I-7141 | 227.01 | Analog Input |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF AI | [30 empty] | F | 7141 |  | FIC-7141
S-02115 | L_I-2016 | 227.01 | Analog Input |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | FF AI | [30 empty] | L | 2016 |  | LIC-2016
S-02115 | L_I/A-2372 | 227.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | L_I/B-2372 | 227.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | L_I/C-2372 | 227.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | L_I-2373 | 227.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | FF AI | [30 empty] | L | 2373 |  | LI-2373
S-02115 | L_I-2403 | 227.01 | Analog Input |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF AI | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | L_I-2419 | 227.01 | Analog Input |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | FF AI | [30 empty] | L | 2419 |  | LIC-2419
S-02115 | L_I-2441 | 227.01 | Analog Input |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | FF AI | [30 empty] | L | 2441 |  | LIC-2441
S-02115 | L_I/A-2474 | 227.01 | Analog Input |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | L_I/B-2474 | 227.01 | Analog Input |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | L_I/C-2474 | 227.01 | Analog Input |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | L_I/A-3042 | 227.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | L_I/B-3042 | 227.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | L_I/C-3042 | 227.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | L_I-3043 | 227.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | FF AI | [30 empty] | L | 3043 |  | LI-3043
S-02115 | L_I/A-3161 | 227.01 | Analog Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | L_I/B-3161 | 227.01 | Analog Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | L_I/C-3161 | 227.01 | Analog Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | L_I/A-3192 | 227.01 | Analog Input |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 4-20 mA | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | L_I/B-3192 | 227.01 | Analog Input |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 4-20 mA | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | L_I/C-3192 | 227.01 | Analog Input |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 4-20 mA | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | L_I-5001 | 227.01 | Analog Input |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | FF AI | [30 empty] | L | 5001 |  | LI-5001
S-02115 | L_I-5041 | 227.01 | Analog Input |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | FF AI | [30 empty] | L | 5041 |  | LIC-5041
S-02115 | L_I-5065 | 227.01 | Analog Input |  | P30 |  | E 2024 2 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | FF AI | [30 empty] | L | 5065 |  | LI-5065
S-02115 | L_I-5070 | 227.01 | Analog Input |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | FF AI | [30 empty] | L | 5070 |  | LIC-5070
S-02115 | L_I-5093 | 227.01 | Analog Input |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | L | 5093 |  | LIC-5093
S-02115 | L_I-5161 | 227.01 | Analog Input |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | FF AI | [30 empty] | L | 5161 |  | LIC-5161
S-02115 | L_I-5182 | 227.01 | Analog Input |  | P34 |  | E 5002 4 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | FF AI | [30 empty] | L | 5182 |  | LI-5182
S-02115 | L_I-5203 | 227.01 | Analog Input |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | L | 5203 |  | LIC-5203
S-02115 | L_I-5232 | 227.01 | Analog Input |  | U15 |  | TK 5080 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | L | 5232 |  | LI-5232
S-02115 | L_I-5270 | 227.01 | Analog Input |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | FF AI | [30 empty] | L | 5270 |  | LIC-5270
S-02115 | L_I-5278 | 227.01 | Analog Input |  | P39 |  | E 5003 2 Shell |  |  | 7.5 | 3.6 |  |  | 149 | 175 | °C | FF AI | [30 empty] | L | 5278 |  | LI-5278
S-02115 | L_I-5308 | 227.01 | Analog Input |  | P39 |  | E 5003 1 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 340 | °C | FF AI | [30 empty] | L | 5308 |  | LI-5308
S-02115 | L_I-5310 | 227.01 | Analog Input |  | P39 |  | E 5003 2 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 175 | °C | FF AI | [30 empty] | L | 5310 |  | LI-5310
S-02115 | L_I-5321 | 227.01 | Analog Input |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | FF AI | [30 empty] | L | 5321 |  | LIC-5321
S-02115 | L_I-5396 | 227.01 | Analog Input |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | FF AI | [30 empty] | L | 5396 |  | LI-5396
S-02115 | L_I-5413 | 227.01 | Analog Input |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | FF AI | [30 empty] | L | 5413 |  | LI-5413
S-02115 | L_I-5446 | 227.01 | Analog Input |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | L | 5446 |  | LI-5446
S-02115 | L_I/A-5501 | 227.01 | Analog Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 4-20 mA | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | L_I/B-5501 | 227.01 | Analog Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 4-20 mA | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | L_I/C-5501 | 227.01 | Analog Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 4-20 mA | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | L_I-5511 | 227.01 | Analog Input |  | U24 |  | TK 5050 | [8 empty] | °C | FF AI | [30 empty] | L | 5511 |  | LI-5511
S-02115 | L_I-6021 | 227.01 | Analog Input |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | FF AI | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | L_I-6033/1 | 227.01 | Analog Input |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | FF AI | [30 empty] | L | 6033 | 1 | LI-6033/1
S-02115 | L_I-6033/2 | 227.01 | Analog Input |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | FF AI | [30 empty] | L | 6033 | 2 | LI-6033/2
S-02115 | L_I-6034/1 | 227.01 | Analog Input |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | FF AI | [30 empty] | L | 6034 | 1 | LI-6034/1
S-02115 | L_I-6034/2 | 227.01 | Analog Input |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | FF AI | [30 empty] | L | 6034 | 2 | LI-6034/2
S-02115 | L_I/A-6051 | 227.01 | Analog Input |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 4-20 mA | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | L_I/B-6051 | 227.01 | Analog Input |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 4-20 mA | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | L_I/C-6051 | 227.01 | Analog Input |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 4-20 mA | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | L_I-6082 | 227.01 | Analog Input |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | FF AI | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | L_I-6083 | 227.01 | Analog Input |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | FF AI | [30 empty] | L | 6083 |  | LI-6083
S-02115 | L_I-7001 | 227.01 | Analog Input |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | L | 7001 |  | LI-7001
S-02115 | L_I-7002 | 227.01 | Analog Input |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | L | 7002 |  | LI-7002
S-02115 | L_I-7060 | 227.01 | Analog Input |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | L | 7060 |  | LI-7060
S-02115 | L_I-7061 | 227.01 | Analog Input |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | L | 7061 |  | LI-7061
S-02115 | L_I/A-7091 | 227.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 4-20 mA | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | L_I/B-7091 | 227.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 4-20 mA | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | L_I/C-7091 | 227.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 4-20 mA | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | L_I-7101 | 227.01 | Analog Input |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | FF AI | [30 empty] | L | 7101 |  | LI-7101
S-02115 | L_I-7102 | 227.01 | Analog Input |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | FF AI | [30 empty] | L | 7102 |  | LI-7102
S-02115 | L_I-7162 | 227.01 | Analog Input |  | U12 |  | TK 7050 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | L | 7162 |  | LI-7162
S-02115 | L_I-7192 | 227.01 | Analog Input |  | U13 |  | TK 7060 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | L | 7192 |  | LI-7192
S-02115 | L_I-7212 | 227.01 | Analog Input |  | U14 |  | TK 7070 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | L | 7212 |  | LI-7212
S-02115 | L_I-7251 | 227.01 | Analog Input |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | FF AI | [30 empty] | L | 7251 |  | LIC-7251
S-02115 | P_I-1001 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | P | 1001 |  | PI-1001
S-02115 | P_I-1006 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | P | 1006 |  | PIC-1006
S-02115 | P_I-1011 | 227.01 | Analog Input |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | PD_I-1032 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | FF AI | [30 empty] | P | 1032 |  | PDI-1032
S-02115 | P_I-1045 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | FF AI | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | P_I-2001 | 227.01 | Analog Input |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | P | 2001 |  | PI-2001
S-02115 | PD_I-2004 | 227.01 | Analog Input |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | P | 2004 |  | PDI-2004
S-02115 | P_I-2015 | 227.01 | Analog Input |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | FF AI | [30 empty] | P | 2015 |  | PIC-2015
S-02115 | PD_I-2032 | 227.01 | Analog Input |  | P03 |  | 4"-HPS-70-103-F34-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | P | 2032 |  | PDI-2032
S-02115 | P_I-2035 | 227.01 | Analog Input |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | P | 2035 |  | PI-2035
S-02115 | P_I-2046 | 227.01 | Analog Input |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | FF AI | [30 empty] | P | 2046 |  | PI-2046
S-02115 | P_I-2047 | 227.01 | Analog Input |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | FF AI | [30 empty] | P | 2047 |  | PI-2047
S-02115 | PD_I-2051 | 227.01 | Analog Input |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | FF AI | [30 empty] | P | 2051 |  | PDI-2051
S-02115 | P_I-2061 | 227.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AI | [30 empty] | P | 2061 |  | PI-2061
S-02115 | P_I-2073 | 227.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AI | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | P_I-2077 | 227.01 | Analog Input |  | P09 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | FF AI | [30 empty] | P | 2077 |  | PI-2077
S-02115 | P_I-2099 | 227.01 | Analog Input |  | P10 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | FF AI | [30 empty] | P | 2099 |  | PI-2099
S-02115 | P_I-2111 | 227.01 | Analog Input |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | FF AI | [30 empty] | P | 2111 |  | PI-2111
S-02115 | P_I-2112 | 227.01 | Analog Input |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | FF AI | [30 empty] | P | 2112 |  | PI-2112
S-02115 | P_I-2150 | 227.01 | Analog Input |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF AI | [30 empty] | P | 2150 |  | PI-2150
S-02115 | P_I-2156 | 227.01 | Analog Input |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | FF AI | [30 empty] | P | 2156 |  | PI-2156
S-02115 | P_I/A-2163 | 227.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 4-20 mA | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | P_I/B-2163 | 227.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 4-20 mA | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | P_I/C-2163 | 227.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 4-20 mA | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | P_I/A-2224 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | P_I/B-2224 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | P_I/C-2224 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PD_I-2252 | 227.01 | Analog Input |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | FF AI | [30 empty] | P | 2252 |  | PDI-2252
S-02115 | P_I-2268 | 227.01 | Analog Input |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | FF AI | [30 empty] | P | 2268 |  | PI-2268
S-02115 | P_I-2282 | 227.01 | Analog Input |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | FF AI | [30 empty] | P | 2282 |  | PI-2282
S-02115 | PD_I-2283 | 227.01 | Analog Input |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | FF AI | [30 empty] | P | 2283 |  | PDI-2283
S-02115 | P_I-2307 | 227.01 | Analog Input |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | FF AI | [30 empty] | P | 2307 |  | PI-2307
S-02115 | PD_I-2321 | 227.01 | Analog Input |  | P16A |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | FF AI | [30 empty] | P | 2321 |  | PDI-2321
S-02115 | P_I-2322 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | FF AI | [30 empty] | P | 2322 |  | PI-2322
S-02115 | PD_I-2323 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | FF AI | [30 empty] | P | 2323 |  | PDI-2323
S-02115 | P_I-2324 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | FF AI | [30 empty] | P | 2324 |  | PI-2324
S-02115 | P_I-2352 | 227.01 | Analog Input |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | FF AI | [30 empty] | P | 2352 |  | PI-2352
S-02115 | P_I-2361 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF AI | [30 empty] | P | 2361 |  | PIC-2361
S-02115 | P_I-2363 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF AI | [30 empty] | P | 2363 |  | PIC-2363
S-02115 | P_I/A-2372 | 227.01 | Analog Input |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | P | 2372 |  | PI-2372
S-02115 | P_I/B-2372 | 227.01 | Analog Input |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | P | 2372 |  | PI-2372
S-02115 | P_I/C-2372 | 227.01 | Analog Input |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | P | 2372 |  | PI-2372
S-02115 | P_I-2406 | 227.01 | Analog Input |  | P19 |  | 34"-RFG-20-120-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF AI | [30 empty] | P | 2406 |  | PIC-2406
S-02115 | P_I-2416 | 227.01 | Analog Input |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | FF AI | [30 empty] | P | 2416 |  | PI-2416
S-02115 | PD_I-2417 | 227.01 | Analog Input |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF AI | [30 empty] | P | 2417 |  | PDIC-2417
S-02115 | P_I-2453 | 227.01 | Analog Input |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | FF AI | [30 empty] | P | 2453 |  | PI-2453
S-02115 | P_I-2455 | 227.01 | Analog Input |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | FF AI | [30 empty] | P | 2455 |  | PI-2455
S-02115 | P_I-2481 | 227.01 | Analog Input |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | P | 2481 |  | PIC-2481
S-02115 | P_I-2493 | 227.01 | Analog Input |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | FF AI | [30 empty] | P | 2493 |  | PI-2493
S-02115 | P_I-2536 | 227.01 | Analog Input |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF AI | [30 empty] | P | 2536 |  | PIC-2536
S-02115 | P_I-2540 | 227.01 | Analog Input |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | P | 2540 |  | PI-2540
S-02115 | P_I/A-2554 | 227.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | P_I/B-2554 | 227.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | P_I/C-2554 | 227.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PD_I-2575 | 227.01 | Analog Input |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | FF AI | [30 empty] | P | 2575 |  | PDIC-2575
S-02115 | P_I-2579 | 227.01 | Analog Input |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | FF AI | [30 empty] | P | 2579 |  | PI-2579
S-02115 | P_I-2601 | 227.01 | Analog Input |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | P | 2601 |  | PI-2601
S-02115 | P_I-2603 | 227.01 | Analog Input |  | U17 |  | 3"-HG-20-109-D24-N |  |  | 29 | 25 | bar g |  | 40 | 100 | °C | FF AI | [30 empty] | P | 2603 |  | PIC-2603
S-02115 | P_I-2607 | 227.01 | Analog Input |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | P | 2607 |  | PI-2607
S-02115 | P_I-2608 | 227.01 | Analog Input |  | U17 |  | 3"-HG-20-108-F24-N |  |  | 55 | 50.4 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | P | 2608 |  | PIC-2608
S-02115 | P_I-3007 | 227.01 | Analog Input |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | P | 3007 |  | PIC-3007
S-02115 | P_I-3023 | 227.01 | Analog Input |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | FF AI | [30 empty] | P | 3023 |  | PI-3023
S-02115 | PD_I-3024 | 227.01 | Analog Input |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | FF AI | [30 empty] | P | 3024 |  | PDI-3024
S-02115 | P_I/A-3042 | 227.01 | Analog Input |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | P_I/B-3042 | 227.01 | Analog Input |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | P_I/C-3042 | 227.01 | Analog Input |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | P_I-3071 | 227.01 | Analog Input |  | P24 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | P | 3071 |  | PI-3071
S-02115 | P_I-3075 | 227.01 | Analog Input |  | P24 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | P | 3075 |  | PI-3075
S-02115 | P_I-3079 | 227.01 | Analog Input |  | P24 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | P | 3079 |  | PI-3079
S-02115 | PD_I-3112 | 227.01 | Analog Input |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | P | 3112 |  | PDI-3112
S-02115 | PD_I-3115 | 227.01 | Analog Input |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | P | 3115 |  | PDI-3115
S-02115 | PD_I-3117 | 227.01 | Analog Input |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | P | 3117 |  | PDI-3117
S-02115 | P_I-3166 | 227.01 | Analog Input |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | P | 3166 |  | PIC-3166
S-02115 | P_I-3194 | 227.01 | Analog Input |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | FF AI | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | P_I-5004 | 227.01 | Analog Input |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | FF AI | [30 empty] | P | 5004 |  | PI-5004
S-02115 | P_I-5022 | 227.01 | Analog Input |  | P29 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | FF AI | [30 empty] | P | 5022 |  | PI-5022
S-02115 | P_I-5047 | 227.01 | Analog Input |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | FF AI | [30 empty] | P | 5047 |  | PI-5047
S-02115 | P_I-5049 | 227.01 | Analog Input |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | P | 5049 |  | PI-5049
S-02115 | P_I-5051 | 227.01 | Analog Input |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | P | 5051 |  | PI-5051
S-02115 | P_I-5069 | 227.01 | Analog Input |  | P31 |  | 14"-LPS-50-103-D24-H |  |  | 9.5 | 2.4 | bar g |  | 187 | 340 | °C | FF AI | [30 empty] | P | 5069 |  | PIC-5069
S-02115 | P_I-5083 | 227.01 | Analog Input |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | FF AI | [30 empty] | P | 5083 |  | PI-5083
S-02115 | P_I-5091 | 227.01 | Analog Input |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | P_I-5093 | 227.01 | Analog Input |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | P | 5093 |  | PI-5093
S-02115 | P_I-5111 | 227.01 | Analog Input |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | P | 5111 |  | PI-5111
S-02115 | P_I-5139 | 227.01 | Analog Input |  | P33 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | FF AI | [30 empty] | P | 5139 |  | PI-5139
S-02115 | P_I-5166 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | P | 5166 |  | PI-5166
S-02115 | P_I-5168 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | P | 5168 |  | PI-5168
S-02115 | P_I-5170 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | P | 5170 |  | PI-5170
S-02115 | P_I-5172 | 227.01 | Analog Input |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | FF AI | [30 empty] | P | 5172 |  | PI-5172
S-02115 | P_I-5176 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | P | 5176 |  | PI-5176
S-02115 | P_I/A-5207 | 227.01 | Analog Input |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | P_I/B-5207 | 227.01 | Analog Input |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | P_I/C-5207 | 227.01 | Analog Input |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | P_I-5219 | 227.01 | Analog Input |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | P | 5219 |  | PI-5219
S-02115 | P_I-5240 | 227.01 | Analog Input |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | FF AI | [30 empty] | P | 5240 |  | PI-5240
S-02115 | P_I-5252 | 227.01 | Analog Input |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | FF AI | [30 empty] | P | 5252 |  | PI-5252
S-02115 | P_I-5254 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | P | 5254 |  | PI-5254
S-02115 | P_I-5256 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | P | 5256 |  | PI-5256
S-02115 | P_I-5258 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | P | 5258 |  | PI-5258
S-02115 | P_I-5260 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | P | 5260 |  | PI-5260
S-02115 | P_I-5307 | 227.01 | Analog Input |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | FF AI | [30 empty] | P | 5307 |  | PI-5307
S-02115 | P_I-5335 | 227.01 | Analog Input |  | P40 |  | 6"-PMP-50-140-D24-P |  |  | 19 | 3.6 | bar g |  | 101 | 165 | °C | FF AI | [30 empty] | P | 5335 |  | PI-5335
S-02115 | P_I-5367 | 227.01 | Analog Input |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | FF AI | [30 empty] | P | 5367 |  | PI-5367
S-02115 | P_I-5369 | 227.01 | Analog Input |  | P41 |  | 2"-PMW-50-124-B24-P |  |  | 7.5 | 4.5 | bar g |  | 149 | 175 | °C | FF AI | [30 empty] | P | 5369 |  | PI-5369
S-02115 | PD_I-5385 | 227.01 | Analog Input |  | P42 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | P | 5385 |  | PDI-5385
S-02115 | P_I-5387 | 227.01 | Analog Input |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | P | 5387 |  | PI-5387
S-02115 | P_I-5398 | 227.01 | Analog Input |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | FF AI | [30 empty] | P | 5398 |  | PI-5398
S-02115 | P_I-5415 | 227.01 | Analog Input |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | FF AI | [30 empty] | P | 5415 |  | PI-5415
S-02115 | P_I-5421 | 227.01 | Analog Input |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | P | 5421 |  | PI-5421
S-02115 | P_I-5448 | 227.01 | Analog Input |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | P | 5448 |  | PI-5448
S-02115 | P_I-6010 | 227.01 | Analog Input |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | FF AI | [30 empty] | P | 6010 |  | PI-6010
S-02115 | P_I-6025 | 227.01 | Analog Input |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | FF AI | [30 empty] | P | 6025 |  | PIC-6025
S-02115 | PD_I-6026 | 227.01 | Analog Input |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 280 | °C | FF AI | [30 empty] | P | 6026 |  | PDI-6026
S-02115 | PD_I-6028 | 227.01 | Analog Input |  | P06 |  | 3"-PRC-20-107-G40-H |  |  | 71 | 45 | bar g |  | 115 | 180 | °C | FF AI | [30 empty] | P | 6028 |  | PDI-6028
S-02115 | P_I-6031 | 227.01 | Analog Input |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | FF AI | [30 empty] | P | 6031 |  | PI-6031
S-02115 | P_I-6054 | 227.01 | Analog Input |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | FF AI | [30 empty] | P | 6054 |  | PI-6054
S-02115 | P_I-6088 | 227.01 | Analog Input |  | P08 |  | 4"-BD-60-119-B40-P |  |  | 9 | 3 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | P | 6088 |  | PI-6088
S-02115 | P_I-7001 | 227.01 | Analog Input |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | FF AI | [30 empty] | P | 7001 |  | PIC-7001
S-02115 | PZ_I/A-7002 | 227.01 | Analog Input |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PZ_I/B-7002 | 227.01 | Analog Input |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PZ_I/C-7002 | 227.01 | Analog Input |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | P_I-7002 | 227.01 | Analog Input |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | P_I-7003 | 227.01 | Analog Input |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | P | 7003 |  | PIC-7003
S-02115 | P_I-7004 | 227.01 | Analog Input |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | P_I-7021 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | FF AI | [30 empty] | P | 7021 |  | PI-7021
S-02115 | P_I-7025 | 227.01 | Analog Input |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | P_I-7028 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | FF AI | [30 empty] | P | 7028 |  | PIC-7028
S-02115 | P_I-7031 | 227.01 | Analog Input |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AI | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | P_I-7034 | 227.01 | Analog Input |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AI | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | P_I-7051 | 227.01 | Analog Input |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | FF AI | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | P_I-7055 | 227.01 | Analog Input |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | FF AI | [30 empty] | P | 7055 |  | PIC-7055
S-02115 | P_I-7056 | 227.01 | Analog Input |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | FF AI | [30 empty] | P | 7056 |  | PIC-7056
S-02115 | P_I-7094 | 227.01 | Analog Input |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | FF AI | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | P_I-7127 | 227.01 | Analog Input |  | U10 |  | 12"-BFW-70-140-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF AI | [30 empty] | P | 7127 |  | PI-7127
S-02115 | P_I-7141 | 227.01 | Analog Input |  | U11 |  | 8"-BFW-70-164-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | FF AI | [30 empty] | P | 7141 |  | PIC-7141
S-02115 | P_I-8001 | 227.01 | Analog Input |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | FF AI | [30 empty] | P | 8001 |  | PI-8001
S-02115 | S_I-2118 | 227.01 | Analog Input |  | P11 | [10 empty] | °C | FF AI | [30 empty] | S | 2118 |  | SI-2118
S-02115 | S_I-2168 | 227.01 | Analog Input |  | P12 | [10 empty] | °C | FF AI | [30 empty] | S | 2168 |  | SI-2168
S-02115 | T_I-1001 | 227.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | T | 1001 |  | TI-1001
S-02115 | T_I-1010 | 227.01 | Analog Input |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | T | 1010 |  | TI-1010
S-02115 | T_I-1012 | 227.01 | Analog Input |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | T | 1012 |  | TI-1012
S-02115 | T_I-1034 | 227.01 | Analog Input |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | FF AI | [30 empty] | T | 1034 |  | TI-1034
S-02115 | T_I-1035 | 227.01 | Analog Input |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | FF AI | [30 empty] | T | 1035 |  | TI-1035
S-02115 | T_I-1037 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | FF AI | [30 empty] | T | 1037 |  | TI-1037
S-02115 | T_I-1041 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | FF AI | [30 empty] | T | 1041 |  | TI-1041
S-02115 | T_I-1042 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | FF AI | [30 empty] | T | 1042 |  | TI-1042
S-02115 | T_I-1045 | 227.01 | Analog Input |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | FF AI | [30 empty] | T | 1045 |  | TI-1045
S-02115 | T_I-1047 | 227.01 | Analog Input |  | P04 |  | 8"-FLG-10-113-B24-P |  |  | 5 |  | bar g |  |  | 410 | °C | FF AI | [30 empty] | T | 1047 |  | TI-1047
S-02115 | T_I-2001 | 227.01 | Analog Input |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | T | 2001 |  | TI-2001
S-02115 | T_I-2003 | 227.01 | Analog Input |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | FF AI | [30 empty] | T | 2003 |  | TI-2003
S-02115 | T_I-2039 | 227.01 | Analog Input |  | P03 |  | 4"-HPS-20-109-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | T | 2039 |  | TI-2039
S-02115 | T_I-2044 | 227.01 | Analog Input |  | P03 |  | 6"-VA-20-104-F70-P |  |  | 45 |  | bar g |  |  | 255 | °C | FF AI | [30 empty] | T | 2044 |  | TI-2044
S-02115 | T_I-2046 | 227.01 | Analog Input |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | FF AI | [30 empty] | T | 2046 |  | TI-2046
S-02115 | T_I-2050 | 227.01 | Analog Input |  | P03 |  | 2"-VA-20-101-F70-P |  |  | 4.5 |  | bar g |  |  | 255 | °C | FF AI | [30 empty] | T | 2050 |  | TI-2050
S-02115 | T_I-2061 | 227.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AI | [30 empty] | T | 2061 |  | TI-2061
S-02115 | T_I-2074 | 227.01 | Analog Input |  | P09 |  | 24"-FLG-20-107-B24-P |  |  | 5 |  | bar g |  |  | 290 | °C | FF AI | [30 empty] | T | 2074 |  | TI-2074
S-02115 | T_I-2111 | 227.01 | Analog Input |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | FF AI | [30 empty] | T | 2111 |  | TI-2111
S-02115 | T_I-2112 | 227.01 | Analog Input |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | FF AI | [30 empty] | T | 2112 |  | TI-2112
S-02115 | T_I-2148 | 227.01 | Analog Input |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | FF AI | [30 empty] | T | 2148 |  | TI-2148
S-02115 | T_I-2149 | 227.01 | Analog Input |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | FF AI | [30 empty] | T | 2149 |  | TI-2149
S-02115 | T_I-2150 | 227.01 | Analog Input |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF AI | [30 empty] | T | 2150 |  | TI-2150
S-02115 | T_I-2151 | 227.01 | Analog Input |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | T | 2151 |  | TI-2151
S-02115 | T_I-2154 | 227.01 | Analog Input |  | P12 |  | WHS | [6 empty] | 236.3 |  | °C | FF AI | [30 empty] | T | 2154 |  | TI-2154
S-02115 | T_I-2155 | 227.01 | Analog Input |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | FF AI | [30 empty] | T | 2155 |  | TI-2155
S-02115 | T_I-2161 | 227.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | FF AI | [30 empty] | T | 2161 |  | TI-2161
S-02115 | T_I-2162 | 227.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | FF AI | [30 empty] | T | 2162 |  | TI-2162
S-02115 | T_I-2220 | 227.01 | Analog Input |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | FF AI | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | T_I-2226 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 1093 |  | °C | FF AI | [30 empty] | T | 2226 |  | TI-2226
S-02115 | T_I-2227 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 794 |  | °C | FF AI | [30 empty] | T | 2227 |  | TI-2227
S-02115 | T_I-2228 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | -0.02 | bar g |  | 439 |  | °C | FF AI | [30 empty] | T | 2228 |  | TI-2228
S-02115 | T_I-2229 | 227.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0.05 | bar g |  | 350 |  | °C | FF AI | [30 empty] | T | 2229 |  | TI-2229
S-02115 | T_I-2232 | 227.01 | Analog Input |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | FF AI | [30 empty] | T | 2232 |  | TIC-2232
S-02115 | T_I-2234 | 227.01 | Analog Input |  | P13 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | FF AI | [30 empty] | T | 2234 |  | TI-2234
S-02115 | T_I-2253 | 227.01 | Analog Input |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | FF AI | [30 empty] | T | 2253 |  | TIC-2253
S-02115 | T_I-2254 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2254 |  | TI-2254
S-02115 | T_I-2255 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2255 |  | TI-2255
S-02115 | T_I-2256 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2256 |  | TI-2256
S-02115 | T_I-2257 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2257 |  | TI-2257
S-02115 | T_I-2258 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2258 |  | TI-2258
S-02115 | T_I-2259 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2259 |  | TI-2259
S-02115 | T_I-2260 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2260 |  | TI-2260
S-02115 | T_I-2261 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2261 |  | TI-2261
S-02115 | T_I-2262 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2262 |  | TI-2262
S-02115 | T_I-2263 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2263 |  | TI-2263
S-02115 | T_I-2264 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2264 |  | TI-2264
S-02115 | T_I-2265 | 227.01 | Analog Input |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | FF AI | [30 empty] | T | 2265 |  | TI-2265
S-02115 | T_I-2268 | 227.01 | Analog Input |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | FF AI | [30 empty] | T | 2268 |  | TI-2268
S-02115 | T_I-2285 | 227.01 | Analog Input |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | FF AI | [30 empty] | T | 2285 |  | TI-2285
S-02115 | T_I-2295 | 227.01 | Analog Input |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | FF AI | [30 empty] | T | 2295 |  | TI-2295
S-02115 | T_I-2297 | 227.01 | Analog Input |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | FF AI | [30 empty] | T | 2297 |  | TI-2297
S-02115 | T_I-2303 | 227.01 | Analog Input |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | FF AI | [30 empty] | T | 2303 |  | TI-2303
S-02115 | T_I-2304 | 227.01 | Analog Input |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | FF AI | [30 empty] | T | 2304 |  | TI-2304
S-02115 | T_I-2326 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | T | 2326 |  | TI-2326
S-02115 | T_I-2327 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | T | 2327 |  | TI-2327
S-02115 | T_I-2328 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | T | 2328 |  | TI-2328
S-02115 | T_I-2330 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | T | 2330 |  | TI-2330
S-02115 | T_I-2331 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | T | 2331 |  | TI-2331
S-02115 | T_I-2332 | 227.01 | Analog Input |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | FF AI | [30 empty] | T | 2332 |  | TI-2332
S-02115 | T_I/A-2335 | 227.01 | Analog Input |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | T_I/B-2335 | 227.01 | Analog Input |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | T_I/C-2335 | 227.01 | Analog Input |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | T_I/A-2336 | 227.01 | Analog Input |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | T_I/B-2336 | 227.01 | Analog Input |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | T_I/C-2336 | 227.01 | Analog Input |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | T_I-2351 | 227.01 | Analog Input |  | P17 |  | 24"-RFG-20-110-D34-H |  |  | 30 | 26.3 | bar g |  | 360 | 390 | °C | FF AI | [30 empty] | T | 2351 |  | TI-2351
S-02115 | T_I-2352 | 227.01 | Analog Input |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | FF AI | [30 empty] | T | 2352 |  | TI-2352
S-02115 | T_I-2353 | 227.01 | Analog Input |  | P17 |  | 24"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | FF AI | [30 empty] | T | 2353 |  | TI-2353
S-02115 | T_I-2354 | 227.01 | Analog Input |  | P17 |  | 42"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | FF AI | [30 empty] | T | 2354 |  | TI-2354
S-02115 | T_I-2355 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF AI | [30 empty] | T | 2355 |  | TI-2355
S-02115 | T_I-2356 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-117-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF AI | [30 empty] | T | 2356 |  | TI-2356
S-02115 | T_I-2359 | 227.01 | Analog Input |  | P17 |  | 20"-HHPS-20-103-H24-H |  |  | 112 | 101 | bar g |  | 338 | 370 | °C | FF AI | [30 empty] | T | 2359 |  | TI-2359
S-02115 | T_I/A-2360 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 4-20 mA | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | T_I/B-2360 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 4-20 mA | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | T_I/C-2360 | 227.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 4-20 mA | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | T_I-2371 | 227.01 | Analog Input |  | P18 |  | 12"-BFW-20-102-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | FF AI | [30 empty] | T | 2371 |  | TI-2371
S-02115 | T_I-2402 | 227.01 | Analog Input |  | P19 |  | 34"-RFG-20-117-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF AI | [30 empty] | T | 2402 |  | TI-2402
S-02115 | T_I-2407 | 227.01 | Analog Input |  | P19 |  | 16"-FLG-20-120-B40-P |  |  | 5 |  | bar g |  |  | 200 | °C | FF AI | [30 empty] | T | 2407 |  | TI-2407
S-02115 | T_I-2418 | 227.01 | Analog Input |  | P19 |  | 12"-BFW-20-104-G24 |  |  | 113 | 104 | bar g |  | 122 | 160 | °C | FF AI | [30 empty] | T | 2418 |  | TI-2418
S-02115 | T_I-2421 | 227.01 | Analog Input |  | P19 |  | 34"-RFG-20-122-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | FF AI | [30 empty] | T | 2421 |  | TI-2421
S-02115 | T_I-2444 | 227.01 | Analog Input |  | P20 |  | 34"-RFG-20-124-D40-P |  |  | 29 | 24.4 | bar g |  | 132 | 200 | °C | FF AI | [30 empty] | T | 2444 |  | TI-2444
S-02115 | T_I-2455 | 227.01 | Analog Input |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | FF AI | [30 empty] | T | 2455 |  | TI-2455
S-02115 | T_I-2457 | 227.01 | Analog Input |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | FF AI | [30 empty] | T | 2457 |  | TIC-2457
S-02115 | T_I-2472 | 227.01 | Analog Input |  | P21 |  | 34"-RFG-20-125-D40-P |  |  | 29 | 24.2 | bar g |  | 65 | 120 | °C | FF AI | [30 empty] | T | 2472 |  | TI-2472
S-02115 | T_I-2476 | 227.01 | Analog Input |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 2476 |  | TI-2476
S-02115 | T_I-2484 | 227.01 | Analog Input |  | P21 |  | 12"-FLG-20-123-B24-N |  |  | 5 |  | bar g |  |  | 100 | °C | FF AI | [30 empty] | T | 2484 |  | TI-2484
S-02115 | T_I-2493 | 227.01 | Analog Input |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 2493 |  | TI-2493
S-02115 | T_I-2536 | 227.01 | Analog Input |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF AI | [30 empty] | T | 2536 |  | TI-2536
S-02115 | T_I-2540 | 227.01 | Analog Input |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | FF AI | [30 empty] | T | 2540 |  | TI-2540
S-02115 | T_I-2553 | 227.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | FF AI | [30 empty] | T | 2553 |  | TI-2553
S-02115 | T_I-2572 | 227.01 | Analog Input |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | FF AI | [30 empty] | T | 2572 |  | TI-2572
S-02115 | T_I-2579 | 227.01 | Analog Input |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | FF AI | [30 empty] | T | 2579 |  | TI-2579
S-02115 | T_I-2601 | 227.01 | Analog Input |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | FF AI | [30 empty] | T | 2601 |  | TI-2601
S-02115 | T_I-2607 | 227.01 | Analog Input |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 2607 |  | TI-2607
S-02115 | T_I-3045 | 227.01 | Analog Input |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | FF AI | [30 empty] | T | 3045 |  | TI-3045
S-02115 | T_I-3073 | 227.01 | Analog Input |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | FF AI | [30 empty] | T | 3073 |  | TI-3073
S-02115 | T_I-3077 | 227.01 | Analog Input |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | FF AI | [30 empty] | T | 3077 |  | TI-3077
S-02115 | T_I-3081 | 227.01 | Analog Input |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | FF AI | [30 empty] | T | 3081 |  | TI-3081
S-02115 | T_I-3084 | 227.01 | Analog Input |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | FF AI | [30 empty] | T | 3084 |  | TI-3084
S-02115 | T_I-3111 | 227.01 | Analog Input |  | P25 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | FF AI | [30 empty] | T | 3111 |  | TI-3111
S-02115 | T_I-3113 | 227.01 | Analog Input |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | T | 3113 |  | TIC-3113
S-02115 | T_I-3116 | 227.01 | Analog Input |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | T | 3116 |  | TIC-3116
S-02115 | T_I-3118 | 227.01 | Analog Input |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AI | [30 empty] | T | 3118 |  | TIC-3118
S-02115 | T_I-3119 | 227.01 | Analog Input |  | P25 |  | 20"-SG-30-110-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | FF AI | [30 empty] | T | 3119 |  | TI-3119
S-02115 | T_I-3120 | 227.01 | Analog Input |  | P25 |  | 20"-SG-30-109-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | FF AI | [30 empty] | T | 3120 |  | TI-3120
S-02115 | T_I-3121 | 227.01 | Analog Input |  | P25 |  | 20"-SG-30-121-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | FF AI | [30 empty] | T | 3121 |  | TI-3121
S-02115 | T_I-3142 | 227.01 | Analog Input |  | P26 |  | 24"-SG-30-122-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | FF AI | [30 empty] | T | 3142 |  | TI-3142
S-02115 | T_I-3145 | 227.01 | Analog Input |  | P26 |  | 24"-SG-30-123-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | FF AI | [30 empty] | T | 3145 |  | TI-3145
S-02115 | T_I-3148 | 227.01 | Analog Input |  | P26 |  | 24"-SG-30-124-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | FF AI | [30 empty] | T | 3148 |  | TI-3148
S-02115 | T_I-3164 | 227.01 | Analog Input |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 3164 |  | TI-3164
S-02115 | T_I-3194 | 227.01 | Analog Input |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 3194 |  | TI-3194
S-02115 | T_I-3198 | 227.01 | Analog Input |  | P28 |  | 10"-PMC-30-111-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 3198 |  | TI-3198
S-02115 | T_I-5020 | 227.01 | Analog Input |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | FF AI | [30 empty] | T | 5020 |  | TI-5020
S-02115 | T_I-5039 | 227.01 | Analog Input |  | P30 |  | RFG-50 |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | FF AI | [30 empty] | T | 5039 |  | TI-5039
S-02115 | T_I-5040 | 227.01 | Analog Input |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | FF AI | [30 empty] | T | 5040 |  | TI-5040
S-02115 | T_I-5045 | 227.01 | Analog Input |  | P30 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | FF AI | [30 empty] | T | 5045 |  | TI-5045
S-02115 | T_I-5052 | 227.01 | Analog Input |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | T | 5052 |  | TI-5052
S-02115 | T_I-5053 | 227.01 | Analog Input |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | T | 5053 |  | TI-5053
S-02115 | T_I-5054 | 227.01 | Analog Input |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | FF AI | [30 empty] | T | 5054 |  | TI-5054
S-02115 | T_I-5056 | 227.01 | Analog Input |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | FF AI | [30 empty] | T | 5056 |  | TI-5056
S-02115 | T_I-5057 | 227.01 | Analog Input |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | FF AI | [30 empty] | T | 5057 |  | TI-5057
S-02115 | T_I-5059 | 227.01 | Analog Input |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AI | [30 empty] | T | 5059 |  | TI-5059
S-02115 | T_I-5060 | 227.01 | Analog Input |  | P30 |  | 20"-PMC-50-110-B24-H |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | FF AI | [30 empty] | T | 5060 |  | TI-5060
S-02115 | T_I-5062 | 227.01 | Analog Input |  | P30 |  | 34"-PMV-50-120-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | FF AI | [30 empty] | T | 5062 |  | TI-5062
S-02115 | T_I-5064 | 227.01 | Analog Input |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | FF AI | [30 empty] | T | 5064 |  | TIC-5064
S-02115 | T_I-5067 | 227.01 | Analog Input |  | P30 |  | 34"-PMW-50-122-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | FF AI | [30 empty] | T | 5067 |  | TI-5067
S-02115 | T_I-5074 | 227.01 | Analog Input |  | P31 |  | 8"-LPC-50-110-D24-H |  |  | 18 | 2.4 | bar g |  | 138 | 190 | °C | FF AI | [30 empty] | T | 5074 |  | TI-5074
S-02115 | T_I-5097 | 227.01 | Analog Input |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | T | 5097 |  | TI-5097
S-02115 | T_I-5110 | 227.01 | Analog Input |  | P32 |  | 6"-FLG-50-131-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | T | 5110 |  | TI-5110
S-02115 | T_I-5111 | 227.01 | Analog Input |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | T | 5111 |  | TI-5111
S-02115 | T_I-5165 | 227.01 | Analog Input |  | P34 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | FF AI | [30 empty] | T | 5165 |  | TI-5165
S-02115 | T_I-5167 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | T | 5167 |  | TI-5167
S-02115 | T_I-5171 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | T | 5171 |  | TI-5171
S-02115 | T_I-5173 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | T | 5173 |  | TI-5173
S-02115 | T_I-5174 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | T | 5174 |  | TI-5174
S-02115 | T_I-5175 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | T | 5175 |  | TI-5175
S-02115 | T_I-5177 | 227.01 | Analog Input |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | FF AI | [30 empty] | T | 5177 |  | TI-5177
S-02115 | T_I-5180 | 227.01 | Analog Input |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | FF AI | [30 empty] | T | 5180 |  | TI-5180
S-02115 | T_I-5181 | 227.01 | Analog Input |  | P34 |  | 24"-PMC-50-140-B24-H |  |  | 5 | 0.7 | bar g |  | 83 | 160 | °C | FF AI | [30 empty] | T | 5181 |  | TI-5181
S-02115 | T_I-5184 | 227.01 | Analog Input |  | P34 |  | 16"-PMC-50-147-B24-H |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | FF AI | [30 empty] | T | 5184 |  | TI-5184
S-02115 | T_I-5208 | 227.01 | Analog Input |  | P36 |  | 24"-PMP-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | T | 5208 |  | TI-5208
S-02115 | T_I-5209 | 227.01 | Analog Input |  | P36 |  | 20"-PMP-50-102-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | T | 5209 |  | TI-5209
S-02115 | T_I-5219 | 227.01 | Analog Input |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | FF AI | [30 empty] | T | 5219 |  | TI-5219
S-02115 | T_I-5221 | 227.01 | Analog Input |  | P36 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | T | 5221 |  | TI-5221
S-02115 | T_I-5261 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5261 |  | TI-5261
S-02115 | T_I-5262 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5262 |  | TI-5262
S-02115 | T_I-5263 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5263 |  | TI-5263
S-02115 | T_I-5264 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5264 |  | TI-5264
S-02115 | T_I-5265 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5265 |  | TI-5265
S-02115 | T_I-5266 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5266 |  | TIC-5266
S-02115 | T_I-5267 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5267 |  | TIC-5267
S-02115 | T_I-5268 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5268 |  | TIC-5268
S-02115 | T_I-5269 | 227.01 | Analog Input |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | FF AI | [30 empty] | T | 5269 |  | TI-5269
S-02115 | T_I-5273 | 227.01 | Analog Input |  | P38 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | FF AI | [30 empty] | T | 5273 |  | TI-5273
S-02115 | T_I-5277 | 227.01 | Analog Input |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | FF AI | [30 empty] | T | 5277 |  | TIC-5277
S-02115 | T_I-5280 | 227.01 | Analog Input |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | FF AI | [30 empty] | T | 5280 |  | TI-5280
S-02115 | T_I-5307 | 227.01 | Analog Input |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | FF AI | [30 empty] | T | 5307 |  | TI-5307
S-02115 | T_I-5325 | 227.01 | Analog Input |  | P40 |  | 24"-PMP-50-130-B24-H |  |  | 7 | 2.6 | bar g |  | 101 | 165 | °C | FF AI | [30 empty] | T | 5325 |  | TI-5325
S-02115 | T_I-5335 | 227.01 | Analog Input |  | P40 |  | 6"-PMP-50-140-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | FF AI | [30 empty] | T | 5335 |  | TI-5335
S-02115 | T_I-5340 | 227.01 | Analog Input |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | T | 5340 |  | TI-5340
S-02115 | T_I-5369 | 227.01 | Analog Input |  | P41 |  | 2"-PMW-50-125-B24-P |  |  | 7.5 | 4.3 | bar g |  | 65 | 120 | °C | FF AI | [30 empty] | T | 5369 |  | TI-5369
S-02115 | T_I-5381 | 227.01 | Analog Input |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | T | 5381 |  | TI-5381
S-02115 | T_I-5441 | 227.01 | Analog Input |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | FF AI | [30 empty] | T | 5441 |  | TI-5441
S-02115 | T_I-5442 | 227.01 | Analog Input |  | P45 |  | 2"-LOS-50-113-B24-P |  |  | 7.5 | 2.5 | bar g |  | 115 | 175 | °C | FF AI | [30 empty] | T | 5442 |  | TI-5442
S-02115 | T_I-5443 | 227.01 | Analog Input |  | P45 |  | 2"-LOS-50-114-B24-N |  |  | 7.5 | 2 | bar g |  | 48 | 75 | °C | FF AI | [30 empty] | T | 5443 |  | TI-5443
S-02115 | T_I-6001 | 227.01 | Analog Input |  | P05 |  | 18"-MPC-60-101-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | FF AI | [30 empty] | T | 6001 |  | TI-6001
S-02115 | T_I-6024 | 227.01 | Analog Input |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 280 | °C | FF AI | [30 empty] | T | 6024 |  | TI-6024
S-02115 | T_I-6026 | 227.01 | Analog Input |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | FF AI | [30 empty] | T | 6026 |  | TI-6026
S-02115 | T_I-6031 | 227.01 | Analog Input |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | FF AI | [30 empty] | T | 6031 |  | TI-6031
S-02115 | T_I-6034 | 227.01 | Analog Input |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | FF AI | [30 empty] | T | 6034 |  | TI-6034
S-02115 | T_I-6054 | 227.01 | Analog Input |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | FF AI | [30 empty] | T | 6054 |  | TI-6054
S-02115 | T_I-6056 | 227.01 | Analog Input |  | P07 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | FF AI | [30 empty] | T | 6056 |  | TI-6056
S-02115 | T_I-6058 | 227.01 | Analog Input |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | FF AI | [30 empty] | T | 6058 |  | TI-6058
S-02115 | T_I-6081 | 227.01 | Analog Input |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | FF AI | [30 empty] | T | 6081 |  | TI-6081
S-02115 | T_I-6084 | 227.01 | Analog Input |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | FF AI | [30 empty] | T | 6084 |  | TI-6084
S-02115 | T_I-7001 | 227.01 | Analog Input |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | FF AI | [30 empty] | T | 7001 |  | TI-7001
S-02115 | T_I-7002 | 227.01 | Analog Input |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | T_I-7003 | 227.01 | Analog Input |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | T_I-7004 | 227.01 | Analog Input |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | T_I-7007 | 227.01 | Analog Input |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AI | [30 empty] | T | 7007 |  | TI-7007
S-02115 | T_I-7021 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | FF AI | [30 empty] | T | 7021 |  | TI-7021
S-02115 | T_I-7025 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | FF AI | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | T_I-7026 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | FF AI | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | T_I-7027 | 227.01 | Analog Input |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | FF AI | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | T_I-7031 | 227.01 | Analog Input |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AI | [30 empty] | T | 7031 |  | TI-7031
S-02115 | T_I-7032 | 227.01 | Analog Input |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | FF AI | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | T_I-7033 | 227.01 | Analog Input |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | FF AI | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | T_I-7052 | 227.01 | Analog Input |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | FF AI | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | T_I-7053 | 227.01 | Analog Input |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | FF AI | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | T_I-7056 | 227.01 | Analog Input |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | FF AI | [30 empty] | T | 7056 |  | TI-7056
S-02115 | T_I/A-7071 | 227.01 | Analog Input |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 4-20 mA | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | T_I/B-7071 | 227.01 | Analog Input |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 4-20 mA | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | T_I/C-7071 | 227.01 | Analog Input |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 4-20 mA | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | T_I-7097 | 227.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | FF AI | [30 empty] | T | 7097 |  | TI-7097
S-02115 | T_I-7098 | 227.01 | Analog Input |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 0 | bar g |  | 120 | 340 | °C | FF AI | [30 empty] | T | 7098 |  | TI-7098
S-02115 | T_I-8001 | 227.01 | Analog Input |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | FF AI | [30 empty] | T | 8001 |  | TI-8001
S-02115 | FZL_I-2007 | 227.02 | Digital Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | I-20 | On/Off | [29 empty] | F | 2007 |  | FIC-2007
S-02115 | FZL_I-2009 | 227.02 | Digital Input |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | I-20 | On/Off | [29 empty] | F | 2009 |  | FIC-2009
S-02115 | HZH_I-1003 | 227.02 | Digital Input |  | P01 | [10 empty] | °C |  | On/Off | [29 empty] | H | 1003 |  | HS-1003
S-02115 | HZL_I-1003 | 227.02 | Digital Input |  | P01 | [10 empty] | °C |  | On/Off | [29 empty] | H | 1003 |  | HS-1003
S-02115 | HZH_I-2003 | 227.02 | Digital Input |  | P02 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2003 |  | HS-2003
S-02115 | HZL_I-2003 | 227.02 | Digital Input |  | P02 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2003 |  | HS-2003
S-02115 | M_I-2124 | 227.02 | Digital Input |  | P11 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2124 |  | ML-2124
S-02115 | M_I-2159 | 227.02 | Digital Input |  | P12 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2159 |  | ML-2159
S-02115 | M_I-2410 | 227.02 | Digital Input |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2410 |  | ML-2410
S-02115 | M_I-2414 | 227.02 | Digital Input |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2414 |  | ML-2414
S-02115 | M_I-2447 | 227.02 | Digital Input |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2447 |  | ML-2447
S-02115 | M_I-2451 | 227.02 | Digital Input |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2451 |  | ML-2451
S-02115 | M_I-2471 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2471 |  | ML-2471
S-02115 | M_I-2487 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2487 |  | ML-2487
S-02115 | M_I-2491 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2491 |  | ML-2491
S-02115 | M_I-2577 | 227.02 | Digital Input |  | U02 | [10 empty] | °C |  | On/Off | [29 empty] | M | 2577 |  | ML-2577
S-02115 | M_I-3141 | 227.02 | Digital Input |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | M | 3141 |  | ML-3141
S-02115 | M_I-3144 | 227.02 | Digital Input |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | M | 3144 |  | ML-3144
S-02115 | M_I-3147 | 227.02 | Digital Input |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | M | 3147 |  | ML-3147
S-02115 | M_I-5013 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5013 |  | ML-5013
S-02115 | M_I-5017 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5017 |  | ML-5017
S-02115 | M_I-5077 | 227.02 | Digital Input |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5077 |  | ML-5077
S-02115 | M_I-5081 | 227.02 | Digital Input |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5081 |  | ML-5081
S-02115 | M_I-5092 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5092 |  | ML-5092
S-02115 | M_I-5101 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5101 |  | ML-5101
S-02115 | M_I-5105 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5105 |  | ML-5105
S-02115 | M_I-5133 | 227.02 | Digital Input |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5133 |  | ML-5133
S-02115 | M_I-5137 | 227.02 | Digital Input |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5137 |  | ML-5137
S-02115 | M_I-5201 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5201 |  | ML-5201
S-02115 | M_I-5212 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5212 |  | ML-5212
S-02115 | M_I-5216 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5216 |  | ML-5216
S-02115 | M_I-5231 | 227.02 | Digital Input |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5231 |  | ML-5231
S-02115 | M_I-5232 | 227.02 | Digital Input |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5232 |  | ML-5232
S-02115 | M_I-5233 | 227.02 | Digital Input |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5233 |  | ML-5233
S-02115 | M_I-5236 | 227.02 | Digital Input |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5236 |  | ML-5236
S-02115 | M_I-5237 | 227.02 | Digital Input |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5237 |  | ML-5237
S-02115 | M_I-5329 | 227.02 | Digital Input |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5329 |  | ML-5329
S-02115 | M_I-5333 | 227.02 | Digital Input |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5333 |  | ML-5333
S-02115 | M_I-5353 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5353 |  | ML-5353
S-02115 | M_I-5357 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5357 |  | ML-5357
S-02115 | M_I-5361 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5361 |  | ML-5361
S-02115 | M_I-5365 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5365 |  | ML-5365
S-02115 | M_I-5368 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5368 |  | ML-5368
S-02115 | M_I-5404 | 227.02 | Digital Input |  | P43 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5404 |  | ML-5404
S-02115 | M_I-5425 | 227.02 | Digital Input |  | P44 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5425 |  | ML-5425
S-02115 | M_I-5429 | 227.02 | Digital Input |  | P44 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5429 |  | ML-5429
S-02115 | M_I-5455 | 227.02 | Digital Input |  | P45 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5455 |  | ML-5455
S-02115 | M_I-5459 | 227.02 | Digital Input |  | P45 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5459 |  | ML-5459
S-02115 | M_I-5511 | 227.02 | Digital Input |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5511 |  | ML-5511
S-02115 | M_I-5512 | 227.02 | Digital Input |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5512 |  | ML-5512
S-02115 | M_I-5513 | 227.02 | Digital Input |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | M | 5513 |  | ML-5513
S-02115 | M_I-6004 | 227.02 | Digital Input |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | M | 6004 |  | ML-6004
S-02115 | M_I-6008 | 227.02 | Digital Input |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | M | 6008 |  | ML-6008
S-02115 | M_I-6062 | 227.02 | Digital Input |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | M | 6062 |  | ML-6062
S-02115 | M_I-6066 | 227.02 | Digital Input |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | M | 6066 |  | ML-6066
S-02115 | M_I-6081 | 227.02 | Digital Input |  | P08 | [10 empty] | °C |  | On/Off | [29 empty] | M | 6081 |  | ML-6081
S-02115 | M_I-6086 | 227.02 | Digital Input |  | P08 | [10 empty] | °C |  | On/Off | [29 empty] | M | 6086 |  | ML-6086
S-02115 | M_I-7005 | 227.02 | Digital Input |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7005 |  | ML-7005
S-02115 | M_I-7006 | 227.02 | Digital Input |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7006 |  | ML-7006
S-02115 | M_I-7101 | 227.02 | Digital Input |  | U22 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7101 |  | ML-7101
S-02115 | M_I-7103 | 227.02 | Digital Input |  | U22 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7103 |  | ML-7103
S-02115 | M_I-7122 | 227.02 | Digital Input |  | U10 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7122 |  | ML-7122
S-02115 | M_I-7161 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7161 |  | ML-7161
S-02115 | M_I-7163 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7163 |  | ML-7163
S-02115 | M_I-7166 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7166 |  | ML-7166
S-02115 | M_I-7169 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7169 |  | ML-7169
S-02115 | M_I-7172 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7172 |  | ML-7172
S-02115 | M_I-7191 | 227.02 | Digital Input |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7191 |  | ML-7191
S-02115 | M_I-7193 | 227.02 | Digital Input |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7193 |  | ML-7193
S-02115 | M_I-7196 | 227.02 | Digital Input |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7196 |  | ML-7196
S-02115 | M_I-7211 | 227.02 | Digital Input |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7211 |  | ML-7211
S-02115 | M_I-7213 | 227.02 | Digital Input |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7213 |  | ML-7213
S-02115 | M_I-7216 | 227.02 | Digital Input |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | M | 7216 |  | ML-7216
S-02115 | UZH_I-2125 | 227.02 | Digital Input |  | P11 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2125 |  | UY-2125
S-02115 | UZL_I-2125 | 227.02 | Digital Input |  | P11 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2125 |  | UY-2125
S-02115 | UZH_I-2233 | 227.02 | Digital Input |  | P13 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2233 |  | UY-2233
S-02115 | UZL_I-2233 | 227.02 | Digital Input |  | P13 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2233 |  | UY-2233
S-02115 | UZH_I-5021 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | U | 5021 |  | UY-5021
S-02115 | UZL_I-5021 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | U | 5021 |  | UY-5021
S-02115 | UZH_I-6035 | 227.02 | Digital Input |  | P06 | [10 empty] | °C |  | On/Off | [29 empty] | U | 6035 |  | UY-6035
S-02115 | UZL_I-6035 | 227.02 | Digital Input |  | P06 | [10 empty] | °C |  | On/Off | [29 empty] | U | 6035 |  | UY-6035
S-02115 | X_I-2124 | 227.02 | Digital Input |  | P11 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2124 |  | XA-2124
S-02115 | X_I-2159 | 227.02 | Digital Input |  | P12 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2159 |  | XA-2159
S-02115 | X_I-2410 | 227.02 | Digital Input |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2410 |  | XA-2410
S-02115 | X_I-2414 | 227.02 | Digital Input |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2414 |  | XA-2414
S-02115 | X_I-2447 | 227.02 | Digital Input |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2447 |  | XA-2447
S-02115 | X_I-2451 | 227.02 | Digital Input |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2451 |  | XA-2451
S-02115 | X_I-2487 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2487 |  | XA-2487
S-02115 | X_I-2491 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2491 |  | XA-2491
S-02115 | X_I-2577 | 227.02 | Digital Input |  | U02 | [10 empty] | °C |  | On/Off | [29 empty] | X | 2577 |  | XA-2577
S-02115 | X_I-3141 | 227.02 | Digital Input |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | X | 3141 |  | XA-3141
S-02115 | X_I-3144 | 227.02 | Digital Input |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | X | 3144 |  | XA-3144
S-02115 | X_I-3147 | 227.02 | Digital Input |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | X | 3147 |  | XA-3147
S-02115 | X_I-5013 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5013 |  | XA-5013
S-02115 | X_I-5017 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5017 |  | XA-5017
S-02115 | X_I-5077 | 227.02 | Digital Input |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5077 |  | XA-5077
S-02115 | X_I-5081 | 227.02 | Digital Input |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5081 |  | XA-5081
S-02115 | X_I-5092 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5092 |  | XA-5092
S-02115 | X_I-5101 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5101 |  | XA-5101
S-02115 | X_I-5105 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5105 |  | XA-5105
S-02115 | X_I-5133 | 227.02 | Digital Input |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5133 |  | XA-5133
S-02115 | X_I-5137 | 227.02 | Digital Input |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5137 |  | XA-5137
S-02115 | X_I-5201 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5201 |  | XA-5201
S-02115 | X_I-5212 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5212 |  | XA-5212
S-02115 | X_I-5216 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5216 |  | XA-5216
S-02115 | X_I-5232 | 227.02 | Digital Input |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5232 |  | XA-5232
S-02115 | X_I-5233 | 227.02 | Digital Input |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5233 |  | XA-5233
S-02115 | X_I-5236 | 227.02 | Digital Input |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5236 |  | XA-5236
S-02115 | X_I-5237 | 227.02 | Digital Input |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5237 |  | XA-5237
S-02115 | X_I-5329 | 227.02 | Digital Input |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5329 |  | XA-5329
S-02115 | X_I-5333 | 227.02 | Digital Input |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5333 |  | XA-5333
S-02115 | X_I-5353 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5353 |  | XA-5353
S-02115 | X_I-5357 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5357 |  | XA-5357
S-02115 | X_I-5361 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5361 |  | XA-5361
S-02115 | X_I-5365 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5365 |  | XA-5365
S-02115 | X_I-5368 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5368 |  | XA-5368
S-02115 | X_I-5425 | 227.02 | Digital Input |  | P44 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5425 |  | XA-5425
S-02115 | X_I-5429 | 227.02 | Digital Input |  | P44 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5429 |  | XA-5429
S-02115 | X_I-5455 | 227.02 | Digital Input |  | P45 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5455 |  | XA-5455
S-02115 | X_I-5459 | 227.02 | Digital Input |  | P45 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5459 |  | XA-5459
S-02115 | X_I-5511 | 227.02 | Digital Input |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5511 |  | XA-5511
S-02115 | X_I-5512 | 227.02 | Digital Input |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | X | 5512 |  | XA-5512
S-02115 | X_I-6004 | 227.02 | Digital Input |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | X | 6004 |  | XA-6004
S-02115 | X_I-6008 | 227.02 | Digital Input |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | X | 6008 |  | XA-6008
S-02115 | X_I-6062 | 227.02 | Digital Input |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | X | 6062 |  | XA-6062
S-02115 | X_I-6066 | 227.02 | Digital Input |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | X | 6066 |  | XA-6066
S-02115 | X_I-7005 | 227.02 | Digital Input |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7005 |  | XA-7005
S-02115 | X_I-7006 | 227.02 | Digital Input |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7006 |  | XA-7006
S-02115 | X_I-7101 | 227.02 | Digital Input |  | U22 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7101 |  | XA-7101
S-02115 | X_I-7103 | 227.02 | Digital Input |  | U22 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7103 |  | XA-7103
S-02115 | X_I-7122 | 227.02 | Digital Input |  | U10 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7122 |  | XA-7122
S-02115 | X_I-7163 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7163 |  | XA-7163
S-02115 | X_I-7166 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7166 |  | XA-7166
S-02115 | X_I-7169 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7169 |  | XA-7169
S-02115 | X_I-7172 | 227.02 | Digital Input |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7172 |  | XA-7172
S-02115 | X_I-7193 | 227.02 | Digital Input |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7193 |  | XA-7193
S-02115 | X_I-7196 | 227.02 | Digital Input |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7196 |  | XA-7196
S-02115 | X_I-7213 | 227.02 | Digital Input |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7213 |  | XA-7213
S-02115 | X_I-7216 | 227.02 | Digital Input |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | X | 7216 |  | XA-7216
S-02115 | Y_I-2124 | 227.02 | Digital Input |  | P11 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2124 |  | YL-2124
S-02115 | Y_I-2159 | 227.02 | Digital Input |  | P12 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2159 |  | YL-2159
S-02115 | Y_I-2410 | 227.02 | Digital Input |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2410 |  | YL-2410
S-02115 | Y_I-2414 | 227.02 | Digital Input |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2414 |  | YL-2414
S-02115 | Y_I-2447 | 227.02 | Digital Input |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2447 |  | YL-2447
S-02115 | Y_I-2451 | 227.02 | Digital Input |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2451 |  | YL-2451
S-02115 | Y_I-2471 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2471 |  | YL-2471
S-02115 | Y_I-2487 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2487 |  | YL-2487
S-02115 | Y_I-2491 | 227.02 | Digital Input |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 2491 |  | YL-2491
S-02115 | Y_I-5013 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5013 |  | YL-5013
S-02115 | Y_I-5017 | 227.02 | Digital Input |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5017 |  | YL-5017
S-02115 | Y_I-5077 | 227.02 | Digital Input |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5077 |  | YL-5077
S-02115 | Y_I-5081 | 227.02 | Digital Input |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5081 |  | YL-5081
S-02115 | Y_I-5101 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5101 |  | YL-5101
S-02115 | Y_I-5105 | 227.02 | Digital Input |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5105 |  | YL-5105
S-02115 | Y_I-5133 | 227.02 | Digital Input |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5133 |  | YL-5133
S-02115 | Y_I-5137 | 227.02 | Digital Input |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5137 |  | YL-5137
S-02115 | Y_I-5212 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5212 |  | YL-5212
S-02115 | Y_I-5216 | 227.02 | Digital Input |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5216 |  | YL-5216
S-02115 | Y_I-5233 | 227.02 | Digital Input |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5233 |  | YL-5233
S-02115 | Y_I-5237 | 227.02 | Digital Input |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5237 |  | YL-5237
S-02115 | Y_I-5329 | 227.02 | Digital Input |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5329 |  | YL-5329
S-02115 | Y_I-5333 | 227.02 | Digital Input |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5333 |  | YL-5333
S-02115 | Y_I-5353 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5353 |  | YL-5353
S-02115 | Y_I-5357 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5357 |  | YL-5357
S-02115 | Y_I-5361 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5361 |  | YL-5361
S-02115 | Y_I-5365 | 227.02 | Digital Input |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5365 |  | YL-5365
S-02115 | Y_I-5404 | 227.02 | Digital Input |  | P43 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 5404 |  | YL-5404
S-02115 | Y_I-6004 | 227.02 | Digital Input |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 6004 |  | YL-6004
S-02115 | Y_I-6008 | 227.02 | Digital Input |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 6008 |  | YL-6008
S-02115 | Y_I-6062 | 227.02 | Digital Input |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 6062 |  | YL-6062
S-02115 | Y_I-6066 | 227.02 | Digital Input |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 6066 |  | YL-6066
S-02115 | Y_I-6081 | 227.02 | Digital Input |  | P08 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 6081 |  | YL-6081
S-02115 | Y_I-6086 | 227.02 | Digital Input |  | P08 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 6086 |  | YL-6086
S-02115 | Y_I-7005 | 227.02 | Digital Input |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 7005 |  | YL-7005
S-02115 | Y_I-7006 | 227.02 | Digital Input |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 7006 |  | YL-7006
S-02115 | Y_I-7122 | 227.02 | Digital Input |  | U10 | [10 empty] | °C |  | On/Off | [29 empty] | Y | 7122 |  | YL-7122
S-02115 | F_O-2007 | 227.03 | Analog Output |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FF AO | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | F_O-2009 | 227.03 | Analog Output |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FF AO | [30 empty] | F | 2009 |  | FIC-2009
S-02115 | F_O-2040 | 227.03 | Analog Output |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AO | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | F_O-2061 | 227.03 | Analog Output |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AO | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | F_O-2072 | 227.03 | Analog Output |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AO | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | F_O-2079 | 227.03 | Analog Output |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF AO | [30 empty] | F | 2079 |  | FIC-2079
S-02115 | F_O-2091 | 227.03 | Analog Output |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AO | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | F_O-2111 | 227.03 | Analog Output |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | FF AO | [30 empty] | F | 2111 |  | FIC-2111
S-02115 | F_O-2150 | 227.03 | Analog Output |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF AO | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | F_O/1-2233 | 227.03 | Analog Output |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | FF AO | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | F_O/2-2233 | 227.03 | Analog Output |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | FF AO | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | F_O-2417 | 227.03 | Analog Output |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF AO | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | F_O/1-2531 | 227.03 | Analog Output |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AO | [30 empty] | F | 2531 |  | FIC-2531
S-02115 | F_O/2-2531 | 227.03 | Analog Output |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AO | [30 empty] | F | 2531 |  | FIC-2531
S-02115 | F_O-2536 | 227.03 | Analog Output |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF AO | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | F_O-3041 | 227.03 | Analog Output |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | FF AO | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | F_O-3169 | 227.03 | Analog Output |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | F | 3169 |  | FIC-3169
S-02115 | F_O-3171 | 227.03 | Analog Output |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | F | 3171 |  | FIC-3171
S-02115 | F_O-5020 | 227.03 | Analog Output |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | F_O-5041 | 227.03 | Analog Output |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | FF AO | [30 empty] | F | 5041 |  | FIC-5041
S-02115 | F_O-5093 | 227.03 | Analog Output |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF AO | [30 empty] | F | 5093 |  | FIC-5093
S-02115 | F_O-5107 | 227.03 | Analog Output |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF AO | [30 empty] | F | 5107 |  | FIC-5107
S-02115 | F_O-5161 | 227.03 | Analog Output |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | FF AO | [30 empty] | F | 5161 |  | FIC-5161
S-02115 | F_O-5203 | 227.03 | Analog Output |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | FF AO | [30 empty] | F | 5203 |  | FIC-5203
S-02115 | F_O-5239 | 227.03 | Analog Output |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | FF AO | [30 empty] | F | 5239 |  | FIC-5239
S-02115 | F_O-5301 | 227.03 | Analog Output |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FF AO | [30 empty] | F | 5301 |  | FIC-5301
S-02115 | F_O-5321 | 227.03 | Analog Output |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | FF AO | [30 empty] | F | 5321 |  | FIC-5321
S-02115 | F_O-5336 | 227.03 | Analog Output |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | FF AO | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | F_O-5337 | 227.03 | Analog Output |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | FF AO | [30 empty] | F | 5337 |  | FIC-5337
S-02115 | F_O-5367 | 227.03 | Analog Output |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | FF AO | [30 empty] | F | 5367 |  | FIC-5367
S-02115 | F_O-5383 | 227.03 | Analog Output |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | FF AO | [30 empty] | F | 5383 |  | FIC-5383
S-02115 | F_O-5441 | 227.03 | Analog Output |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | FF AO | [30 empty] | F | 5441 |  | FIC-5441
S-02115 | F_O-5501 | 227.03 | Analog Output |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | FF AO | [30 empty] | F | 5501 |  | FIC-5501
S-02115 | F_O-6031 | 227.03 | Analog Output |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | FF AO | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | F_O-6070 | 227.03 | Analog Output |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | FF AO | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | F_O-6081 | 227.03 | Analog Output |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | FF AO | [30 empty] | F | 6081 |  | FIC-6081
S-02115 | F_O-6082 | 227.03 | Analog Output |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | FF AO | [30 empty] | F | 6082 |  | FIC-6082
S-02115 | F_O-6086 | 227.03 | Analog Output |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | FF AO | [30 empty] | F | 6086 |  | FIC-6086
S-02115 | F_O-7091 | 227.03 | Analog Output |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | FF AO | [30 empty] | F | 7091 |  | FIC-7091
S-02115 | F_O-7141 | 227.03 | Analog Output |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF AO | [30 empty] | F | 7141 |  | FIC-7141
S-02115 | H_O-2031 | 227.03 | Analog Output |  | P03 | [10 empty] | °C | FF AO | [30 empty] | H | 2031 |  | HIC-2031
S-02115 | H_O-2076 | 227.03 | Analog Output |  | P09 | [10 empty] | °C | FF AO | [30 empty] | H | 2076 |  | HIC-2076
S-02115 | H_O-2097 | 227.03 | Analog Output |  | P10 | [10 empty] | °C | FF AO | [30 empty] | H | 2097 |  | HIC-2097
S-02115 | H_0-2119 | 227.03 | Analog Output |  | P11 | [10 empty] | °C | FF AO | SC-2119 Steam turbine | [29 empty] | H | 2119 |  | HIC-2119
S-02115 | H_O-2167 | 227.03 | Analog Output |  | P12 | [10 empty] | °C | FF AO | SC-2167 Steam turbine | [29 empty] | H | 2167 |  | HIC-2167
S-02115 | H_O/1-2225 | 227.03 | Analog Output |  | P13 | [10 empty] | °C | FF AO | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | H_O/2-2225 | 227.03 | Analog Output |  | P13 | [10 empty] | °C | FF AO | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | H_O-2371 | 227.03 | Analog Output |  | P18 | [10 empty] | °C | FF AO | [30 empty] | H | 2371 |  | HIC-2371
S-02115 | H_O-2472 | 227.03 | Analog Output |  | P21 | [10 empty] | °C | FF AO | Speed control AE 2026 | [29 empty] | H | 2472 |  | HIC-2472
S-02115 | H_O-3011 | 227.03 | Analog Output |  | P22 | [10 empty] | °C | FF AO | [30 empty] | H | 3011 |  | HIC-3011
S-02115 | H_O-3142 | 227.03 | Analog Output |  | P26 | [10 empty] | °C | FF AO | Speedcontrol AE 3002 1 | [29 empty] | H | 3142 |  | HIC-3142
S-02115 | H_O-3145 | 227.03 | Analog Output |  | P26 | [10 empty] | °C | FF AO | Speedcontrol AE 3002 2 | [29 empty] | H | 3145 |  | HIC-3145
S-02115 | H_O-3148 | 227.03 | Analog Output |  | P26 | [10 empty] | °C | FF AO | Speedcontrol AE 3002 3 | [29 empty] | H | 3148 |  | HIC-3148
S-02115 | H_O-5093 | 227.03 | Analog Output |  | P32 | [10 empty] | °C | FF AO | Speed control AE 5004 | [29 empty] | H | 5093 |  | HIC-5093
S-02115 | H_O-5202 | 227.03 | Analog Output |  | P36 | [10 empty] | °C | FF AO | Speed control AE 5005 | [29 empty] | H | 5202 |  | HIC-5202
S-02115 | H_O-5338 | 227.03 | Analog Output |  | P40 | [10 empty] | °C | FF AO | [30 empty] | H | 5338 |  | HIC-5338
S-02115 | H_O-5369 | 227.03 | Analog Output |  | P41 | [10 empty] | °C | FF AO | Speed control AE 5006 | [29 empty] | H | 5369 |  | HIC-5369
S-02115 | H_0-5403 | 227.03 | Analog Output |  | P43 | [10 empty] | °C | 4-20 mA | [30 empty] | H | 5403 |  | HIC-5403
S-02115 | H_O-5454 | 227.03 | Analog Output |  | P45 | [10 empty] | °C | 4-20 mA | [30 empty] | H | 5454 |  | HIC-5454
S-02115 | H_O-5458 | 227.03 | Analog Output |  | P45 | [10 empty] | °C | 4-20 mA | [30 empty] | H | 5458 |  | HIC-5458
S-02115 | H_O-6069 | 227.03 | Analog Output |  | P07 | [10 empty] | °C | FF AO | [30 empty] | H | 6069 |  | HIC-6069
S-02115 | H_O-7102 | 227.03 | Analog Output |  | U22 | [10 empty] | °C | 4-20 mA | [30 empty] | H | 7102 |  | HIC-7102
S-02115 | H_O-7104 | 227.03 | Analog Output |  | U22 | [10 empty] | °C | 4-20 mA | [30 empty] | H | 7104 |  | HIC-7104
S-02115 | H_O-7131 | 227.03 | Analog Output |  | U10 | [10 empty] | °C | FF AO | SC-7131 Steam turbine | [29 empty] | H | 7131 |  | HIC-7131
S-02115 | H_O-7136 | 227.03 | Analog Output |  | U10 | [10 empty] | °C | FF AO | SC-7136 Steam turbine | [29 empty] | H | 7136 |  | HIC-7136
S-02115 | L_O-2016 | 227.03 | Analog Output |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | FF AO | [30 empty] | L | 2016 |  | LIC-2016
S-02115 | L_O-2372 | 227.03 | Analog Output |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | FF AO | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | L_O-2403 | 227.03 | Analog Output |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF AO | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | L_O-2419 | 227.03 | Analog Output |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | FF AO | [30 empty] | L | 2419 |  | LIC-2419
S-02115 | L_O-2441 | 227.03 | Analog Output |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | FF AO | [30 empty] | L | 2441 |  | LIC-2441
S-02115 | L_O-2474 | 227.03 | Analog Output |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | L_O/A-3161 | 227.03 | Analog Output |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | L_O/B-3161 | 227.03 | Analog Output |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | L_O-3192 | 227.03 | Analog Output |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | FF AO | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | L_O-5001 | 227.03 | Analog Output |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 4-20 mA | [30 empty] | L | 5001 |  | LI-5001
S-02115 | L_O-5070 | 227.03 | Analog Output |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | FF AO | [30 empty] | L | 5070 |  | LIC-5070
S-02115 | L_O-5413 | 227.03 | Analog Output |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 4-20 mA | [30 empty] | L | 5413 |  | LI-5413
S-02115 | L_O-5446 | 227.03 | Analog Output |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 5446 |  | LI-5446
S-02115 | L_O-5501 | 227.03 | Analog Output |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | FF AO | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | L_O/A-6021 | 227.03 | Analog Output |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | FF AO | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | L_O/B-6021 | 227.03 | Analog Output |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | FF AO | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | L_O-6082 | 227.03 | Analog Output |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | FF AO | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | L_O-7001 | 227.03 | Analog Output |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 4-20 mA | [30 empty] | L | 7001 |  | LI-7001
S-02115 | L_O-7002 | 227.03 | Analog Output |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 4-20 mA | [30 empty] | L | 7002 |  | LI-7002
S-02115 | L_O-7251 | 227.03 | Analog Output |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | FF AO | [30 empty] | L | 7251 |  | LIC-7251
S-02115 | P_O-1006 | 227.03 | Analog Output |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF AO | [30 empty] | P | 1006 |  | PIC-1006
S-02115 | P_O-1011 | 227.03 | Analog Output |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF AO | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | P_O-1045 | 227.03 | Analog Output |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | FF AO | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | P_O-2015 | 227.03 | Analog Output |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | FF AO | [30 empty] | P | 2015 |  | PIC-2015
S-02115 | P_O-2073 | 227.03 | Analog Output |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF AO | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | P_O-2224 | 227.03 | Analog Output |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | FF AO | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | P_O-2361 | 227.03 | Analog Output |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF AO | [30 empty] | P | 2361 |  | PIC-2361
S-02115 | P_O-2363 | 227.03 | Analog Output |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF AO | [30 empty] | P | 2363 |  | PIC-2363
S-02115 | P_O-2406 | 227.03 | Analog Output |  | P19 |  | 34"-RFG-20-120-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF AO | [30 empty] | P | 2406 |  | PIC-2406
S-02115 | P_O-2481 | 227.03 | Analog Output |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | P | 2481 |  | PIC-2481
S-02115 | P_O-2536 | 227.03 | Analog Output |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF AO | [30 empty] | P | 2536 |  | PIC-2536
S-02115 | PD_O-2575 | 227.03 | Analog Output |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | FF AO | [30 empty] | P | 2575 |  | PDIC-2575
S-02115 | P_O-2603 | 227.03 | Analog Output |  | U17 |  | 3"-HG-20-109-D24-N |  |  | 29 | 25 | bar g |  | 40 | 100 | °C | FF AO | [30 empty] | P | 2603 |  | PIC-2603
S-02115 | P_O-2608 | 227.03 | Analog Output |  | U17 |  | 3"-HG-20-108-F24-N |  |  | 55 | 50.4 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | P | 2608 |  | PIC-2608
S-02115 | P_O-3042 | 227.03 | Analog Output |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | FF AO | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | P_O-3166 | 227.03 | Analog Output |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF AO | [30 empty] | P | 3166 |  | PIC-3166
S-02115 | P_O-3194 | 227.03 | Analog Output |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | FF AO | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | P_O-5069 | 227.03 | Analog Output |  | P31 |  | 14"-LPS-50-103-D24-H |  |  | 9.5 | 2.4 | bar g |  | 187 | 340 | °C | FF AO | [30 empty] | P | 5069 |  | PIC-5069
S-02115 | P_O/A-5091 | 227.03 | Analog Output |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AO | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | P_O/B-5091 | 227.03 | Analog Output |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | FF AO | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | P_O-5109 | 227.03 | Analog Output |  | P32 | [10 empty] | °C | FF AO | [30 empty] | P | 5109 |  | PIC-5109
S-02115 | P_O/A-5207 | 227.03 | Analog Output |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | FF AO | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | P_O/B-5207 | 227.03 | Analog Output |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | FF AO | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | P_O-6025 | 227.03 | Analog Output |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | FF AO | [30 empty] | P | 6025 |  | PIC-6025
S-02115 | P_O/A-7002 | 227.03 | Analog Output |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AO | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | P_O/B-7002 | 227.03 | Analog Output |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AO | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | P_O/C-7002 | 227.03 | Analog Output |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AO | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | P_O-7004 | 227.03 | Analog Output |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF AO | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | P_O/A-7025 | 227.03 | Analog Output |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AO | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | P_O/B-7025 | 227.03 | Analog Output |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AO | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | P_O-7028 | 227.03 | Analog Output |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | FF AO | [30 empty] | P | 7028 |  | PIC-7028
S-02115 | P_O/A-7031 | 227.03 | Analog Output |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AO | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | P_O/B-7031 | 227.03 | Analog Output |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AO | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | P_O/C-7031 | 227.03 | Analog Output |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AO | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | P_O/D-7031 | 227.03 | Analog Output |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AO | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | P_O-7034 | 227.03 | Analog Output |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF AO | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | P_O/A-7051 | 227.03 | Analog Output |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | FF AO | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | P_O/B-7051 | 227.03 | Analog Output |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | FF AO | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | P_O-7056 | 227.03 | Analog Output |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | FF AO | [30 empty] | P | 7056 |  | PIC-7056
S-02115 | P_O-7094 | 227.03 | Analog Output |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | FF AO | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | P_O-7101 | 227.03 | Analog Output |  | U09 | [10 empty] | °C | FF AO | [30 empty] | P | 7101 |  | PIC-7101
S-02115 | T_O-2220 | 227.03 | Analog Output |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | FF AO | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | T_O/1-2335 | 227.03 | Analog Output |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | FF AO | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | T_O/2-2335 | 227.03 | Analog Output |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | FF AO | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | T_O/1-2336 | 227.03 | Analog Output |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | FF AO | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | T_O/2-2336 | 227.03 | Analog Output |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | FF AO | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | T_O-2457 | 227.03 | Analog Output |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | FF AO | [30 empty] | T | 2457 |  | TIC-2457
S-02115 | T_O-3113 | 227.03 | Analog Output |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AO | [30 empty] | T | 3113 |  | TIC-3113
S-02115 | T_O-3116 | 227.03 | Analog Output |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AO | [30 empty] | T | 3116 |  | TIC-3116
S-02115 | T_O-3118 | 227.03 | Analog Output |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | FF AO | [30 empty] | T | 3118 |  | TIC-3118
S-02115 | T_O-5064 | 227.03 | Analog Output |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | FF AO | [30 empty] | T | 5064 |  | TIC-5064
S-02115 | T_O-5277 | 227.03 | Analog Output |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | FF AO | [30 empty] | T | 5277 |  | TIC-5277
S-02115 | T_O-7002 | 227.03 | Analog Output |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | FF AO | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | T_O-7003 | 227.03 | Analog Output |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | FF AO | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | T_O-7004 | 227.03 | Analog Output |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | FF AO | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | T_O/A-7025 | 227.03 | Analog Output |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | FF AO | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | T_O/B-7025 | 227.03 | Analog Output |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | FF AO | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | T_O-7026 | 227.03 | Analog Output |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | FF AO | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | T_O-7027 | 227.03 | Analog Output |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | FF AO | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | T_O-7032 | 227.03 | Analog Output |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | FF AO | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | T_O-7033 | 227.03 | Analog Output |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | FF AO | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | T_O-7052 | 227.03 | Analog Output |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | FF AO | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | T_O-7053 | 227.03 | Analog Output |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | FF AO | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | T_O/A-7071 | 227.03 | Analog Output |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | FF AO | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | T_O/B-7071 | 227.03 | Analog Output |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | FF AO | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | FU_O-5041 | 227.04 | Digital Output |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | I-50 | On/Off | [29 empty] | F | 5041 |  | FIC-5041
S-02115 | FU_O-5161 | 227.04 | Digital Output |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | I-50 | On/Off | [29 empty] | F | 5161 |  | FIC-5161
S-02115 | FU_O-5239 | 227.04 | Digital Output |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | I-50 | On/Off | [29 empty] | F | 5239 |  | FIC-5239
S-02115 | FU_O-5336 | 227.04 | Digital Output |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | I-50 | On/Off | [29 empty] | F | 5336 |  | FIC-5336
S-02115 | FU_O-5337 | 227.04 | Digital Output |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | I-50 | On/Off | [29 empty] | F | 5337 |  | FIC-5337
S-02115 | FU_O-6031 | 227.04 | Digital Output |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | I-32 | On/Off | [29 empty] | F | 6031 |  | FIC-6031
S-02115 | FU_O-6082 | 227.04 | Digital Output |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | I-37 | [30 empty] | F | 6082 |  | FIC-6082
S-02115 | H_O-1003 | 227.04 | Digital Output |  | P01 | [10 empty] | °C |  | On/Off | [29 empty] | H | 1003 |  | HS-1003
S-02115 | H_O-2003 | 227.04 | Digital Output |  | P02 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2003 |  | HS-2003
S-02115 | H_O-2410 | 227.04 | Digital Output |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2410 |  | HS-2410
S-02115 | H_O-2414 | 227.04 | Digital Output |  | P19 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2414 |  | HS-2414
S-02115 | H_O-2447 | 227.04 | Digital Output |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2447 |  | HS-2447
S-02115 | H_O-2451 | 227.04 | Digital Output |  | P20 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2451 |  | HS-2451
S-02115 | H_O-2471 | 227.04 | Digital Output |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2471 |  | HS-2471
S-02115 | H_O-2487 | 227.04 | Digital Output |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2487 |  | HS-2487
S-02115 | H_O-2491 | 227.04 | Digital Output |  | P21 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2491 |  | HS-2491
S-02115 | H_O-2577 | 227.04 | Digital Output |  | U02 | [10 empty] | °C |  | On/Off | [29 empty] | H | 2577 |  | HS-2577
S-02115 | H_O-3141 | 227.04 | Digital Output |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | H | 3141 |  | HS-3141
S-02115 | H_O-3144 | 227.04 | Digital Output |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | H | 3144 |  | HS-3144
S-02115 | H_O-3147 | 227.04 | Digital Output |  | P26 | [10 empty] | °C |  | On/Off | [29 empty] | H | 3147 |  | HS-3147
S-02115 | H_O-5013 | 227.04 | Digital Output |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5013 |  | HS-5013
S-02115 | H_O-5017 | 227.04 | Digital Output |  | P29 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5017 |  | HS-5017
S-02115 | H_O-5077 | 227.04 | Digital Output |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5077 |  | HS-5077
S-02115 | H_O-5081 | 227.04 | Digital Output |  | P31 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5081 |  | HS-5081
S-02115 | H_O-5092 | 227.04 | Digital Output |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5092 |  | HS-5092
S-02115 | H_O-5101 | 227.04 | Digital Output |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5101 |  | HS-5101
S-02115 | H_O-5105 | 227.04 | Digital Output |  | P32 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5105 |  | HS-5105
S-02115 | H_O-5133 | 227.04 | Digital Output |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5133 |  | HS-5133
S-02115 | H_O-5137 | 227.04 | Digital Output |  | P33 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5137 |  | HS-5137
S-02115 | H_O-5201 | 227.04 | Digital Output |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5201 |  | HS-5201
S-02115 | H_O-5212 | 227.04 | Digital Output |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5212 |  | HS-5212
S-02115 | H_O-5216 | 227.04 | Digital Output |  | P36 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5216 |  | HS-5216
S-02115 | H_O-5232 | 227.04 | Digital Output |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5232 |  | HS-5232
S-02115 | H_O-5233 | 227.04 | Digital Output |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5233 |  | HS-5233
S-02115 | H_O-5236 | 227.04 | Digital Output |  | U15 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5236 |  | HS-5236
S-02115 | H_O-5237 | 227.04 | Digital Output |  | P37 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5237 |  | HS-5237
S-02115 | H_O-5329 | 227.04 | Digital Output |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5329 |  | HS-5329
S-02115 | H_O-5333 | 227.04 | Digital Output |  | P40 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5333 |  | HS-5333
S-02115 | H_O-5353 | 227.04 | Digital Output |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5353 |  | HS-5353
S-02115 | H_O-5357 | 227.04 | Digital Output |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5357 |  | HS-5357
S-02115 | H_O-5361 | 227.04 | Digital Output |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5361 |  | HS-5361
S-02115 | H_O-5365 | 227.04 | Digital Output |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5365 |  | HS-5365
S-02115 | H_O-5368 | 227.04 | Digital Output |  | P41 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5368 |  | HS-5368
S-02115 | H_O-5404 | 227.04 | Digital Output |  | P43 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5404 |  | HS-5404
S-02115 | H_O-5425 | 227.04 | Digital Output |  | P44 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5425 |  | HS-5425
S-02115 | H_O-5429 | 227.04 | Digital Output |  | P44 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5429 |  | HS-5429
S-02115 | H_O-5455 | 227.04 | Digital Output |  | P45 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5455 |  | HS-5455
S-02115 | H_O-5459 | 227.04 | Digital Output |  | P45 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5459 |  | HS-5459
S-02115 | H_O-5511 | 227.04 | Digital Output |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5511 |  | HS-5511
S-02115 | H_O-5517 | 227.04 | Digital Output |  | U24 | [10 empty] | °C |  | On/Off | [29 empty] | H | 5517 |  | HS-5517
S-02115 | H_O-6004 | 227.04 | Digital Output |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | H | 6004 |  | HS-6004
S-02115 | H_O-6008 | 227.04 | Digital Output |  | P05 | [10 empty] | °C |  | On/Off | [29 empty] | H | 6008 |  | HS-6008
S-02115 | H_O-6062 | 227.04 | Digital Output |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | H | 6062 |  | HS-6062
S-02115 | H_O-6066 | 227.04 | Digital Output |  | P07 | [10 empty] | °C |  | On/Off | [29 empty] | H | 6066 |  | HS-6066
S-02115 | H_O-6081 | 227.04 | Digital Output |  | P08 | [10 empty] | °C |  | On/Off | [29 empty] | H | 6081 |  | HS-6081
S-02115 | H_O-6086 | 227.04 | Digital Output |  | P08 | [10 empty] | °C |  | On/Off | [29 empty] | H | 6086 |  | HS-6086
S-02115 | H_O-7005 | 227.04 | Digital Output |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7005 |  | HS-7005
S-02115 | H_O-7006 | 227.04 | Digital Output |  | U18 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7006 |  | HS-7006
S-02115 | H_O-7101 | 227.04 | Digital Output |  | U22 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7101 |  | HS-7101
S-02115 | H_O-7103 | 227.04 | Digital Output |  | U22 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7103 |  | HS-7103
S-02115 | H_O-7122 | 227.04 | Digital Output |  | U10 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7122 |  | HS-7122
S-02115 | H_O-7163 | 227.04 | Digital Output |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7163 |  | HS-7163
S-02115 | H_O-7166 | 227.04 | Digital Output |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7166 |  | HS-7166
S-02115 | H_O-7169 | 227.04 | Digital Output |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7169 |  | HS-7169
S-02115 | H_O-7172 | 227.04 | Digital Output |  | U12 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7172 |  | HS-7172
S-02115 | H_O-7193 | 227.04 | Digital Output |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7193 |  | HS-7193
S-02115 | H_O-7196 | 227.04 | Digital Output |  | U13 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7196 |  | HS-7196
S-02115 | H_O-7213 | 227.04 | Digital Output |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7213 |  | HS-7213
S-02115 | H_O-7216 | 227.04 | Digital Output |  | U14 | [10 empty] | °C |  | On/Off | [29 empty] | H | 7216 |  | HS-7216
S-02115 | LU_O-6082 | 227.04 | Digital Output |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | I-39 | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | U_O-2125 | 227.04 | Digital Output |  | P11 | [10 empty] | °C | I-61 | On/Off | [29 empty] | U | 2125 |  | UY-2125
S-02115 | U_O-2233 | 227.04 | Digital Output |  | P13 | [10 empty] | °C | I-17 | On/Off | [29 empty] | U | 2233 |  | UY-2233
S-02115 | UY-2576 | 227.04 | Digital Output |  | U02 | [10 empty] | °C | I-16 | On/Off | [29 empty] | U | 2576 |  | UY-2576
S-02115 | U_O-5021 | 227.04 | Digital Output |  | P29 | [10 empty] | °C | I-61 | On/Off | [29 empty] | U | 5021 |  | UY-5021
S-02115 | US_O-6035 | 227.04 | Digital Output |  | P06 | [10 empty] | °C | I-32 | On/Off | [29 empty] | U | 6035 |  | UY-6035
S-02115 | U_O-6083 | 227.04 | Digital Output |  | P08 | [10 empty] | °C | I-37 | [30 empty] | U | 6083 |  | UY-6083
S-02115 | U_O-6084 | 227.04 | Digital Output |  | P08 | [10 empty] | °C | I-37 | [30 empty] | U | 6084 |  | UY-6084
S-02115 | UY-7101 | 227.04 | Digital Output |  | U22 | [10 empty] | °C | I-38 | [30 empty] | U | 7101 |  | UY-7101
S-02115 | UY-7103 | 227.04 | Digital Output |  | U22 | [10 empty] | °C | I-38 | [30 empty] | U | 7103 |  | UY-7103
S-02115 | UY-7121 | 227.04 | Digital Output |  | U10 | [10 empty] | °C | I-73 | On/Off | [29 empty] | U | 7121 |  | UY-7121
S-02115 | X_O-2284 | 227.04 | Digital Output |  | P15 | [10 empty] | °C | I-15 | On/Off | [29 empty] | X | 2284 |  | XAL-2284
S-02115 | AI-1001 | 227.1 | Analog Indicator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0.5-0.7 SG | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AI-1035 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-40 wt ppm | [30 empty] | A | 1035 |  | AI-1035
S-02115 | AI-1045 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-1 wt ppm | [30 empty] | A | 1045 |  | AI-1045
S-02115 | AI/1-2223 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-10 Vol % | [30 empty] | A | 2223 |  | AI-2223
S-02115 | AI/2-2223 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-2000 ppm | [30 empty] | A | 2223 |  | AI-2223
S-02115 | AI-2224 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-10 Vol % | [30 empty] | A | 2224 |  | AI-2224
S-02115 | AI-2379 | 227.1 | Analog Indicator |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-1 µS/cm | [30 empty] | A | 2379 |  | AI-2379
S-02115 | AI-2382 | 227.1 | Analog Indicator |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 2-14 pH | [30 empty] | A | 2382 |  | AI-2382
S-02115 | AI-2384 | 227.1 | Analog Indicator |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 0-100 µS/cm | [30 empty] | A | 2384 |  | AI-2384
S-02115 | AI-2479 | 227.1 | Analog Indicator |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-10 Vol % | [30 empty] | A | 2479 |  | AI-2479
S-02115 | AI-2531 | 227.1 | Analog Indicator |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-50 MJ/Nm3 | [30 empty] | A | 2531 |  | AI-2531
S-02115 | AI-2532 | 227.1 | Analog Indicator |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-20 MJ/Nm3 | [30 empty] | A | 2532 |  | AI-2532
S-02115 | AI1-3001 | 227.1 | Analog Indicator |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 50-95 Vol % | AFY-3004 | [29 empty] | A | 3001 |  | AI-3001
S-02115 | AI2-3001 | 227.1 | Analog Indicator |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 50-95 Vol % | AFY-3004 | [29 empty] | A | 3001 |  | AI-3001
S-02115 | AI1-3002 | 227.1 | Analog Indicator |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-40 Vol % | AFY-3004 | [29 empty] | A | 3002 |  | AI-3002
S-02115 | AI2-3002 | 227.1 | Analog Indicator |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-40 Vol % | AFY-3004 | [29 empty] | A | 3002 |  | AI-3002
S-02115 | AI1-3003 | 227.1 | Analog Indicator |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-15 Vol % | AFY-3004 | [29 empty] | A | 3003 |  | AI-3003
S-02115 | AI2-3003 | 227.1 | Analog Indicator |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-15 Vol % | AFY-3004 | [29 empty] | A | 3003 |  | AI-3003
S-02115 | AFI/1-3004 | 227.1 | Analog Indicator |  | P22 | [10 empty] | °C | 0-5 | [30 empty] | A | 3004 |  | AFI-3004
S-02115 | AFI/2-3004 | 227.1 | Analog Indicator |  | P22 | [10 empty] | °C | 0-15 | [30 empty] | A | 3004 |  | AFI-3004
S-02115 | AI-3053 | 227.1 | Analog Indicator |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 2-14 pH | [30 empty] | A | 3053 |  | AI-3053
S-02115 | AI-3055 | 227.1 | Analog Indicator |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 0-100 µS/cm | [30 empty] | A | 3055 |  | AI-3055
S-02115 | AI-7099 | 227.1 | Analog Indicator |  | U09 |  | 18"-BFW-70-129-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 2-12 pH | Amine dosing | [29 empty] | A | 7099 |  | AIC-7099
S-02115 | FI-1006 | 227.1 | Analog Indicator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-210000 Nm3/h | [30 empty] | F | 1006 |  | FI-1006
S-02115 | FFI-2020 | 227.1 | Analog Indicator |  | P02 | [10 empty] | °C | 0-0.55 mole/mole | [30 empty] | F | 2020 |  | FFI-2020
S-02115 | FFI-2042 | 227.1 | Analog Indicator |  | P03 | [10 empty] | °C | 0-20 Nm3 / kg | [30 empty] | F | 2042 |  | FFI-2042
S-02115 | FI-2065 | 227.1 | Analog Indicator |  | P09 | [10 empty] | °C | 0-250000 kg/h | [30 empty] | F | 2065 |  | FI-2065
S-02115 | FFI-2069 | 227.1 | Analog Indicator |  | P09 | [10 empty] | °C | 1.5-3 S/C ratio | [30 empty] | F | 2069 |  | FFI-2069
S-02115 | FI-2069 | 227.1 | Analog Indicator |  | P09 | [10 empty] | °C | 0-275000 kg/h | [30 empty] | F | 2069 |  | FFI-2069
S-02115 | FI-2115 | 227.1 | Analog Indicator |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-29000 kg/h | [30 empty] | F | 2115 |  | FI-2115
S-02115 | FI-2151 | 227.1 | Analog Indicator |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-195000 Nm3/h | FFY-2152 | [29 empty] | F | 2151 |  | FI-2151
S-02115 | FFI-2152 | 227.1 | Analog Indicator |  | P12 | [10 empty] | °C | 0.01-0.04 H2/NG ratio | [30 empty] | F | 2152 |  | FFI-2152
S-02115 | FI-2165 | 227.1 | Analog Indicator |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-21000 kg/h | [30 empty] | F | 2165 |  | FI-2165
S-02115 | FI-2372 | 227.1 | Analog Indicator |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-460000 kg/h | LY-2372/3 | [29 empty] | F | 2372 |  | FI-2372
S-02115 | FI-2476 | 227.1 | Analog Indicator |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-650000 Nm3/h | [30 empty] | F | 2476 |  | FI-2476
S-02115 | FI-2582 | 227.1 | Analog Indicator |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-35000 Nm3/h |  | P&T PI-2579 & TI-2579 | [28 empty] | F | 2582 |  | FI-2582
S-02115 | FI-2607 | 227.1 | Analog Indicator |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-6500 Nm3/h | [30 empty] | F | 2607 |  | FI-2607
S-02115 | FI-3020 | 227.1 | Analog Indicator |  | P22 |  | 18"-SG-30-101-H40-H |  |  | 99 | 80 | bar g |  | 122 | 165 | °C | 0-650000 Nm3/h | FY-3168 | [29 empty] | F | 3020 |  | FI-3020
S-02115 | FI-3050 | 227.1 | Analog Indicator |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 0-330000 kg/h | LY-3042/3 | [29 empty] | F | 3050 |  | FI-3050
S-02115 | FI-3167 | 227.1 | Analog Indicator |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-2000000 Nm3/h | FY-3168 | [29 empty] | F | 3167 |  | FI-3167
S-02115 | FI-3168 | 227.1 | Analog Indicator |  | P27 | [10 empty] | °C | 0-2500000 Nm3/h | [30 empty] | F | 3168 |  | FI-3168
S-02115 | FI-3194 | 227.1 | Analog Indicator |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 0-6000 Nm3/h | [30 empty] | F | 3194 |  | FI-3194
S-02115 | FI-3198 | 227.1 | Analog Indicator |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 0-280000 kg/h | FY-5301 | [29 empty] | F | 3198 |  | FI-3198
S-02115 | FI-5068 | 227.1 | Analog Indicator |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 0-40000 kg/h | [30 empty] | F | 5068 |  | FI-5068
S-02115 | FI-5111 | 227.1 | Analog Indicator |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-700 Nm3/h | [30 empty] | F | 5111 |  | FI-5111
S-02115 | FI-5338 | 227.1 | Analog Indicator |  | P40 | [10 empty] | °C | 0-250000 kg/h | [30 empty] | F | 5338 |  | FI-5338
S-02115 | FI-5407 | 227.1 | Analog Indicator |  | P43 |  | 3"-PMP-50-161-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | 0-10000 kg/h | [30 empty] | F | 5407 |  | FI-5407
S-02115 | FI-5421 | 227.1 | Analog Indicator |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 0-240000 kg/h | [30 empty] | F | 5421 |  | FI-5421
S-02115 | FI-6032 | 227.1 | Analog Indicator |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 0-60000 kg/h | [30 empty] | F | 6032 |  | FI-6032
S-02115 | FI-6057 | 227.1 | Analog Indicator |  | P07 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 0-5500 kg/h | [30 empty] | F | 6057 |  | FI-6057
S-02115 | FI-6068 | 227.1 | Analog Indicator |  | P07 |  | 10"-PRC-60-111-G40-H |  |  | 72 | 44 | bar g |  | 225 | 290 | °C | 0-310000 kg/h | [30 empty] | F | 6068 |  | FI-6068
S-02115 | FI-7001 | 227.1 | Analog Indicator |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-175000 kg/h | [30 empty] | F | 7001 |  | FI-7001
S-02115 | FI-7029 | 227.1 | Analog Indicator |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-250000 kg/h | [30 empty] | F | 7029 |  | FI-7029
S-02115 | FI-7030 | 227.1 | Analog Indicator |  | U04 |  | 24"-HPS-70-136-F34-H |  |  | 52 | 42 | bar g |  | 410 | 470 | °C | 0-225000 kg/h | [30 empty] | F | 7030 |  | FI-7030
S-02115 | FI-7101 | 227.1 | Analog Indicator |  | U22 |  | 2"-PRC-70-141-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | 0-6000 kg/h | [30 empty] | F | 7101 |  | FI-7101
S-02115 | FI-7129 | 227.1 | Analog Indicator |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-16000 kg/h | [30 empty] | F | 7129 |  | FI-7129
S-02115 | FI-7134 | 227.1 | Analog Indicator |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-16000 kg/h | [30 empty] | F | 7134 |  | FI-7134
S-02115 | LI-1004 | 227.1 | Analog Indicator |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-100 % | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LI-2373 | 227.1 | Analog Indicator |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-100 % | [30 empty] | L | 2373 |  | LI-2373
S-02115 | LI-2404 | 227.1 | Analog Indicator |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 0-100 % | [30 empty] | L | 2404 |  | LI-2404
S-02115 | LI-2442 | 227.1 | Analog Indicator |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | 0-100 % | [30 empty] | L | 2442 |  | LI-2442
S-02115 | LI-3043 | 227.1 | Analog Indicator |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-100 % | [30 empty] | L | 3043 |  | LI-3043
S-02115 | LI-5001 | 227.1 | Analog Indicator |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 0-100 % | [30 empty] | L | 5001 |  | LI-5001
S-02115 | LI-5002 | 227.1 | Analog Indicator |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 0-100 % | [30 empty] | L | 5002 |  | LI-5002
S-02115 | LI-5042 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | 0-100 % | [30 empty] | L | 5042 |  | LI-5042
S-02115 | LI-5065 | 227.1 | Analog Indicator |  | P30 |  | E 2024 2 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | 0-100 % | [30 empty] | L | 5065 |  | LI-5065
S-02115 | LI-5071 | 227.1 | Analog Indicator |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | 0-100 % | [30 empty] | L | 5071 |  | LI-5071
S-02115 | LI-5094 | 227.1 | Analog Indicator |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | 0-100 % | [30 empty] | L | 5094 |  | LI-5094
S-02115 | LI-5162 | 227.1 | Analog Indicator |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | 0-100 % | [30 empty] | L | 5162 |  | LI-5162
S-02115 | LI-5182 | 227.1 | Analog Indicator |  | P34 |  | E 5002 4 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | 0-100 % | [30 empty] | L | 5182 |  | LI-5182
S-02115 | LI-5204 | 227.1 | Analog Indicator |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 0-100 % | [30 empty] | L | 5204 |  | LI-5204
S-02115 | LI-5232 | 227.1 | Analog Indicator |  | U15 |  | TK 5080 |  |  |  |  | bar g |  |  |  | °C | 0-100 % | [30 empty] | L | 5232 |  | LI-5232
S-02115 | LI-5271 | 227.1 | Analog Indicator |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | 0-100 % | [30 empty] | L | 5271 |  | LI-5271
S-02115 | LI-5278 | 227.1 | Analog Indicator |  | P39 |  | E 5003 2 Shell |  |  | 7.5 | 3.6 |  |  | 149 | 175 | °C | 0-100 % | [30 empty] | L | 5278 |  | LI-5278
S-02115 | LI-5308 | 227.1 | Analog Indicator |  | P39 |  | E 5003 1 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 340 | °C | 0-100 % | [30 empty] | L | 5308 |  | LI-5308
S-02115 | LI-5310 | 227.1 | Analog Indicator |  | P39 |  | E 5003 2 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 175 | °C | 0-100 % | [30 empty] | L | 5310 |  | LI-5310
S-02115 | LI-5322 | 227.1 | Analog Indicator |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | 0-100 % | [30 empty] | L | 5322 |  | LI-5322
S-02115 | LI-5396 | 227.1 | Analog Indicator |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | 0-100 % | [30 empty] | L | 5396 |  | LI-5396
S-02115 | LI-5397 | 227.1 | Analog Indicator |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | 0-100 % | [30 empty] | L | 5397 |  | LI-5397
S-02115 | LI-5413 | 227.1 | Analog Indicator |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 0-100 % | [30 empty] | L | 5413 |  | LI-5413
S-02115 | LI-5414 | 227.1 | Analog Indicator |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 0-100 % | [30 empty] | L | 5414 |  | LI-5414
S-02115 | LI-5446 | 227.1 | Analog Indicator |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 0-100 % | [30 empty] | L | 5446 |  | LI-5446
S-02115 | LI-5447 | 227.1 | Analog Indicator |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 0-100 % | [30 empty] | L | 5447 |  | LI-5447
S-02115 | LI-5511 | 227.1 | Analog Indicator |  | U24 |  | TK 5050 | [8 empty] | °C | 0-100 % | [30 empty] | L | 5511 |  | LI-5511
S-02115 | LI-6022/1 | 227.1 | Analog Indicator |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | 0-100 % | [30 empty] | L | 6022 | 1 | LI-6022/1
S-02115 | LI-6022/2 | 227.1 | Analog Indicator |  | P06 |  | T 6001 2 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | 0-100 % | [30 empty] | L | 6022 | 2 | LI-6022/2
S-02115 | LI-6033/1 | 227.1 | Analog Indicator |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | 0-100 % | [30 empty] | L | 6033 | 1 | LI-6033/1
S-02115 | LI-6033/2 | 227.1 | Analog Indicator |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | 0-100 % | [30 empty] | L | 6033 | 2 | LI-6033/2
S-02115 | LI-6034/1 | 227.1 | Analog Indicator |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | 0-100 % | [30 empty] | L | 6034 | 1 | LI-6034/1
S-02115 | LI-6034/2 | 227.1 | Analog Indicator |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | 0-100 % | [30 empty] | L | 6034 | 2 | LI-6034/2
S-02115 | LI-6083 | 227.1 | Analog Indicator |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | 0-100 % | [30 empty] | L | 6083 |  | LI-6083
S-02115 | LI-7001 | 227.1 | Analog Indicator |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 0-100 % | [30 empty] | L | 7001 |  | LI-7001
S-02115 | LI-7002 | 227.1 | Analog Indicator |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 0-100 % | [30 empty] | L | 7002 |  | LI-7002
S-02115 | LI-7060 | 227.1 | Analog Indicator |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 0-100 % | [30 empty] | L | 7060 |  | LI-7060
S-02115 | LI-7061 | 227.1 | Analog Indicator |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 0-100 % | [30 empty] | L | 7061 |  | LI-7061
S-02115 | LI-7101 | 227.1 | Analog Indicator |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | 0-100 % | [30 empty] | L | 7101 |  | LI-7101
S-02115 | LI-7102 | 227.1 | Analog Indicator |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | 0-100 % | [30 empty] | L | 7102 |  | LI-7102
S-02115 | LI-7162 | 227.1 | Analog Indicator |  | U12 |  | TK 7050 |  |  |  |  | bar g |  |  |  | °C | 0-100 % | [30 empty] | L | 7162 |  | LI-7162
S-02115 | LI-7192 | 227.1 | Analog Indicator |  | U13 |  | TK 7060 |  |  |  |  | bar g |  |  |  | °C | 0-100 % | [30 empty] | L | 7192 |  | LI-7192
S-02115 | LI-7212 | 227.1 | Analog Indicator |  | U14 |  | TK 7070 |  |  |  |  | bar g |  |  |  | °C | 0-100 % | [30 empty] | L | 7212 |  | LI-7212
S-02115 | PI-1001 | 227.1 | Analog Indicator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-80 bar g | [30 empty] | P | 1001 |  | PI-1001
S-02115 | PDI-1032 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-1.6 bar | [30 empty] | P | 1032 |  | PDI-1032
S-02115 | PI-2001 | 227.1 | Analog Indicator |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-60 bar g | [30 empty] | P | 2001 |  | PI-2001
S-02115 | PDI-2004 | 227.1 | Analog Indicator |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-1 bar | [30 empty] | P | 2004 |  | PDI-2004
S-02115 | PDI-2032 | 227.1 | Analog Indicator |  | P03 |  | 4"-HPS-70-103-F34-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-1 bar | [30 empty] | P | 2032 |  | PDI-2032
S-02115 | PI-2035 | 227.1 | Analog Indicator |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-70 bar g | [30 empty] | P | 2035 |  | PI-2035
S-02115 | PDI-2036 | 227.1 | Analog Indicator |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-8 bar | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PI-2046 | 227.1 | Analog Indicator |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | 0-60 bar g | PDY-2320 | [29 empty] | P | 2046 |  | PI-2046
S-02115 | PI-2047 | 227.1 | Analog Indicator |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-60 bar g | [30 empty] | P | 2047 |  | PI-2047
S-02115 | PDI-2051 | 227.1 | Analog Indicator |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-4 bar | [30 empty] | P | 2051 |  | PDI-2051
S-02115 | PI-2061 | 227.1 | Analog Indicator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-70 bar g | [30 empty] | P | 2061 |  | PI-2061
S-02115 | PZI-2073 | 227.1 | Analog Indicator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-100 % | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | PI-2077 | 227.1 | Analog Indicator |  | P09 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | 0-70 bar g | [30 empty] | P | 2077 |  | PI-2077
S-02115 | PI-2099 | 227.1 | Analog Indicator |  | P10 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | 0-60 bar g | [30 empty] | P | 2099 |  | PI-2099
S-02115 | PI-2111 | 227.1 | Analog Indicator |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | -25 - 0 mbar g | [30 empty] | P | 2111 |  | PI-2111
S-02115 | PI-2112 | 227.1 | Analog Indicator |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 0-100 mbar g | [30 empty] | P | 2112 |  | PI-2112
S-02115 | PI-2150 | 227.1 | Analog Indicator |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-80 bar g | [30 empty] | P | 2150 |  | PI-2150
S-02115 | PI-2156 | 227.1 | Analog Indicator |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | -100 - 0 mbar g | [30 empty] | P | 2156 |  | PI-2156
S-02115 | PDI-2252 | 227.1 | Analog Indicator |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | 0-2 bar | [30 empty] | P | 2252 |  | PDI-2252
S-02115 | PI-2268 | 227.1 | Analog Indicator |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 0-60 bar g | [30 empty] | P | 2268 |  | PI-2268
S-02115 | PI-2282 | 227.1 | Analog Indicator |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-60 bar g | [30 empty] | P | 2282 |  | PI-2282
S-02115 | PDI-2283 | 227.1 | Analog Indicator |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-8 bar | [30 empty] | P | 2283 |  | PDI-2283
S-02115 | PI-2307 | 227.1 | Analog Indicator |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-60 bar g | [30 empty] | P | 2307 |  | PI-2307
S-02115 | PDI-2320 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-6 bar | [30 empty] | P | 2320 |  | PDI-2320
S-02115 | PDI-2321 | 227.1 | Analog Indicator |  | P16A |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-6 bar | [30 empty] | P | 2321 |  | PDI-2321
S-02115 | PI-2322 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-45 bar g | PDY-2320 | [29 empty] | P | 2322 |  | PI-2322
S-02115 | PDI-2323 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-1 bar | [30 empty] | P | 2323 |  | PDI-2323
S-02115 | PI-2324 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-40 bar g | [30 empty] | P | 2324 |  | PI-2324
S-02115 | PI-2352 | 227.1 | Analog Indicator |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | 0-35 bar g | [30 empty] | P | 2352 |  | PI-2352
S-02115 | PI-2372 | 227.1 | Analog Indicator |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-140 bar g | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PI-2416 | 227.1 | Analog Indicator |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | 0-80 bar g | [30 empty] | P | 2416 |  | PI-2416
S-02115 | PI-2453 | 227.1 | Analog Indicator |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | 0-80 bar g | [30 empty] | P | 2453 |  | PI-2453
S-02115 | PI-2455 | 227.1 | Analog Indicator |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-10 bar g | [30 empty] | P | 2455 |  | PI-2455
S-02115 | PI-2493 | 227.1 | Analog Indicator |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 0-80 bar g | [30 empty] | P | 2493 |  | PI-2493
S-02115 | PI-2540 | 227.1 | Analog Indicator |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | 0-3 bar g | [30 empty] | P | 2540 |  | PI-2540
S-02115 | PI-2579 | 227.1 | Analog Indicator |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-12 bar g | [30 empty] | P | 2579 |  | PI-2579
S-02115 | PI-2582 | 227.1 | Analog Indicator |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-12 bar g | [30 empty] | P | 2582 |  | PI-2582
S-02115 | PI-2601 | 227.1 | Analog Indicator |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-35 bar g | [30 empty] | P | 2601 |  | PI-2601
S-02115 | PI-2607 | 227.1 | Analog Indicator |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-120 bar g | [30 empty] | P | 2607 |  | PI-2607
S-02115 | PI-3023 | 227.1 | Analog Indicator |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 0-120 bar g | [30 empty] | P | 3023 |  | PI-3023
S-02115 | PDI-3024 | 227.1 | Analog Indicator |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 0-10 bar | [30 empty] | P | 3024 |  | PDI-3024
S-02115 | PI-3071 | 227.1 | Analog Indicator |  | P24 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-120 bar g | [30 empty] | P | 3071 |  | PI-3071
S-02115 | PI-3075 | 227.1 | Analog Indicator |  | P24 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-120 bar g | [30 empty] | P | 3075 |  | PI-3075
S-02115 | PI-3079 | 227.1 | Analog Indicator |  | P24 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-120 bar g | [30 empty] | P | 3079 |  | PI-3079
S-02115 | PDI-3112 | 227.1 | Analog Indicator |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-4 bar | [30 empty] | P | 3112 |  | PDI-3112
S-02115 | PDI-3115 | 227.1 | Analog Indicator |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-4 bar | [30 empty] | P | 3115 |  | PDI-3115
S-02115 | PDI-3117 | 227.1 | Analog Indicator |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-4 bar | [30 empty] | P | 3117 |  | PDI-3117
S-02115 | PI-5004 | 227.1 | Analog Indicator |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | -10 - +30 mbar g | [30 empty] | P | 5004 |  | PI-5004
S-02115 | PI-5022 | 227.1 | Analog Indicator |  | P29 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 0-14 bar g | [30 empty] | P | 5022 |  | PI-5022
S-02115 | PI-5047 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-1.5 bar g | PDI-5048 | [29 empty] | P | 5047 |  | PI-5047
S-02115 | PDI-5048 | 227.1 | Analog Indicator |  | P30 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5048 |  | PDI-5048
S-02115 | PI-5049 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-1.5 bar g | PDI-5048 & PDI-5050 | [29 empty] | P | 5049 |  | PI-5049
S-02115 | PDI-5050 | 227.1 | Analog Indicator |  | P30 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5050 |  | PDI-5050
S-02115 | PI-5051 | 227.1 | Analog Indicator |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-1.5 bar g | PDI-5050 | [29 empty] | P | 5051 |  | PI-5051
S-02115 | PI-5083 | 227.1 | Analog Indicator |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | 0-10 bar g | [30 empty] | P | 5083 |  | PI-5083
S-02115 | PI-5093 | 227.1 | Analog Indicator |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-12 bar g | [30 empty] | P | 5093 |  | PI-5093
S-02115 | PI-5111 | 227.1 | Analog Indicator |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-4 bar g | [30 empty] | P | 5111 |  | PI-5111
S-02115 | PI-5139 | 227.1 | Analog Indicator |  | P33 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 0-10 bar g | [30 empty] | P | 5139 |  | PI-5139
S-02115 | PI-5166 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1.5 bar g | PDI-5167 | [29 empty] | P | 5166 |  | PI-5166
S-02115 | PDI-5167 | 227.1 | Analog Indicator |  | P34 | [10 empty] | °C | 0-150 mbar | [30 empty] | P | 5167 |  | PDI-5167
S-02115 | PI-5168 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1 bar g | PDI-5169, PDI-5173 | [29 empty] | P | 5168 |  | PI-5168
S-02115 | PDI-5169 | 227.1 | Analog Indicator |  | P34 | [10 empty] | °C | 0-400 mbar | [30 empty] | P | 5169 |  | PDI-5169
S-02115 | PI-5170 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1 bar g | PDI-5169, PDI-5171 | [29 empty] | P | 5170 |  | PI-5170
S-02115 | PDI-5171 | 227.1 | Analog Indicator |  | P34 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5171 |  | PDI-5171
S-02115 | PI-5172 | 227.1 | Analog Indicator |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | 0-0.6 bar g | PDI-5171 | [29 empty] | P | 5172 |  | PI-5172
S-02115 | PDI-5173 | 227.1 | Analog Indicator |  | P34 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5173 |  | PDI-5173
S-02115 | PI-5176 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-1.5 bar g | PDI-5167, PDI-5173 | [29 empty] | P | 5176 |  | PI-5176
S-02115 | PI-5219 | 227.1 | Analog Indicator |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-12 bar g | [30 empty] | P | 5219 |  | PI-5219
S-02115 | PI-5240 | 227.1 | Analog Indicator |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 0-20 bar g | [30 empty] | P | 5240 |  | PI-5240
S-02115 | PI-5252 | 227.1 | Analog Indicator |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | 0-6 bar g | PDI-5253 | [29 empty] | P | 5252 |  | PI-5252
S-02115 | PDI-5253 | 227.1 | Analog Indicator |  | P38 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5253 |  | PDI-5253
S-02115 | PI-5254 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g | PDI-5255 | [29 empty] | P | 5254 |  | PI-5254
S-02115 | PDI-5255 | 227.1 | Analog Indicator |  | P38 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5255 |  | PDI-5255
S-02115 | PI-5256 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g | PDI-5255, PDI-5257 | [29 empty] | P | 5256 |  | PI-5256
S-02115 | PDI-5257 | 227.1 | Analog Indicator |  | P38 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5257 |  | PDI-5257
S-02115 | PI-5258 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g | PDI-5257, PDI-5259 | [29 empty] | P | 5258 |  | PI-5258
S-02115 | PDI-5259 | 227.1 | Analog Indicator |  | P38 | [10 empty] | °C | 0-500 mbar | [30 empty] | P | 5259 |  | PDI-5259
S-02115 | PI-5260 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-6 bar g | PDI-5259 | [29 empty] | P | 5260 |  | PI-5260
S-02115 | PI-5307 | 227.1 | Analog Indicator |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 0-14 bar g | [30 empty] | P | 5307 |  | PI-5307
S-02115 | PI-5335 | 227.1 | Analog Indicator |  | P40 |  | 6"-PMP-50-140-D24-P |  |  | 19 | 3.6 | bar g |  | 101 | 165 | °C | 0-25 bar g | [30 empty] | P | 5335 |  | PI-5335
S-02115 | PI-5367 | 227.1 | Analog Indicator |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 0-90 bar g | [30 empty] | P | 5367 |  | PI-5367
S-02115 | PI-5369 | 227.1 | Analog Indicator |  | P41 |  | 2"-PMW-50-124-B24-P |  |  | 7.5 | 4.5 | bar g |  | 149 | 175 | °C | 0-10 bar g | [30 empty] | P | 5369 |  | PI-5369
S-02115 | PDI-5385 | 227.1 | Analog Indicator |  | P42 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-0.5 bar | [30 empty] | P | 5385 |  | PDI-5385
S-02115 | PI-5387 | 227.1 | Analog Indicator |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-10 bar g | [30 empty] | P | 5387 |  | PI-5387
S-02115 | PI-5398 | 227.1 | Analog Indicator |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | -10 - +30 mbar g | [30 empty] | P | 5398 |  | PI-5398
S-02115 | PI-5415 | 227.1 | Analog Indicator |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | -10 - +30 mbar g | [30 empty] | P | 5415 |  | PI-5415
S-02115 | PI-5421 | 227.1 | Analog Indicator |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 0-10 bar g | [30 empty] | P | 5421 |  | PI-5421
S-02115 | PI-5448 | 227.1 | Analog Indicator |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | -10 - +30 mbar g | [30 empty] | P | 5448 |  | PI-5448
S-02115 | PI-6010 | 227.1 | Analog Indicator |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | 0-90 bar g | [30 empty] | P | 6010 |  | PI-6010
S-02115 | PDI-6026 | 227.1 | Analog Indicator |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 280 | °C | 0-2.5 bar | [30 empty] | P | 6026 |  | PDI-6026
S-02115 | PDI-6028 | 227.1 | Analog Indicator |  | P06 |  | 3"-PRC-20-107-G40-H |  |  | 71 | 45 | bar g |  | 115 | 180 | °C | 0-2 bar | [30 empty] | P | 6028 |  | PDI-6028
S-02115 | PI-6031 | 227.1 | Analog Indicator |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-80 bar g | [30 empty] | P | 6031 |  | PI-6031
S-02115 | PI-6054 | 227.1 | Analog Indicator |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | 0-70 bar g | [30 empty] | P | 6054 |  | PI-6054
S-02115 | PI-6088 | 227.1 | Analog Indicator |  | P08 |  | 4"-BD-60-119-B40-P |  |  | 9 | 3 | bar g |  | 78 | 150 | °C | 0-6 bar g | [30 empty] | P | 6088 |  | PI-6088
S-02115 | PZI/A-7002 | 227.1 | Analog Indicator |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PZI/B-7002 | 227.1 | Analog Indicator |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | TY-7003 | [29 empty] | P | 7002 |  | PIC-7002
S-02115 | PZI/C-7002 | 227.1 | Analog Indicator |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | TY-7004 | [29 empty] | P | 7002 |  | PIC-7002
S-02115 | PI-7021 | 227.1 | Analog Indicator |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-60 bar g | [30 empty] | P | 7021 |  | PI-7021
S-02115 | PI-7112 | 227.1 | Analog Indicator |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-3 bar g | [30 empty] | P | 7112 |  | PI-7112
S-02115 | PI-7116 | 227.1 | Analog Indicator |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-3 bar g | [30 empty] | P | 7116 |  | PI-7116
S-02115 | PI-7120 | 227.1 | Analog Indicator |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-3 bar g | [30 empty] | P | 7120 |  | PI-7120
S-02115 | PI-7127 | 227.1 | Analog Indicator |  | U10 |  | 12"-BFW-70-140-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-200 bar g | [30 empty] | P | 7127 |  | PI-7127
S-02115 | PI-8001 | 227.1 | Analog Indicator |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | 0-3 bar g | [30 empty] | P | 8001 |  | PI-8001
S-02115 | SI-2118 | 227.1 | Analog Indicator |  | P11 | [10 empty] | °C | By Vendor | [30 empty] | S | 2118 |  | SI-2118
S-02115 | SI-2168 | 227.1 | Analog Indicator |  | P12 | [10 empty] | °C | By Vendor | [30 empty] | S | 2168 |  | SI-2168
S-02115 | TI-1001 | 227.1 | Analog Indicator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-100 °C | [30 empty] | T | 1001 |  | TI-1001
S-02115 | TI-1010 | 227.1 | Analog Indicator |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-100 °C | [30 empty] | T | 1010 |  | TI-1010
S-02115 | TI-1012 | 227.1 | Analog Indicator |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-100 °C | [30 empty] | T | 1012 |  | TI-1012
S-02115 | TI-1034 | 227.1 | Analog Indicator |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-500 °C | [30 empty] | T | 1034 |  | TI-1034
S-02115 | TI-1035 | 227.1 | Analog Indicator |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-500 °C | [30 empty] | T | 1035 |  | TI-1035
S-02115 | TI-1037 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-500 °C | [30 empty] | T | 1037 |  | TI-1037
S-02115 | TI-1041 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-500 °C | [30 empty] | T | 1041 |  | TI-1041
S-02115 | TI-1042 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-500 °C | [30 empty] | T | 1042 |  | TI-1042
S-02115 | TI-1045 | 227.1 | Analog Indicator |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-500 °C | [30 empty] | T | 1045 |  | TI-1045
S-02115 | TI-1047 | 227.1 | Analog Indicator |  | P04 |  | 8"-FLG-10-113-B24-P |  |  | 5 |  | bar g |  |  | 410 | °C | 0-500 °C | [30 empty] | T | 1047 |  | TI-1047
S-02115 | TI-2001 | 227.1 | Analog Indicator |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-100 °C | [30 empty] | T | 2001 |  | TI-2001
S-02115 | TI-2003 | 227.1 | Analog Indicator |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | 0-400 °C | [30 empty] | T | 2003 |  | TI-2003
S-02115 | TI-2039 | 227.1 | Analog Indicator |  | P03 |  | 4"-HPS-20-109-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | [30 empty] | T | 2039 |  | TI-2039
S-02115 | TI-2044 | 227.1 | Analog Indicator |  | P03 |  | 6"-VA-20-104-F70-P |  |  | 45 |  | bar g |  |  | 255 | °C | 0-300 °C | [30 empty] | T | 2044 |  | TI-2044
S-02115 | TI-2046 | 227.1 | Analog Indicator |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | 0-300 °C | [30 empty] | T | 2046 |  | TI-2046
S-02115 | TI-2047 | 227.1 | Analog Indicator |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 0-300 °C | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TI-2050 | 227.1 | Analog Indicator |  | P03 |  | 2"-VA-20-101-F70-P |  |  | 4.5 |  | bar g |  |  | 255 | °C | 0-300 °C | [30 empty] | T | 2050 |  | TI-2050
S-02115 | TI-2061 | 227.1 | Analog Indicator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-400 °C | [30 empty] | T | 2061 |  | TI-2061
S-02115 | TI-2074 | 227.1 | Analog Indicator |  | P09 |  | 24"-FLG-20-107-B24-P |  |  | 5 |  | bar g |  |  | 290 | °C | 0-400 °C | [30 empty] | T | 2074 |  | TI-2074
S-02115 | TI-2111 | 227.1 | Analog Indicator |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | 0-100 °C | [30 empty] | T | 2111 |  | TI-2111
S-02115 | TI-2112 | 227.1 | Analog Indicator |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 0-100 °C | [30 empty] | T | 2112 |  | TI-2112
S-02115 | TI-2148 | 227.1 | Analog Indicator |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | 0-500 °C | [30 empty] | T | 2148 |  | TI-2148
S-02115 | TI-2149 | 227.1 | Analog Indicator |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | 0-500 °C | [30 empty] | T | 2149 |  | TI-2149
S-02115 | TI-2150 | 227.1 | Analog Indicator |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-200 °C | [30 empty] | T | 2150 |  | TI-2150
S-02115 | TI-2151 | 227.1 | Analog Indicator |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-100 °C | [30 empty] | T | 2151 |  | TI-2151
S-02115 | TI-2154 | 227.1 | Analog Indicator |  | P12 |  | WHS | [6 empty] | 236.3 |  | °C | 0-300 °C | [30 empty] | T | 2154 |  | TI-2154
S-02115 | TI-2155 | 227.1 | Analog Indicator |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | 0-200 °C | [30 empty] | T | 2155 |  | TI-2155
S-02115 | TI-2161 | 227.1 | Analog Indicator |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-300 °C | [30 empty] | T | 2161 |  | TI-2161
S-02115 | TI-2162 | 227.1 | Analog Indicator |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-300 °C | [30 empty] | T | 2162 |  | TI-2162
S-02115 | TI-2221 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TI-2226 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 1093 |  | °C | 0-1200 °C | [30 empty] | T | 2226 |  | TI-2226
S-02115 | TI-2227 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 794 |  | °C | 0-900 °C | [30 empty] | T | 2227 |  | TI-2227
S-02115 | TI-2228 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | -0.02 | bar g |  | 439 |  | °C | 0-500 °C | [30 empty] | T | 2228 |  | TI-2228
S-02115 | TI-2229 | 227.1 | Analog Indicator |  | P13 |  | WHS |  |  |  | 0.05 | bar g |  | 350 |  | °C | 0-400 °C | [30 empty] | T | 2229 |  | TI-2229
S-02115 | TI-2234 | 227.1 | Analog Indicator |  | P13 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-800 °C | [30 empty] | T | 2234 |  | TI-2234
S-02115 | TI-2254 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2254 |  | TI-2254
S-02115 | TI-2255 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2255 |  | TI-2255
S-02115 | TI-2256 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2256 |  | TI-2256
S-02115 | TI-2257 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2257 |  | TI-2257
S-02115 | TI-2258 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2258 |  | TI-2258
S-02115 | TI-2259 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2259 |  | TI-2259
S-02115 | TI-2260 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2260 |  | TI-2260
S-02115 | TI-2261 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2261 |  | TI-2261
S-02115 | TI-2262 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2262 |  | TI-2262
S-02115 | TI-2263 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2263 |  | TI-2263
S-02115 | TI-2264 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2264 |  | TI-2264
S-02115 | TI-2265 | 227.1 | Analog Indicator |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 0-700 °C | [30 empty] | T | 2265 |  | TI-2265
S-02115 | TI-2268 | 227.1 | Analog Indicator |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 0-600 °C | [30 empty] | T | 2268 |  | TI-2268
S-02115 | TI-2285 | 227.1 | Analog Indicator |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-300 °C | [30 empty] | T | 2285 |  | TI-2285
S-02115 | TI-2295 | 227.1 | Analog Indicator |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | [30 empty] | T | 2295 |  | TI-2295
S-02115 | TI-2297 | 227.1 | Analog Indicator |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 0-1200 °C | [30 empty] | T | 2297 |  | TI-2297
S-02115 | TI-2303 | 227.1 | Analog Indicator |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | [30 empty] | T | 2303 |  | TI-2303
S-02115 | TI-2304 | 227.1 | Analog Indicator |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | [30 empty] | T | 2304 |  | TI-2304
S-02115 | TI-2305 | 227.1 | Analog Indicator |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 0-900 °C | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TI-2325 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 0-1300 °C | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TI-2326 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | [30 empty] | T | 2326 |  | TI-2326
S-02115 | TI-2327 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | [30 empty] | T | 2327 |  | TI-2327
S-02115 | TI-2328 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | [30 empty] | T | 2328 |  | TI-2328
S-02115 | TI-2329 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 0-700 °C | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TI-2330 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | [30 empty] | T | 2330 |  | TI-2330
S-02115 | TI-2331 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | [30 empty] | T | 2331 |  | TI-2331
S-02115 | TI-2332 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | 0-400 °C | [30 empty] | T | 2332 |  | TI-2332
S-02115 | TI-2333 | 227.1 | Analog Indicator |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TI-2334 | 227.1 | Analog Indicator |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 0-1300 °C | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TI-2351 | 227.1 | Analog Indicator |  | P17 |  | 24"-RFG-20-110-D34-H |  |  | 30 | 26.3 | bar g |  | 360 | 390 | °C | 0-500 °C | [30 empty] | T | 2351 |  | TI-2351
S-02115 | TI-2352 | 227.1 | Analog Indicator |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | 0-500 °C | [30 empty] | T | 2352 |  | TI-2352
S-02115 | TI-2353 | 227.1 | Analog Indicator |  | P17 |  | 24"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | 0-500 °C | [30 empty] | T | 2353 |  | TI-2353
S-02115 | TI-2354 | 227.1 | Analog Indicator |  | P17 |  | 42"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | 0-500 °C | [30 empty] | T | 2354 |  | TI-2354
S-02115 | TI-2355 | 227.1 | Analog Indicator |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | [30 empty] | T | 2355 |  | TI-2355
S-02115 | TI-2356 | 227.1 | Analog Indicator |  | P17 |  | 24"-HHPS-20-117-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C | [30 empty] | T | 2356 |  | TI-2356
S-02115 | TI-2359 | 227.1 | Analog Indicator |  | P17 |  | 20"-HHPS-20-103-H24-H |  |  | 112 | 101 | bar g |  | 338 | 370 | °C | 0-500 °C | [30 empty] | T | 2359 |  | TI-2359
S-02115 | TI-2371 | 227.1 | Analog Indicator |  | P18 |  | 12"-BFW-20-102-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | 0-400 °C | [30 empty] | T | 2371 |  | TI-2371
S-02115 | TI-2402 | 227.1 | Analog Indicator |  | P19 |  | 34"-RFG-20-117-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 0-300 °C | [30 empty] | T | 2402 |  | TI-2402
S-02115 | TI-2407 | 227.1 | Analog Indicator |  | P19 |  | 16"-FLG-20-120-B40-P |  |  | 5 |  | bar g |  |  | 200 | °C | 0-300 °C | [30 empty] | T | 2407 |  | TI-2407
S-02115 | TI-2418 | 227.1 | Analog Indicator |  | P19 |  | 12"-BFW-20-104-G24 |  |  | 113 | 104 | bar g |  | 122 | 160 | °C | 0-200 °C | [30 empty] | T | 2418 |  | TI-2418
S-02115 | TI-2421 | 227.1 | Analog Indicator |  | P19 |  | 34"-RFG-20-122-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 0-300 °C | [30 empty] | T | 2421 |  | TI-2421
S-02115 | TI-2444 | 227.1 | Analog Indicator |  | P20 |  | 34"-RFG-20-124-D40-P |  |  | 29 | 24.4 | bar g |  | 132 | 200 | °C | 0-300 °C | [30 empty] | T | 2444 |  | TI-2444
S-02115 | TI-2455 | 227.1 | Analog Indicator |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-100 °C | [30 empty] | T | 2455 |  | TI-2455
S-02115 | TI-2472 | 227.1 | Analog Indicator |  | P21 |  | 34"-RFG-20-125-D40-P |  |  | 29 | 24.2 | bar g |  | 65 | 120 | °C | 0-200 °C | [30 empty] | T | 2472 |  | TI-2472
S-02115 | TI-2476 | 227.1 | Analog Indicator |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 2476 |  | TI-2476
S-02115 | TI-2484 | 227.1 | Analog Indicator |  | P21 |  | 12"-FLG-20-123-B24-N |  |  | 5 |  | bar g |  |  | 100 | °C | 0-200 °C | [30 empty] | T | 2484 |  | TI-2484
S-02115 | TI-2493 | 227.1 | Analog Indicator |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 2493 |  | TI-2493
S-02115 | TI-2536 | 227.1 | Analog Indicator |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-200 °C | [30 empty] | T | 2536 |  | TI-2536
S-02115 | TI-2540 | 227.1 | Analog Indicator |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | 0-100 °C | [30 empty] | T | 2540 |  | TI-2540
S-02115 | TI-2553 | 227.1 | Analog Indicator |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-200 °C | [30 empty] | T | 2553 |  | TI-2553
S-02115 | TI-2572 | 227.1 | Analog Indicator |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-100 °C | [30 empty] | T | 2572 |  | TI-2572
S-02115 | TI-2579 | 227.1 | Analog Indicator |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-200 °C | [30 empty] | T | 2579 |  | TI-2579
S-02115 | TI-2601 | 227.1 | Analog Indicator |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-100 °C | [30 empty] | T | 2601 |  | TI-2601
S-02115 | TI-2607 | 227.1 | Analog Indicator |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 2607 |  | TI-2607
S-02115 | TI-3045 | 227.1 | Analog Indicator |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 0-400 °C | [30 empty] | T | 3045 |  | TI-3045
S-02115 | TI-3072 | 227.1 | Analog Indicator |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TI-3073 | 227.1 | Analog Indicator |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | [30 empty] | T | 3073 |  | TI-3073
S-02115 | TI-3076 | 227.1 | Analog Indicator |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TI-3077 | 227.1 | Analog Indicator |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | [30 empty] | T | 3077 |  | TI-3077
S-02115 | TI-3080 | 227.1 | Analog Indicator |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 0-400 °C | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TI-3081 | 227.1 | Analog Indicator |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | [30 empty] | T | 3081 |  | TI-3081
S-02115 | TI-3084 | 227.1 | Analog Indicator |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-500 °C | [30 empty] | T | 3084 |  | TI-3084
S-02115 | TI-3111 | 227.1 | Analog Indicator |  | P25 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 0-200 °C | [30 empty] | T | 3111 |  | TI-3111
S-02115 | TI-3119 | 227.1 | Analog Indicator |  | P25 |  | 20"-SG-30-110-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 0-200 °C | [30 empty] | T | 3119 |  | TI-3119
S-02115 | TI-3120 | 227.1 | Analog Indicator |  | P25 |  | 20"-SG-30-109-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 0-200 °C | [30 empty] | T | 3120 |  | TI-3120
S-02115 | TI-3121 | 227.1 | Analog Indicator |  | P25 |  | 20"-SG-30-121-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 0-200 °C | [30 empty] | T | 3121 |  | TI-3121
S-02115 | TI-3142 | 227.1 | Analog Indicator |  | P26 |  | 24"-SG-30-122-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 0-200 °C | [30 empty] | T | 3142 |  | TI-3142
S-02115 | TI-3145 | 227.1 | Analog Indicator |  | P26 |  | 24"-SG-30-123-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 0-200 °C | [30 empty] | T | 3145 |  | TI-3145
S-02115 | TI-3148 | 227.1 | Analog Indicator |  | P26 |  | 24"-SG-30-124-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 0-200 °C | [30 empty] | T | 3148 |  | TI-3148
S-02115 | TI-3164 | 227.1 | Analog Indicator |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 3164 |  | TI-3164
S-02115 | TI-3194 | 227.1 | Analog Indicator |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 3194 |  | TI-3194
S-02115 | TI-3198 | 227.1 | Analog Indicator |  | P28 |  | 10"-PMC-30-111-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 3198 |  | TI-3198
S-02115 | TI-5020 | 227.1 | Analog Indicator |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 0-200 °C | [30 empty] | T | 5020 |  | TI-5020
S-02115 | TI-5039 | 227.1 | Analog Indicator |  | P30 |  | RFG-50 |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 0-200 °C | [30 empty] | T | 5039 |  | TI-5039
S-02115 | TI-5040 | 227.1 | Analog Indicator |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 0-200 °C | [30 empty] | T | 5040 |  | TI-5040
S-02115 | TI-5045 | 227.1 | Analog Indicator |  | P30 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | 0-200 °C | [30 empty] | T | 5045 |  | TI-5045
S-02115 | TI-5052 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-200 °C | [30 empty] | T | 5052 |  | TI-5052
S-02115 | TI-5053 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-200 °C | [30 empty] | T | 5053 |  | TI-5053
S-02115 | TI-5054 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-200 °C | [30 empty] | T | 5054 |  | TI-5054
S-02115 | TI-5056 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-200 °C | [30 empty] | T | 5056 |  | TI-5056
S-02115 | TI-5057 | 227.1 | Analog Indicator |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 0-200 °C | [30 empty] | T | 5057 |  | TI-5057
S-02115 | TI-5059 | 227.1 | Analog Indicator |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-200 °C | [30 empty] | T | 5059 |  | TI-5059
S-02115 | TI-5060 | 227.1 | Analog Indicator |  | P30 |  | 20"-PMC-50-110-B24-H |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | 0-200 °C | [30 empty] | T | 5060 |  | TI-5060
S-02115 | TI-5062 | 227.1 | Analog Indicator |  | P30 |  | 34"-PMV-50-120-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | 0-200 °C | [30 empty] | T | 5062 |  | TI-5062
S-02115 | TI-5067 | 227.1 | Analog Indicator |  | P30 |  | 34"-PMW-50-122-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | 0-200 °C | [30 empty] | T | 5067 |  | TI-5067
S-02115 | TI-5074 | 227.1 | Analog Indicator |  | P31 |  | 8"-LPC-50-110-D24-H |  |  | 18 | 2.4 | bar g |  | 138 | 190 | °C | 0-300 °C | [30 empty] | T | 5074 |  | TI-5074
S-02115 | TI-5097 | 227.1 | Analog Indicator |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | 0-200 °C | [30 empty] | T | 5097 |  | TI-5097
S-02115 | TI-5110 | 227.1 | Analog Indicator |  | P32 |  | 6"-FLG-50-131-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-100 °C | [30 empty] | T | 5110 |  | TI-5110
S-02115 | TI-5111 | 227.1 | Analog Indicator |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-100 °C | [30 empty] | T | 5111 |  | TI-5111
S-02115 | TI-5165 | 227.1 | Analog Indicator |  | P34 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | 0-200 °C | [30 empty] | T | 5165 |  | TI-5165
S-02115 | TI-5167 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | [30 empty] | T | 5167 |  | TI-5167
S-02115 | TI-5171 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | [30 empty] | T | 5171 |  | TI-5171
S-02115 | TI-5173 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | [30 empty] | T | 5173 |  | TI-5173
S-02115 | TI-5174 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | [30 empty] | T | 5174 |  | TI-5174
S-02115 | TI-5175 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | [30 empty] | T | 5175 |  | TI-5175
S-02115 | TI-5177 | 227.1 | Analog Indicator |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | 0-200 °C | [30 empty] | T | 5177 |  | TI-5177
S-02115 | TI-5180 | 227.1 | Analog Indicator |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 0-200 °C | [30 empty] | T | 5180 |  | TI-5180
S-02115 | TI-5181 | 227.1 | Analog Indicator |  | P34 |  | 24"-PMC-50-140-B24-H |  |  | 5 | 0.7 | bar g |  | 83 | 160 | °C | 0-200 °C | [30 empty] | T | 5181 |  | TI-5181
S-02115 | TI-5184 | 227.1 | Analog Indicator |  | P34 |  | 16"-PMC-50-147-B24-H |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | 0-200 °C | [30 empty] | T | 5184 |  | TI-5184
S-02115 | TI-5208 | 227.1 | Analog Indicator |  | P36 |  | 24"-PMP-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 0-200 °C | [30 empty] | T | 5208 |  | TI-5208
S-02115 | TI-5209 | 227.1 | Analog Indicator |  | P36 |  | 20"-PMP-50-102-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | 0-200 °C | [30 empty] | T | 5209 |  | TI-5209
S-02115 | TI-5219 | 227.1 | Analog Indicator |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-200 °C | [30 empty] | T | 5219 |  | TI-5219
S-02115 | TI-5221 | 227.1 | Analog Indicator |  | P36 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 0-100 °C | [30 empty] | T | 5221 |  | TI-5221
S-02115 | TI-5261 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | [30 empty] | T | 5261 |  | TI-5261
S-02115 | TI-5262 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | [30 empty] | T | 5262 |  | TI-5262
S-02115 | TI-5263 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | [30 empty] | T | 5263 |  | TI-5263
S-02115 | TI-5264 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | [30 empty] | T | 5264 |  | TI-5264
S-02115 | TI-5265 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | [30 empty] | T | 5265 |  | TI-5265
S-02115 | TI-5269 | 227.1 | Analog Indicator |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C | [30 empty] | T | 5269 |  | TI-5269
S-02115 | TI-5273 | 227.1 | Analog Indicator |  | P38 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | 0-200 °C | [30 empty] | T | 5273 |  | TI-5273
S-02115 | TI-5280 | 227.1 | Analog Indicator |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | 0-200 °C | [30 empty] | T | 5280 |  | TI-5280
S-02115 | TI-5307 | 227.1 | Analog Indicator |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 0-300 °C | [30 empty] | T | 5307 |  | TI-5307
S-02115 | TI-5325 | 227.1 | Analog Indicator |  | P40 |  | 24"-PMP-50-130-B24-H |  |  | 7 | 2.6 | bar g |  | 101 | 165 | °C | 0-200 °C | [30 empty] | T | 5325 |  | TI-5325
S-02115 | TI-5335 | 227.1 | Analog Indicator |  | P40 |  | 6"-PMP-50-140-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 0-200 °C | [30 empty] | T | 5335 |  | TI-5335
S-02115 | TI-5340 | 227.1 | Analog Indicator |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 0-100 °C | [30 empty] | T | 5340 |  | TI-5340
S-02115 | TI-5369 | 227.1 | Analog Indicator |  | P41 |  | 2"-PMW-50-125-B24-P |  |  | 7.5 | 4.3 | bar g |  | 65 | 120 | °C | 0-200 °C | [30 empty] | T | 5369 |  | TI-5369
S-02115 | TI-5381 | 227.1 | Analog Indicator |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-100 °C | [30 empty] | T | 5381 |  | TI-5381
S-02115 | TI-5441 | 227.1 | Analog Indicator |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 0-200 °C | [30 empty] | T | 5441 |  | TI-5441
S-02115 | TI-5442 | 227.1 | Analog Indicator |  | P45 |  | 2"-LOS-50-113-B24-P |  |  | 7.5 | 2.5 | bar g |  | 115 | 175 | °C | 0-200 °C | [30 empty] | T | 5442 |  | TI-5442
S-02115 | TI-5443 | 227.1 | Analog Indicator |  | P45 |  | 2"-LOS-50-114-B24-N |  |  | 7.5 | 2 | bar g |  | 48 | 75 | °C | 0-100 °C | [30 empty] | T | 5443 |  | TI-5443
S-02115 | TI-6001 | 227.1 | Analog Indicator |  | P05 |  | 18"-MPC-60-101-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | 0-300 °C | [30 empty] | T | 6001 |  | TI-6001
S-02115 | TI-6024 | 227.1 | Analog Indicator |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 280 | °C | 0-300 °C | [30 empty] | T | 6024 |  | TI-6024
S-02115 | TI-6026 | 227.1 | Analog Indicator |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | 0-400 °C | [30 empty] | T | 6026 |  | TI-6026
S-02115 | TI-6031 | 227.1 | Analog Indicator |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-200 °C | [30 empty] | T | 6031 |  | TI-6031
S-02115 | TI-6034 | 227.1 | Analog Indicator |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-200 °C | [30 empty] | T | 6034 |  | TI-6034
S-02115 | TI-6054 | 227.1 | Analog Indicator |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | 0-300 °C | [30 empty] | T | 6054 |  | TI-6054
S-02115 | TI-6056 | 227.1 | Analog Indicator |  | P07 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | 0-400 °C | [30 empty] | T | 6056 |  | TI-6056
S-02115 | TI-6058 | 227.1 | Analog Indicator |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 0-300 °C | [30 empty] | T | 6058 |  | TI-6058
S-02115 | TI-6081 | 227.1 | Analog Indicator |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | 0-200 °C | [30 empty] | T | 6081 |  | TI-6081
S-02115 | TI-6084 | 227.1 | Analog Indicator |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 0-300 °C | [30 empty] | T | 6084 |  | TI-6084
S-02115 | TI-7001 | 227.1 | Analog Indicator |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-500 °C | [30 empty] | T | 7001 |  | TI-7001
S-02115 | TI-7007 | 227.1 | Analog Indicator |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | [30 empty] | T | 7007 |  | TI-7007
S-02115 | TI-7021 | 227.1 | Analog Indicator |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | [30 empty] | T | 7021 |  | TI-7021
S-02115 | TI-7031 | 227.1 | Analog Indicator |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-400 °C | [30 empty] | T | 7031 |  | TI-7031
S-02115 | TI-7056 | 227.1 | Analog Indicator |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | 0-400 °C | [30 empty] | T | 7056 |  | TI-7056
S-02115 | TI-7097 | 227.1 | Analog Indicator |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-200 °C | [30 empty] | T | 7097 |  | TI-7097
S-02115 | TI-7098 | 227.1 | Analog Indicator |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 0 | bar g |  | 120 | 340 | °C | 0-350 °C | [30 empty] | T | 7098 |  | TI-7098
S-02115 | TI-8001 | 227.1 | Analog Indicator |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | 0-500 °C | [30 empty] | T | 8001 |  | TI-8001
S-02115 | F_C-2061 | 227.11 | Communication Link |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | ESD | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | F_C-2072 | 227.11 | Communication Link |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | ESD | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | F_C-2079 | 227.11 | Communication Link |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | ESD | [30 empty] | F | 2079 |  | FIC-2079
S-02115 | F_C-2091 | 227.11 | Communication Link |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | ESD | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | F_C-2150 | 227.11 | Communication Link |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | ESD | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | F_C-2536 | 227.11 | Communication Link |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | ESD | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | F_C-2582 | 227.11 | Communication Link |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | ESD | [30 empty] | F | 2582 |  | FI-2582
S-02115 | F_C-3171 | 227.11 | Communication Link |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | ESD | [30 empty] | F | 3171 |  | FIC-3171
S-02115 | H_C-2063 | 227.11 | Communication Link |  | P09 | [10 empty] | °C | ESD | [30 empty] | H | 2063 |  | HSIC-2063
S-02115 | H_C-2098 | 227.11 | Communication Link |  | P10 | [10 empty] | °C | ESD | [30 empty] | H | 2098 |  | HS-2098
S-02115 | H_C-2225 | 227.11 | Communication Link |  | P13 | [10 empty] | °C | ESD | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | L_C-1004 | 227.11 | Communication Link |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | ESD | [30 empty] | L | 1004 |  | LI-1004
S-02115 | L_C-2403 | 227.11 | Communication Link |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | ESD | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | L_C-2404 | 227.11 | Communication Link |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | ESD | [30 empty] | L | 2404 |  | LI-2404
S-02115 | L_C-2442 | 227.11 | Communication Link |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | ESD | [30 empty] | L | 2442 |  | LI-2442
S-02115 | L_C-3161 | 227.11 | Communication Link |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | ESD | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | L_C-5002 | 227.11 | Communication Link |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | ESD | [30 empty] | L | 5002 |  | LI-5002
S-02115 | L_C-5042 | 227.11 | Communication Link |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | ESD | [30 empty] | L | 5042 |  | LI-5042
S-02115 | L_C-5071 | 227.11 | Communication Link |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | ESD | [30 empty] | L | 5071 |  | LI-5071
S-02115 | L_C-5094 | 227.11 | Communication Link |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | ESD | [30 empty] | L | 5094 |  | LI-5094
S-02115 | L_C-5162 | 227.11 | Communication Link |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | ESD | [30 empty] | L | 5162 |  | LI-5162
S-02115 | L_C-5204 | 227.11 | Communication Link |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | ESD | [30 empty] | L | 5204 |  | LI-5204
S-02115 | L_C-5271 | 227.11 | Communication Link |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | ESD | [30 empty] | L | 5271 |  | LI-5271
S-02115 | L_C-5322 | 227.11 | Communication Link |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | ESD | [30 empty] | L | 5322 |  | LI-5322
S-02115 | L_C-5397 | 227.11 | Communication Link |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | ESD | [30 empty] | L | 5397 |  | LI-5397
S-02115 | L_C-5414 | 227.11 | Communication Link |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | ESD | [30 empty] | L | 5414 |  | LI-5414
S-02115 | L_C-5447 | 227.11 | Communication Link |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | ESD | [30 empty] | L | 5447 |  | LI-5447
S-02115 | L_C-5501 | 227.11 | Communication Link |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | ESD | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | L_C-6022/1 | 227.11 | Communication Link |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | ESD | [30 empty] | L | 6022 | 1 | LI-6022/1
S-02115 | L_C-6022/2 | 227.11 | Communication Link |  | P06 |  | T 6001 2 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | ESD | [30 empty] | L | 6022 | 2 | LI-6022/2
S-02115 | P_C-2036 | 227.11 | Communication Link |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | ESD (Median) | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | P_C-2073 | 227.11 | Communication Link |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | ESD | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | P_C-2582 | 227.11 | Communication Link |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | ESD | [30 empty] | P | 2582 |  | PI-2582
S-02115 | P_C-7112 | 227.11 | Communication Link |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | ESD | [30 empty] | P | 7112 |  | PI-7112
S-02115 | P_C-7116 | 227.11 | Communication Link |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | ESD | [30 empty] | P | 7116 |  | PI-7116
S-02115 | P_C-7120 | 227.11 | Communication Link |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | ESD | [30 empty] | P | 7120 |  | PI-7120
S-02115 | T_C-2047 | 227.11 | Communication Link |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | ESD (Median) | [30 empty] | T | 2047 |  | TI-2047
S-02115 | T_C-2221 | 227.11 | Communication Link |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | ESD | [30 empty] | T | 2221 |  | TI-2221
S-02115 | T_C-2305 | 227.11 | Communication Link |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | ESD (Median) | [30 empty] | T | 2305 |  | TI-2305
S-02115 | T_C-2325 | 227.11 | Communication Link |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | ESD (Median) | [30 empty] | T | 2325 |  | TI-2325
S-02115 | T_C-2329 | 227.11 | Communication Link |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | ESD (Median) | [30 empty] | T | 2329 |  | TI-2329
S-02115 | T_C-2333 | 227.11 | Communication Link |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | ESD (Median) | [30 empty] | T | 2333 |  | TI-2333
S-02115 | T_C-2334 | 227.11 | Communication Link |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | ESD (Median) | [30 empty] | T | 2334 |  | TI-2334
S-02115 | T_C-3072 | 227.11 | Communication Link |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | ESD (Median) | [30 empty] | T | 3072 |  | TI-3072
S-02115 | T_C-3076 | 227.11 | Communication Link |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | ESD (Median) | [30 empty] | T | 3076 |  | TI-3076
S-02115 | T_C-3080 | 227.11 | Communication Link |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | ESD (Median) | [30 empty] | T | 3080 |  | TI-3080
S-02115 | U_C-1001 | 227.11 | Communication Link |  | P01 | [10 empty] | °C | ESD | [30 empty] | U | 1001 |  | USY-1001
S-02115 | U_C-2010 | 227.11 | Communication Link |  | P02 | [10 empty] | °C | ESD | [30 empty] | U | 2010 |  | USY-2010
S-02115 | U_C-2021 | 227.11 | Communication Link |  | P02 | [10 empty] | °C | ESD | [30 empty] | U | 2021 |  | USY-2021
S-02115 | U_C-2038 | 227.11 | Communication Link |  | P03 | [10 empty] | °C | ESD | [30 empty] | U | 2038 |  | USY-2038
S-02115 | U_C-2043 | 227.11 | Communication Link |  | P03 | [10 empty] | °C | ESD | [30 empty] | U | 2043 |  | USY-2043
S-02115 | U_C-2045 | 227.11 | Communication Link |  | P03 | [10 empty] | °C | ESD | [30 empty] | U | 2045 |  | USY-2045
S-02115 | U_C-2048 | 227.11 | Communication Link |  | P03 | [10 empty] | °C | ESD | [30 empty] | U | 2048 |  | USY-2048
S-02115 | U_C-2049 | 227.11 | Communication Link |  | P03 | [10 empty] | °C | ESD | [30 empty] | U | 2049 |  | USY-2049
S-02115 | U_C-2092 | 227.11 | Communication Link |  | P10 | [10 empty] | °C | ESD | [30 empty] | U | 2092 |  | USY-2092
S-02115 | U_C-2093 | 227.11 | Communication Link |  | P10 | [10 empty] | °C | ESD | [30 empty] | U | 2093 |  | USY-2093
S-02115 | U_C-2094 | 227.11 | Communication Link |  | P10 | [10 empty] | °C | ESD | [30 empty] | U | 2094 |  | USY-2094
S-02115 | U_C-2117 | 227.11 | Communication Link |  | P11 | [10 empty] | °C | ESD | [30 empty] | U | 2117 |  | USY-2117
S-02115 | U_C-2166 | 227.11 | Communication Link |  | P12 | [10 empty] | °C | ESD | [30 empty] | U | 2166 |  | USY-2166
S-02115 | U_C-2381 | 227.11 | Communication Link |  | P18 | [10 empty] | °C | ESD | [30 empty] | U | 2381 |  | USY-2381
S-02115 | U_C-2482 | 227.11 | Communication Link |  | P21 | [10 empty] | °C | ESD | [30 empty] | U | 2482 |  | USY-2482
S-02115 | U_C-2541 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2541 |  | USY-2541
S-02115 | U_C-2542 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2542 |  | USY-2542
S-02115 | U_C-2543 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2543 |  | USY-2543
S-02115 | U_C-2544 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2544 |  | USY-2544
S-02115 | U_C-2545 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2545 |  | USY-2545
S-02115 | U_C-2547 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2547 |  | USY-2547
S-02115 | U_C-2548 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2548 |  | USY-2548
S-02115 | U_C-2549 | 227.11 | Communication Link |  | U01 | [10 empty] | °C | ESD | [30 empty] | U | 2549 |  | USY-2549
S-02115 | U_C-3018 | 227.11 | Communication Link |  | P22 | [10 empty] | °C | ESD | [30 empty] | U | 3018 |  | USY-3018
S-02115 | U_C-3052 | 227.11 | Communication Link |  | P23 | [10 empty] | °C | ESD | [30 empty] | U | 3052 |  | USY-3052
S-02115 | U_C-3172 | 227.11 | Communication Link |  | P27 | [10 empty] | °C | ESD | [30 empty] | U | 3172 |  | USY-3172
S-02115 | U_C-5302 | 227.11 | Communication Link |  | P39 | [10 empty] | °C | ESD | [30 empty] | U | 5302 |  | USY-5302
S-02115 | U_C-5391 | 227.11 | Communication Link |  | P43 | [10 empty] | °C | ESD | [30 empty] | U | 5391 |  | USY-5391
S-02115 | U_C-5392 | 227.11 | Communication Link |  | P43 | [10 empty] | °C | ESD | [30 empty] | U | 5392 |  | USY-5392
S-02115 | U_C-5393 | 227.11 | Communication Link |  | P43 | [10 empty] | °C | ESD | [30 empty] | U | 5393 |  | USY-5393
S-02115 | U_C-5420 | 227.11 | Communication Link |  | P44 | [10 empty] | °C | ESD | [30 empty] | U | 5420 |  | USY-5420
S-02115 | U_C-5421 | 227.11 | Communication Link |  | P44 | [10 empty] | °C | ESD | [30 empty] | U | 5421 |  | USY-5421
S-02115 | U_C-5422 | 227.11 | Communication Link |  | P44 | [10 empty] | °C | ESD | [30 empty] | U | 5422 |  | USY-5422
S-02115 | U_C-6081 | 227.11 | Communication Link |  | P08 | [10 empty] | °C | ESD | [30 empty] | U | 6081 |  | USY-6081
S-02115 | U_C-6082 | 227.11 | Communication Link |  | P08 | [10 empty] | °C | ESD | [30 empty] | U | 6082 |  | USY-6082
S-02115 | U_C-7130 | 227.11 | Communication Link |  | U10 | [10 empty] | °C | ESD | [30 empty] | U | 7130 |  | USY-7130
S-02115 | U_C-7135 | 227.11 | Communication Link |  | U10 | [10 empty] | °C | ESD | [30 empty] | U | 7135 |  | USY-7135
S-02115 | FIC-2007 | 227.2 | Controller |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-78000 Nm3/h |  | FFY-2020, FFY-2042 |  |  |  | IS-2 | [24 empty] | F | 2007 |  | FIC-2007
S-02115 | FIC-2009 | 227.2 | Controller |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-24000 Nm3/h | [5 empty] | IS-2 | [24 empty] | F | 2009 |  | FIC-2009
S-02115 | FIC-2040 | 227.2 | Controller |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-9500 kg/h | [5 empty] | IS-21 | [24 empty] | F | 2040 |  | FIC-2040
S-02115 | FIC-2061 | 227.2 | Controller |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-500000 Nm3/h |  |  |  | PIC-2073 | [26 empty] | F | 2061 |  | FIC-2061
S-02115 | FIC-2072 | 227.2 | Controller |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-85000 kg/h |  |  |  | FY-2070/2 |  | IS-1 | [24 empty] | F | 2072 |  | FIC-2072
S-02115 | FIC-2079 | 227.2 | Controller |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-6500 Nm3/h | [5 empty] | IS-1 | [24 empty] | F | 2079 |  | FIC-2079
S-02115 | FIC-2091 | 227.2 | Controller |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-150000 Nm3/h | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | FIC-2111 | 227.2 | Controller |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 0-420000 Nm3/h | [5 empty] | IS-1 | [24 empty] | F | 2111 |  | FIC-2111
S-02115 | FIC-2150 | 227.2 | Controller |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 0-6500 Nm3/h |  | FFY-2152 |  | FY-2151 | [26 empty] | F | 2150 |  | FIC-2150
S-02115 | FIC-2233 | 227.2 | Controller |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 0-17000 kg/h |  |  |  | TIC-2232 | [26 empty] | F | 2233 |  | FIC-2233
S-02115 | FIC-2417 | 227.2 | Controller |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-460000 kg/h | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | FIC-2531 | 227.2 | Controller |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-30000 Nm3/h |  | QY-2532/2 |  |  |  | IS-1 | [24 empty] | F | 2531 |  | FIC-2531
S-02115 | FIC-2536 | 227.2 | Controller |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-80000 Nm3/h |  | QY-2535/1 |  |  |  | I-14 | [24 empty] | F | 2536 |  | FIC-2536
S-02115 | FIC-3041 | 227.2 | Controller |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | 0-330000 kg/h | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | FIC-3169 | 227.2 | Controller |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-80000 Nm3/h | [5 empty] | IS-3 | [24 empty] | F | 3169 |  | FIC-3169
S-02115 | FIC-3171 | 227.2 | Controller |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-80000 Nm3/h | [5 empty] | IS-3 | [24 empty] | F | 3171 |  | FIC-3171
S-02115 | FIC-5020 | 227.2 | Controller |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 0-10000 kg/h | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | FIC-5041 | 227.2 | Controller |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 0-290000 kg/h |  |  |  | LY-5041 | [26 empty] | F | 5041 |  | FIC-5041
S-02115 | FIC-5093 | 227.2 | Controller |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-135000 kg/h |  |  |  | LIC-5093 | [26 empty] | F | 5093 |  | FIC-5093
S-02115 | FIC-5107 | 227.2 | Controller |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-1200 kg/h | [30 empty] | F | 5107 |  | FIC-5107
S-02115 | FIC-5161 | 227.2 | Controller |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 0-290000 kg/h |  | LY-5041 |  | LY-5161 | [26 empty] | F | 5161 |  | FIC-5161
S-02115 | FIC-5203 | 227.2 | Controller |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-340000 kg/h |  | FY-5337 |  | LIC-5203 | [26 empty] | F | 5203 |  | FIC-5203
S-02115 | FIC-5239 | 227.2 | Controller |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 0-140000 kg/h |  | LY-5161 |  | HS-5267 | [26 empty] | F | 5239 |  | FIC-5239
S-02115 | FIC-5301 | 227.2 | Controller |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 0-230000 kg/h | [30 empty] | F | 5301 |  | FIC-5301
S-02115 | FIC-5321 | 227.2 | Controller |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 0-420000 kg/h |  | FY-5336 1/2 |  | LIC-5321 | [26 empty] | F | 5321 |  | FIC-5321
S-02115 | FIC-5336 | 227.2 | Controller |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 0-100000 kg/h | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | FIC-5337 | 227.2 | Controller |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 0-150000 kg/m3 |  | FY-5338 | [28 empty] | F | 5337 |  | FIC-5337
S-02115 | FIC-5367 | 227.2 | Controller |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 0-32000 kg/h |  |  |  | LIC-5270 | [26 empty] | F | 5367 |  | FIC-5367
S-02115 | FIC-5383 | 227.2 | Controller |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | 0-8000 kg/h | [30 empty] | F | 5383 |  | FIC-5383
S-02115 | FIC-5441 | 227.2 | Controller |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 0-2900 kg/h | [30 empty] | F | 5441 |  | FIC-5441
S-02115 | FIC-5501 | 227.2 | Controller |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | 0-32000 kg/h |  |  |  | LIC-5270 | [26 empty] | F | 5501 |  | FIC-5501
S-02115 | FIC-6031 | 227.2 | Controller |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-245000 kg/h |  | ZIC-6025 | [28 empty] | F | 6031 |  | FIC-6031
S-02115 | FIC-6070 | 227.2 | Controller |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 0-200000 Nm3/h |  | FY-2065 |  |  |  | IS-1 | [24 empty] | F | 6070 |  | FIC-6070
S-02115 | FIC-6081 | 227.2 | Controller |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 0-8000 kg/h | [30 empty] | F | 6081 |  | FIC-6081
S-02115 | FIC-6082 | 227.2 | Controller |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | 0-8000 kg/h | [30 empty] | F | 6082 |  | FIC-6082
S-02115 | FIC-6086 | 227.2 | Controller |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 0-60000 kg/h | [30 empty] | F | 6086 |  | FIC-6086
S-02115 | FIC-7091 | 227.2 | Controller |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 0-400000 kg/h |  |  |  | LIC-7091 | [26 empty] | F | 7091 |  | FIC-7091
S-02115 | FIC-7141 | 227.2 | Controller |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-300000 kg/h | [30 empty] | F | 7141 |  | FIC-7141
S-02115 | LIC-2016 | 227.2 | Controller |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | 0-100 % | [30 empty] | L | 2016 |  | LIC-2016
S-02115 | LIC-2372 | 227.2 | Controller |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-100 % | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LIC-2403 | 227.2 | Controller |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 0-100 % | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LIC-2419 | 227.2 | Controller |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 0-100 % | [30 empty] | L | 2419 |  | LIC-2419
S-02115 | LIC-2441 | 227.2 | Controller |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | 0-100 % | [30 empty] | L | 2441 |  | LIC-2441
S-02115 | LIC-2474 | 227.2 | Controller |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-100 % |  | FY-2233/2 | [28 empty] | L | 2474 |  | LIC-2474
S-02115 | LIC-3042 | 227.2 | Controller |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-100 % | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LIC-3161 | 227.2 | Controller |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 0-100 % | [5 empty] | IS-42 | [24 empty] | L | 3161 |  | LIC-3161
S-02115 | LIC-3192 | 227.2 | Controller |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 0-100 % | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LIC-5041 | 227.2 | Controller |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | 0-100 % | [30 empty] | L | 5041 |  | LIC-5041
S-02115 | LIC-5070 | 227.2 | Controller |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | 0-100 % | [30 empty] | L | 5070 |  | LIC-5070
S-02115 | LIC-5093 | 227.2 | Controller |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | 0-100 % |  |  | FIC-5093 | [27 empty] | L | 5093 |  | LIC-5093
S-02115 | LIC-5161 | 227.2 | Controller |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | 0-100 % | [30 empty] | L | 5161 |  | LIC-5161
S-02115 | LIC-5203 | 227.2 | Controller |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 0-100 % |  | FIC-5203 | [28 empty] | L | 5203 |  | LIC-5203
S-02115 | LIC-5270 | 227.2 | Controller |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | 0-100 % |  | FIC-5367 (FIC-5501 optional) | [28 empty] | L | 5270 |  | LIC-5270
S-02115 | LIC-5321 | 227.2 | Controller |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | 0-100 % |  | FIC-5321 | [28 empty] | L | 5321 |  | LIC-5321
S-02115 | LIC-5501 | 227.2 | Controller |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 0-100 % |  | FY-2233/2 | [28 empty] | L | 5501 |  | LIC-5501
S-02115 | LIC-6021 | 227.2 | Controller |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | 0-100 % | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LIC-6051 | 227.2 | Controller |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 0-100 % |  | FY6081,LY6031,FHS6051,FY6086 | [28 empty] | L | 6051 |  | LIC-6051
S-02115 | LIC-6082 | 227.2 | Controller |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | 0-100 % | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | LIC-7091 | 227.2 | Controller |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-100 % |  |  | FIC-7091 | [27 empty] | L | 7091 |  | LIC-7091
S-02115 | LIC-7251 | 227.2 | Controller |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | 0-100 % | [30 empty] | L | 7251 |  | LIC-7251
S-02115 | PIC-1006 | 227.2 | Controller |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-70 bar g | [30 empty] | P | 1006 |  | PIC-1006
S-02115 | PIC-1011 | 227.2 | Controller |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 0-10 bar g | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | PIC-1045 | 227.2 | Controller |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-70 bar g | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | PIC-2015 | 227.2 | Controller |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | 0-70 bar g | [5 empty] | IS-2 | [24 empty] | P | 2015 |  | PIC-2015
S-02115 | PIC-2073 | 227.2 | Controller |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 0-70 bar g |  | FIC-2061 |  |  |  | IS-2 | [24 empty] | P | 2073 |  | PIC-2073
S-02115 | PIC-2163 | 227.2 | Controller |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-60 mbar g |  | FY-2111 | [28 empty] | P | 2163 |  | PIC-2163
S-02115 | PIC-2224 | 227.2 | Controller |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | -40 - +20 mmWG |  | F 2001 |  |  |  | IS-1 | [24 empty] | P | 2224 |  | PIC-2224
S-02115 | PIC-2361 | 227.2 | Controller |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-140 bar g | [30 empty] | P | 2361 |  | PIC-2361
S-02115 | PIC-2363 | 227.2 | Controller |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-140 bar g | [30 empty] | P | 2363 |  | PIC-2363
S-02115 | PIC-2406 | 227.2 | Controller |  | P19 |  | 34"-RFG-20-120-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 0-40 bar g | [30 empty] | P | 2406 |  | PIC-2406
S-02115 | PDIC-2417 | 227.2 | Controller |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-6 bar |  |  | SC-7131 & SC-7136 | [27 empty] | P | 2417 |  | PDIC-2417
S-02115 | PIC-2481 | 227.2 | Controller |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-35 bar g | [5 empty] | IS-1, IS-3 | [24 empty] | P | 2481 |  | PIC-2481
S-02115 | PIC/A-2536 | 227.2 | Controller |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-10 bar g |  | FY-2536/1 | [28 empty] | P | 2536 |  | PIC-2536
S-02115 | PIC/B-2536 | 227.2 | Controller |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-10 bar g | [30 empty] | P | 2536 |  | PIC-2536
S-02115 | PIC-2554 | 227.2 | Controller |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-3 bar g |  | FY-2531/3 | [28 empty] | P | 2554 |  | PIC-2554
S-02115 | PDIC-2575 | 227.2 | Controller |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | By Vendor bar g | [30 empty] | P | 2575 |  | PDIC-2575
S-02115 | PIC-2603 | 227.2 | Controller |  | U17 |  | 3"-HG-20-109-D24-N |  |  | 29 | 25 | bar g |  | 40 | 100 | °C | 0-35 bar g | [30 empty] | P | 2603 |  | PIC-2603
S-02115 | PIC-2608 | 227.2 | Controller |  | U17 |  | 3"-HG-20-108-F24-N |  |  | 55 | 50.4 | bar g |  | 48 | 100 | °C | 0-80 bar g | [30 empty] | P | 2608 |  | PIC-2608
S-02115 | PIC-3007 | 227.2 | Controller |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-35 bar g |  | C 3001/C 3002 | [28 empty] | P | 3007 |  | PIC-3007
S-02115 | PIC-3042 | 227.2 | Controller |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-60 bar g | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PIC/A-3166 | 227.2 | Controller |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-120 bar g |  | FIC-3169 | [28 empty] | P | 3166 |  | PIC-3166
S-02115 | PIC/B-3166 | 227.2 | Controller |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-120 bar g | [5 empty] | IS-41 | [24 empty] | P | 3166 |  | PIC-3166
S-02115 | PIC-3194 | 227.2 | Controller |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 0-10 bar g | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | PIC-5069 | 227.2 | Controller |  | P31 |  | 14"-LPS-50-103-D24-H |  |  | 9.5 | 2.4 | bar g |  | 187 | 340 | °C | 0-6 bar g | [30 empty] | P | 5069 |  | PIC-5069
S-02115 | PIC-5091 | 227.2 | Controller |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-1.5 bar g |  | PIC-5109 (PV) | [28 empty] | P | 5091 |  | PIC-5091
S-02115 | PIC-5109 | 227.2 | Controller |  | P32 | [10 empty] | °C | 0-1.5 bar g |  |  |  |  | PIC-5091 | [25 empty] | P | 5109 |  | PIC-5109
S-02115 | PIC-5207 | 227.2 | Controller |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | -0.1 - +0.9 bar g | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PIC-6025 | 227.2 | Controller |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | 0-60 bar g |  |  |  | ZIC-6025 | [26 empty] | P | 6025 |  | PIC-6025
S-02115 | PIC-7001 | 227.2 | Controller |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-60 bar g |  | FT-7001 1/2 Control | [28 empty] | P | 7001 |  | PIC-7001
S-02115 | PIC-7002 | 227.2 | Controller |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-120 bar g | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PIC-7003 | 227.2 | Controller |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-60 bar g |  | PY-7002 1 | [28 empty] | P | 7003 |  | PIC-7003
S-02115 | PIC-7004 | 227.2 | Controller |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-60 bar g | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | PIC-7025 | 227.2 | Controller |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-120 bar g | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | PIC-7028 | 227.2 | Controller |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | 0-60 bar g | [30 empty] | P | 7028 |  | PIC-7028
S-02115 | PIC-7031 | 227.2 | Controller |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-60 bar g | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PIC-7034 | 227.2 | Controller |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-60 bar g | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | PIC-7051 | 227.2 | Controller |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-12 bar g | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | PIC-7055 | 227.2 | Controller |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-12 bar g |  | FT-7002 1/2 Extraction | [28 empty] | P | 7055 |  | PIC-7055
S-02115 | PIC-7056 | 227.2 | Controller |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | 0-12 bar g | [30 empty] | P | 7056 |  | PIC-7056
S-02115 | PIC-7094 | 227.2 | Controller |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-4 bar g |  | TY-2457 | PIC-7101 | [27 empty] | P | 7094 |  | PIC-7094
S-02115 | PIC-7101 | 227.2 | Controller |  | U09 | [10 empty] | °C | 0-4 bar g |  |  |  |  | PIC-7094 | [25 empty] | P | 7101 |  | PIC-7101
S-02115 | PIC-7141 | 227.2 | Controller |  | U11 |  | 8"-BFW-70-164-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 0-100 bar g |  |  | FIC-7141 | [27 empty] | P | 7141 |  | PIC-7141
S-02115 | QIC-2535 | 227.2 | Controller |  | U01 | [10 empty] | °C | 0-40 MW |  | FY-2531/2, FIC-2536 | [28 empty] | Q | 2535 |  | QIC-2535
S-02115 | TIC-2220 | 227.2 | Controller |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-500 °C | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | TIC-2232 | 227.2 | Controller |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | 0-400 °C |  |  | FIC-2233 |  | TIC-2253 | [25 empty] | T | 2232 |  | TIC-2232
S-02115 | TIC-2253 | 227.2 | Controller |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | 0-700 °C |  | TIC-2232 | [28 empty] | T | 2253 |  | TIC-2253
S-02115 | TIC-2335 | 227.2 | Controller |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C |  | THIC-2360 1/2 |  | TIC-2360 | [26 empty] | T | 2335 |  | TIC-2335
S-02115 | TIC-2336 | 227.2 | Controller |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-700 °C |  | THIC-2360 3/4 |  | TIC-2360 | [26 empty] | T | 2336 |  | TIC-2336
S-02115 | TIC-2360 | 227.2 | Controller |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-600 °C |  |  | TIC-2335 & TIC-2336 | [27 empty] | T | 2360 |  | TIC-2360
S-02115 | TIC-2457 | 227.2 | Controller |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 0-200 °C | [30 empty] | T | 2457 |  | TIC-2457
S-02115 | TIC-3113 | 227.2 | Controller |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-300 °C | [5 empty] | I-45 | [24 empty] | T | 3113 |  | TIC-3113
S-02115 | TIC-3116 | 227.2 | Controller |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-300 °C | [5 empty] | I-46 | [24 empty] | T | 3116 |  | TIC-3116
S-02115 | TIC-3118 | 227.2 | Controller |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 0-300 °C | [5 empty] | I-47 | [24 empty] | T | 3118 |  | TIC-3118
S-02115 | TIC-5064 | 227.2 | Controller |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 0-300 °C | [30 empty] | T | 5064 |  | TIC-5064
S-02115 | TIC-5266 | 227.2 | Controller |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C |  | FHS-5239 | [28 empty] | T | 5266 |  | TIC-5266
S-02115 | TIC-5267 | 227.2 | Controller |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C |  | FHS-5239 | [28 empty] | T | 5267 |  | TIC-5267
S-02115 | TIC-5268 | 227.2 | Controller |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 0-200 °C |  | FHS-5239 | [28 empty] | T | 5268 |  | TIC-5268
S-02115 | TIC-5277 | 227.2 | Controller |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 0-300 °C | [30 empty] | T | 5277 |  | TIC-5277
S-02115 | TIC-7002 | 227.2 | Controller |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | TIC-7003 | 227.2 | Controller |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | TIC-7004 | 227.2 | Controller |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 0-500 °C | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | TIC-7025 | 227.2 | Controller |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | 0-500 °C | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | TIC-7026 | 227.2 | Controller |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | TIC-7027 | 227.2 | Controller |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | TIC-7032 | 227.2 | Controller |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | 0-400 °C | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | TIC-7033 | 227.2 | Controller |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | 0-400 °C | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | TIC-7052 | 227.2 | Controller |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | 0-400 °C | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | TIC-7053 | 227.2 | Controller |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | 0-400 °C | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | TIC-7071 | 227.2 | Controller |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 0-400 °C | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | ZIC-6025 | 227.2 | Controller |  | P06 | [10 empty] | °C | 0-100 % |  | PIC-6025 | [28 empty] | Z | 6025 |  | ZIC-6025
S-02115 | AAH-1001 | 227.3 | Alarm |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | High | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AAL-1001 | 227.3 | Alarm |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Low | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AAH-1035 | 227.3 | Alarm |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | High | [30 empty] | A | 1035 |  | AI-1035
S-02115 | AAH-1045 | 227.3 | Alarm |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | High | [30 empty] | A | 1045 |  | AI-1045
S-02115 | AAH/1-2223 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | A | 2223 |  | AI-2223
S-02115 | AAH/2-2223 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | A | 2223 |  | AI-2223
S-02115 | AAL/1-2223 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Low | [30 empty] | A | 2223 |  | AI-2223
S-02115 | AAH-2224 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | A | 2224 |  | AI-2224
S-02115 | AAL-2224 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Low | [30 empty] | A | 2224 |  | AI-2224
S-02115 | AAH-2379 | 227.3 | Alarm |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | High | [30 empty] | A | 2379 |  | AI-2379
S-02115 | AAH-2382 | 227.3 | Alarm |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | High | [30 empty] | A | 2382 |  | AI-2382
S-02115 | AAL-2382 | 227.3 | Alarm |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Low | [30 empty] | A | 2382 |  | AI-2382
S-02115 | AAH-2384 | 227.3 | Alarm |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | High | [30 empty] | A | 2384 |  | AI-2384
S-02115 | AAH-2479 | 227.3 | Alarm |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | High | [30 empty] | A | 2479 |  | AI-2479
S-02115 | AFAL/1-3004 | 227.3 | Alarm |  | P22 | [10 empty] | °C | Low | [30 empty] | A | 3004 |  | AFI-3004
S-02115 | AFAL/2-3004 | 227.3 | Alarm |  | P22 | [10 empty] | °C | Low | [30 empty] | A | 3004 |  | AFI-3004
S-02115 | AAH-3053 | 227.3 | Alarm |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | High | [30 empty] | A | 3053 |  | AI-3053
S-02115 | AAL-3053 | 227.3 | Alarm |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Low | [30 empty] | A | 3053 |  | AI-3053
S-02115 | AAH-3055 | 227.3 | Alarm |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | High | [30 empty] | A | 3055 |  | AI-3055
S-02115 | AAH-7099 | 227.3 | Alarm |  | U09 |  | 18"-BFW-70-129-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | High | [30 empty] | A | 7099 |  | AIC-7099
S-02115 | AAL-7099 | 227.3 | Alarm |  | U09 |  | 18"-BFW-70-129-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Low | [30 empty] | A | 7099 |  | AIC-7099
S-02115 | FAL-2007 | 227.3 | Alarm |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Low | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FFAH-2020 | 227.3 | Alarm |  | P02 | [10 empty] | °C | High | [30 empty] | F | 2020 |  | FFI-2020
S-02115 | FAL-2040 | 227.3 | Alarm |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FAL-2061 | 227.3 | Alarm |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Low | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FAL-2065 | 227.3 | Alarm |  | P09 | [10 empty] | °C | Low | [30 empty] | F | 2065 |  | FI-2065
S-02115 | FAL-2069 | 227.3 | Alarm |  | P09 | [10 empty] | °C | Low | [30 empty] | F | 2069 |  | FFI-2069
S-02115 | FFAL-2069 | 227.3 | Alarm |  | P09 | [10 empty] | °C | Low | [30 empty] | F | 2069 |  | FFI-2069
S-02115 | FAL-2111 | 227.3 | Alarm |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | Low | [30 empty] | F | 2111 |  | FIC-2111
S-02115 | FAL-2150 | 227.3 | Alarm |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Low | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FDAL-2150 | 227.3 | Alarm |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Deviation Low | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FFAL-2152 | 227.3 | Alarm |  | P12 | [10 empty] | °C | Low | [30 empty] | F | 2152 |  | FFI-2152
S-02115 | FAH-2417 | 227.3 | Alarm |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | High | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | FAL-2417 | 227.3 | Alarm |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Low | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | FAH-2476 | 227.3 | Alarm |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | High | [30 empty] | F | 2476 |  | FI-2476
S-02115 | FAL-2582 | 227.3 | Alarm |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | Low | [30 empty] | F | 2582 |  | FI-2582
S-02115 | FAH-3167 | 227.3 | Alarm |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | High | [30 empty] | F | 3167 |  | FI-3167
S-02115 | FAL-5020 | 227.3 | Alarm |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | Low | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | FAH-5093 | 227.3 | Alarm |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | High | [30 empty] | F | 5093 |  | FIC-5093
S-02115 | FAL-5093 | 227.3 | Alarm |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | Low | [30 empty] | F | 5093 |  | FIC-5093
S-02115 | FAH-5203 | 227.3 | Alarm |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | High | [30 empty] | F | 5203 |  | FIC-5203
S-02115 | FAL-5203 | 227.3 | Alarm |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | Low | [30 empty] | F | 5203 |  | FIC-5203
S-02115 | FAH-5321 | 227.3 | Alarm |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | High | [30 empty] | F | 5321 |  | FIC-5321
S-02115 | FAL-5321 | 227.3 | Alarm |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | Low | [30 empty] | F | 5321 |  | FIC-5321
S-02115 | FAH-5336 | 227.3 | Alarm |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | High | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | FAL-5336 | 227.3 | Alarm |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Low | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | FAH-5337 | 227.3 | Alarm |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | High | [30 empty] | F | 5337 |  | FIC-5337
S-02115 | FAL-5337 | 227.3 | Alarm |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Low | [30 empty] | F | 5337 |  | FIC-5337
S-02115 | FDA-5441 | 227.3 | Alarm |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | Deviation | [30 empty] | F | 5441 |  | FIC-5441
S-02115 | FAL-6031 | 227.3 | Alarm |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Low | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | FAL-6068 | 227.3 | Alarm |  | P07 |  | 10"-PRC-60-111-G40-H |  |  | 72 | 44 | bar g |  | 225 | 290 | °C | Low | [30 empty] | F | 6068 |  | FI-6068
S-02115 | FAH-7091 | 227.3 | Alarm |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | High | [30 empty] | F | 7091 |  | FIC-7091
S-02115 | FAL-7091 | 227.3 | Alarm |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | Low | [30 empty] | F | 7091 |  | FIC-7091
S-02115 | LAH-1004 | 227.3 | Alarm |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | High | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LAL-1004 | 227.3 | Alarm |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Low | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LAH-2016 | 227.3 | Alarm |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | High | [30 empty] | L | 2016 |  | LIC-2016
S-02115 | LAL-2016 | 227.3 | Alarm |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | Low | [30 empty] | L | 2016 |  | LIC-2016
S-02115 | LAH-2372 | 227.3 | Alarm |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | High | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LAL-2372 | 227.3 | Alarm |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Low | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LAH-2373 | 227.3 | Alarm |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | High | [30 empty] | L | 2373 |  | LI-2373
S-02115 | LAL-2373 | 227.3 | Alarm |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Low | [30 empty] | L | 2373 |  | LI-2373
S-02115 | LAH-2403 | 227.3 | Alarm |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | High | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LAL-2403 | 227.3 | Alarm |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Low | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LAH-2419 | 227.3 | Alarm |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | High | [30 empty] | L | 2419 |  | LIC-2419
S-02115 | LAL-2419 | 227.3 | Alarm |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Low | [30 empty] | L | 2419 |  | LIC-2419
S-02115 | LAH-2441 | 227.3 | Alarm |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | High | [30 empty] | L | 2441 |  | LIC-2441
S-02115 | LAL-2441 | 227.3 | Alarm |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | Low | [30 empty] | L | 2441 |  | LIC-2441
S-02115 | LAH-2474 | 227.3 | Alarm |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | High | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LAL-2474 | 227.3 | Alarm |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Low | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LAH-3042 | 227.3 | Alarm |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | High | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LAL-3042 | 227.3 | Alarm |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Low | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LAH-3043 | 227.3 | Alarm |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | High | [30 empty] | L | 3043 |  | LI-3043
S-02115 | LAL-3043 | 227.3 | Alarm |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Low | [30 empty] | L | 3043 |  | LI-3043
S-02115 | LAH-3161 | 227.3 | Alarm |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | High | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LAL-3161 | 227.3 | Alarm |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | Low | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LAH-3192 | 227.3 | Alarm |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | High | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LAL-3192 | 227.3 | Alarm |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Low | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LAH-5001 | 227.3 | Alarm |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | High | [30 empty] | L | 5001 |  | LI-5001
S-02115 | LAL-5001 | 227.3 | Alarm |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | Low | [30 empty] | L | 5001 |  | LI-5001
S-02115 | LAH-5041 | 227.3 | Alarm |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | High | [30 empty] | L | 5041 |  | LIC-5041
S-02115 | LAL-5041 | 227.3 | Alarm |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | Low | [30 empty] | L | 5041 |  | LIC-5041
S-02115 | LAH-5042 | 227.3 | Alarm |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | High | [30 empty] | L | 5042 |  | LI-5042
S-02115 | LAL-5065 | 227.3 | Alarm |  | P30 |  | E 2024 2 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | Low | [30 empty] | L | 5065 |  | LI-5065
S-02115 | LAH-5070 | 227.3 | Alarm |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | High | [30 empty] | L | 5070 |  | LIC-5070
S-02115 | LAL-5070 | 227.3 | Alarm |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | Low | [30 empty] | L | 5070 |  | LIC-5070
S-02115 | LAH-5093 | 227.3 | Alarm |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | High | [30 empty] | L | 5093 |  | LIC-5093
S-02115 | LAL-5093 | 227.3 | Alarm |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | Low | [30 empty] | L | 5093 |  | LIC-5093
S-02115 | LAH-5094 | 227.3 | Alarm |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | High | [30 empty] | L | 5094 |  | LI-5094
S-02115 | LAH-5161 | 227.3 | Alarm |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | High | [30 empty] | L | 5161 |  | LIC-5161
S-02115 | LAL-5161 | 227.3 | Alarm |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | Low | [30 empty] | L | 5161 |  | LIC-5161
S-02115 | LAH-5162 | 227.3 | Alarm |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | High | [30 empty] | L | 5162 |  | LI-5162
S-02115 | LAL-5182 | 227.3 | Alarm |  | P34 |  | E 5002 4 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | Low | [30 empty] | L | 5182 |  | LI-5182
S-02115 | LAH-5203 | 227.3 | Alarm |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | High | [30 empty] | L | 5203 |  | LIC-5203
S-02115 | LAL-5203 | 227.3 | Alarm |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Low | [30 empty] | L | 5203 |  | LIC-5203
S-02115 | LAH-5204 | 227.3 | Alarm |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | High | [30 empty] | L | 5204 |  | LI-5204
S-02115 | LAL-5232 | 227.3 | Alarm |  | U15 |  | TK 5080 |  |  |  |  | bar g |  |  |  | °C | Low | [30 empty] | L | 5232 |  | LI-5232
S-02115 | LAH-5270 | 227.3 | Alarm |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | High | [30 empty] | L | 5270 |  | LIC-5270
S-02115 | LAL-5270 | 227.3 | Alarm |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | Low | [30 empty] | L | 5270 |  | LIC-5270
S-02115 | LAH-5271 | 227.3 | Alarm |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | High | [30 empty] | L | 5271 |  | LI-5271
S-02115 | LAL-5308 | 227.3 | Alarm |  | P39 |  | E 5003 1 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 340 | °C | Low | [30 empty] | L | 5308 |  | LI-5308
S-02115 | LAL-5310 | 227.3 | Alarm |  | P39 |  | E 5003 2 Tube |  |  | 9.5 | 6.5 | bar g |  | 188 | 175 | °C | Low | [30 empty] | L | 5310 |  | LI-5310
S-02115 | LAH-5321 | 227.3 | Alarm |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | High | [30 empty] | L | 5321 |  | LIC-5321
S-02115 | LAL-5321 | 227.3 | Alarm |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | Low | [30 empty] | L | 5321 |  | LIC-5321
S-02115 | LAH-5396 | 227.3 | Alarm |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | High | [30 empty] | L | 5396 |  | LI-5396
S-02115 | LAL-5396 | 227.3 | Alarm |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | Low | [30 empty] | L | 5396 |  | LI-5396
S-02115 | LAH-5413 | 227.3 | Alarm |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | High | [30 empty] | L | 5413 |  | LI-5413
S-02115 | LAL-5413 | 227.3 | Alarm |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | Low | [30 empty] | L | 5413 |  | LI-5413
S-02115 | LAH-5446 | 227.3 | Alarm |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | High | [30 empty] | L | 5446 |  | LI-5446
S-02115 | LAL-5446 | 227.3 | Alarm |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | Low | [30 empty] | L | 5446 |  | LI-5446
S-02115 | LAH-5501 | 227.3 | Alarm |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | High | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LAL-5501 | 227.3 | Alarm |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | Low | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LAL-5511 | 227.3 | Alarm |  | U24 |  | TK 5050 | [8 empty] | °C | Low | [30 empty] | L | 5511 |  | LI-5511
S-02115 | LAH-6021 | 227.3 | Alarm |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | High | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LAL-6021 | 227.3 | Alarm |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | Low | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LAH-6033/1 | 227.3 | Alarm |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | High | [30 empty] | L | 6033 | 1 | LI-6033/1
S-02115 | LAL-6033/1 | 227.3 | Alarm |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Low | [30 empty] | L | 6033 | 1 | LI-6033/1
S-02115 | LAH-6033/2 | 227.3 | Alarm |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | High | [30 empty] | L | 6033 | 2 | LI-6033/2
S-02115 | LAL-6033/2 | 227.3 | Alarm |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Low | [30 empty] | L | 6033 | 2 | LI-6033/2
S-02115 | LAL-6034/1 | 227.3 | Alarm |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Low | [30 empty] | L | 6034 | 1 | LI-6034/1
S-02115 | LAL-6034/2 | 227.3 | Alarm |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Low | [30 empty] | L | 6034 | 2 | LI-6034/2
S-02115 | LAH-6051 | 227.3 | Alarm |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | High | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LAL-6051 | 227.3 | Alarm |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | Low | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LAH-6082 | 227.3 | Alarm |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | High | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | LAL-6082 | 227.3 | Alarm |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | Low | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | LAH-7001 | 227.3 | Alarm |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | High | [30 empty] | L | 7001 |  | LI-7001
S-02115 | LAL-7001 | 227.3 | Alarm |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | Low | [30 empty] | L | 7001 |  | LI-7001
S-02115 | LAH-7002 | 227.3 | Alarm |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | High | [30 empty] | L | 7002 |  | LI-7002
S-02115 | LAL-7002 | 227.3 | Alarm |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | Low | [30 empty] | L | 7002 |  | LI-7002
S-02115 | LAH-7091 | 227.3 | Alarm |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | High | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | LAL-7091 | 227.3 | Alarm |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | Low | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | LAH-7101 | 227.3 | Alarm |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | High | [30 empty] | L | 7101 |  | LI-7101
S-02115 | LAL-7101 | 227.3 | Alarm |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | Low | [30 empty] | L | 7101 |  | LI-7101
S-02115 | LAL-7162 | 227.3 | Alarm |  | U12 |  | TK 7050 |  |  |  |  | bar g |  |  |  | °C | Low | [30 empty] | L | 7162 |  | LI-7162
S-02115 | LAL-7192 | 227.3 | Alarm |  | U13 |  | TK 7060 |  |  |  |  | bar g |  |  |  | °C | Low | [30 empty] | L | 7192 |  | LI-7192
S-02115 | LAL-7212 | 227.3 | Alarm |  | U14 |  | TK 7070 |  |  |  |  | bar g |  |  |  | °C | Low | [30 empty] | L | 7212 |  | LI-7212
S-02115 | LAH-7251 | 227.3 | Alarm |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | High | [30 empty] | L | 7251 |  | LIC-7251
S-02115 | LAL-7251 | 227.3 | Alarm |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | Low | [30 empty] | L | 7251 |  | LIC-7251
S-02115 | LAH-8001 | 227.3 | Alarm |  | U21 | [10 empty] | °C | High | [30 empty] | L | 8001 |  | LA-8001
S-02115 | LAL-8001 | 227.3 | Alarm |  | U21 | [10 empty] | °C | Low | [30 empty] | L | 8001 |  | LA-8001
S-02115 | LALL-8001 | 227.3 | Alarm |  | U21 | [10 empty] | °C | Low-low | [30 empty] | L | 8001 |  | LA-8001
S-02115 | PAH-1001 | 227.3 | Alarm |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | High | [30 empty] | P | 1001 |  | PI-1001
S-02115 | PAL-1001 | 227.3 | Alarm |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Low | [30 empty] | P | 1001 |  | PI-1001
S-02115 | PAL-1006 | 227.3 | Alarm |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Low | [30 empty] | P | 1006 |  | PIC-1006
S-02115 | PAH-1011 | 227.3 | Alarm |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | High | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | PAL-1011 | 227.3 | Alarm |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Low | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | PDAH-1032 | 227.3 | Alarm |  | P04 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | High | [30 empty] | P | 1032 |  | PDI-1032
S-02115 | PAH-1045 | 227.3 | Alarm |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | High | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | PAL-1045 | 227.3 | Alarm |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Low | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | PAH-2001 | 227.3 | Alarm |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | High | [30 empty] | P | 2001 |  | PI-2001
S-02115 | PAL-2001 | 227.3 | Alarm |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Low | [30 empty] | P | 2001 |  | PI-2001
S-02115 | PDAH-2004 | 227.3 | Alarm |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | High | [30 empty] | P | 2004 |  | PDI-2004
S-02115 | PAL-2015 | 227.3 | Alarm |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | Low | [30 empty] | P | 2015 |  | PIC-2015
S-02115 | PDAH-2032 | 227.3 | Alarm |  | P03 |  | 4"-HPS-70-103-F34-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | High | [30 empty] | P | 2032 |  | PDI-2032
S-02115 | PAL-2035 | 227.3 | Alarm |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | P | 2035 |  | PI-2035
S-02115 | PDAL-2036 | 227.3 | Alarm |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PDAH-2051 | 227.3 | Alarm |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | High | I-20 | [29 empty] | P | 2051 |  | PDI-2051
S-02115 | PAH-2073 | 227.3 | Alarm |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | High | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | PAH-2077 | 227.3 | Alarm |  | P09 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | High | [30 empty] | P | 2077 |  | PI-2077
S-02115 | PAL-2077 | 227.3 | Alarm |  | P09 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Low | [30 empty] | P | 2077 |  | PI-2077
S-02115 | PAH-2099 | 227.3 | Alarm |  | P10 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | High | [30 empty] | P | 2099 |  | PI-2099
S-02115 | PAL-2111 | 227.3 | Alarm |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | Low | [30 empty] | P | 2111 |  | PI-2111
S-02115 | PAH-2150 | 227.3 | Alarm |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | High | [30 empty] | P | 2150 |  | PI-2150
S-02115 | PAL-2150 | 227.3 | Alarm |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Low | [30 empty] | P | 2150 |  | PI-2150
S-02115 | PAL-2163 | 227.3 | Alarm |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | Low | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PAH-2224 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PAL-2224 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Low | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PDAH-2252 | 227.3 | Alarm |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | High | [30 empty] | P | 2252 |  | PDI-2252
S-02115 | PAH-2268 | 227.3 | Alarm |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | High | [30 empty] | P | 2268 |  | PI-2268
S-02115 | PAH-2282 | 227.3 | Alarm |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | High | [30 empty] | P | 2282 |  | PI-2282
S-02115 | PDAH-2283 | 227.3 | Alarm |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | High | [30 empty] | P | 2283 |  | PDI-2283
S-02115 | PDAH-2323 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | High | [30 empty] | P | 2323 |  | PDI-2323
S-02115 | PAH-2361 | 227.3 | Alarm |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | High | [30 empty] | P | 2361 |  | PIC-2361
S-02115 | PAL-2363 | 227.3 | Alarm |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Low | [30 empty] | P | 2363 |  | PIC-2363
S-02115 | PAH-2372 | 227.3 | Alarm |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | High | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PAL-2372 | 227.3 | Alarm |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Low | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PAH-2481 | 227.3 | Alarm |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | High | [30 empty] | P | 2481 |  | PIC-2481
S-02115 | PAH-2540 | 227.3 | Alarm |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | High | [30 empty] | P | 2540 |  | PI-2540
S-02115 | PAL-2540 | 227.3 | Alarm |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | Low | [30 empty] | P | 2540 |  | PI-2540
S-02115 | PAH-2554 | 227.3 | Alarm |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | High | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PAL-2554 | 227.3 | Alarm |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Low | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PDAH-2575 | 227.3 | Alarm |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | High | [30 empty] | P | 2575 |  | PDIC-2575
S-02115 | PAH-2579 | 227.3 | Alarm |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | High | [30 empty] | P | 2579 |  | PI-2579
S-02115 | PAL-2579 | 227.3 | Alarm |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | Low | [30 empty] | P | 2579 |  | PI-2579
S-02115 | PAL-2601 | 227.3 | Alarm |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | Low | [30 empty] | P | 2601 |  | PI-2601
S-02115 | PAH-3007 | 227.3 | Alarm |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | High | [30 empty] | P | 3007 |  | PIC-3007
S-02115 | PAL-3007 | 227.3 | Alarm |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Low | [30 empty] | P | 3007 |  | PIC-3007
S-02115 | PAH-3042 | 227.3 | Alarm |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | High | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PAL-3042 | 227.3 | Alarm |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Low | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PDAH-3112 | 227.3 | Alarm |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | High | [30 empty] | P | 3112 |  | PDI-3112
S-02115 | PDAH-3115 | 227.3 | Alarm |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | High | [30 empty] | P | 3115 |  | PDI-3115
S-02115 | PDAH-3117 | 227.3 | Alarm |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | High | [30 empty] | P | 3117 |  | PDI-3117
S-02115 | PAH-3166 | 227.3 | Alarm |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | High | [30 empty] | P | 3166 |  | PIC-3166
S-02115 | PAL-3166 | 227.3 | Alarm |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Low | [30 empty] | P | 3166 |  | PIC-3166
S-02115 | PAH-3194 | 227.3 | Alarm |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | High | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | PAL-3194 | 227.3 | Alarm |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Low | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | PAH-5004 | 227.3 | Alarm |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | High | [30 empty] | P | 5004 |  | PI-5004
S-02115 | PAL-5004 | 227.3 | Alarm |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | Low | [30 empty] | P | 5004 |  | PI-5004
S-02115 | PAH-5047 | 227.3 | Alarm |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | High | [30 empty] | P | 5047 |  | PI-5047
S-02115 | PDAH-5048 | 227.3 | Alarm |  | P30 | [10 empty] | °C | High | [30 empty] | P | 5048 |  | PDI-5048
S-02115 | PDAH-5050 | 227.3 | Alarm |  | P30 | [10 empty] | °C | High | [30 empty] | P | 5050 |  | PDI-5050
S-02115 | PAL-5083 | 227.3 | Alarm |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | Low | [30 empty] | P | 5083 |  | PI-5083
S-02115 | PAH-5091 | 227.3 | Alarm |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | High | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | PAL-5093 | 227.3 | Alarm |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | Low | [30 empty] | P | 5093 |  | PI-5093
S-02115 | PAL-5139 | 227.3 | Alarm |  | P33 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | Low | [30 empty] | P | 5139 |  | PI-5139
S-02115 | PDAH-5167 | 227.3 | Alarm |  | P34 | [10 empty] | °C | High | [30 empty] | P | 5167 |  | PDI-5167
S-02115 | PDAH-5169 | 227.3 | Alarm |  | P34 | [10 empty] | °C | High | [30 empty] | P | 5169 |  | PDI-5169
S-02115 | PDAH-5171 | 227.3 | Alarm |  | P34 | [10 empty] | °C | High | [30 empty] | P | 5171 |  | PDI-5171
S-02115 | PDAH-5173 | 227.3 | Alarm |  | P34 | [10 empty] | °C | High | [30 empty] | P | 5173 |  | PDI-5173
S-02115 | PAH-5207 | 227.3 | Alarm |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | High | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PAL-5207 | 227.3 | Alarm |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Low | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PAL-5219 | 227.3 | Alarm |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | Low | [30 empty] | P | 5219 |  | PI-5219
S-02115 | PAL-5240 | 227.3 | Alarm |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | Low | [30 empty] | P | 5240 |  | PI-5240
S-02115 | PDAH-5253 | 227.3 | Alarm |  | P38 | [10 empty] | °C | High | [30 empty] | P | 5253 |  | PDI-5253
S-02115 | PDAH-5255 | 227.3 | Alarm |  | P38 | [10 empty] | °C | High | [30 empty] | P | 5255 |  | PDI-5255
S-02115 | PDAH-5257 | 227.3 | Alarm |  | P38 | [10 empty] | °C | High | [30 empty] | P | 5257 |  | PDI-5257
S-02115 | PDAH-5259 | 227.3 | Alarm |  | P38 | [10 empty] | °C | High | [30 empty] | P | 5259 |  | PDI-5259
S-02115 | PAH-5307 | 227.3 | Alarm |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | High | [30 empty] | P | 5307 |  | PI-5307
S-02115 | PAL-5307 | 227.3 | Alarm |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | Low | [30 empty] | P | 5307 |  | PI-5307
S-02115 | PAL-5335 | 227.3 | Alarm |  | P40 |  | 6"-PMP-50-140-D24-P |  |  | 19 | 3.6 | bar g |  | 101 | 165 | °C | Low | [30 empty] | P | 5335 |  | PI-5335
S-02115 | PAL-5367 | 227.3 | Alarm |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | Low | [30 empty] | P | 5367 |  | PI-5367
S-02115 | PDAH-5385 | 227.3 | Alarm |  | P42 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | High | [30 empty] | P | 5385 |  | PDI-5385
S-02115 | PAH-5398 | 227.3 | Alarm |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | High | [30 empty] | P | 5398 |  | PI-5398
S-02115 | PAL-5398 | 227.3 | Alarm |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | Low | [30 empty] | P | 5398 |  | PI-5398
S-02115 | PAH-5415 | 227.3 | Alarm |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | High | [30 empty] | P | 5415 |  | PI-5415
S-02115 | PAL-5415 | 227.3 | Alarm |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | Low | [30 empty] | P | 5415 |  | PI-5415
S-02115 | PAH-5421 | 227.3 | Alarm |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | High | [30 empty] | P | 5421 |  | PI-5421
S-02115 | PAH-5448 | 227.3 | Alarm |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | High | [30 empty] | P | 5448 |  | PI-5448
S-02115 | PAL-5448 | 227.3 | Alarm |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | Low | [30 empty] | P | 5448 |  | PI-5448
S-02115 | PAL-6010 | 227.3 | Alarm |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | Low | [30 empty] | P | 6010 |  | PI-6010
S-02115 | PDAH-6028 | 227.3 | Alarm |  | P06 |  | 3"-PRC-20-107-G40-H |  |  | 71 | 45 | bar g |  | 115 | 180 | °C | High | [30 empty] | P | 6028 |  | PDI-6028
S-02115 | PAH-7004 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | High | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | PAL-7004 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | PAH-7034 | 227.3 | Alarm |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | High | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | PAL-7034 | 227.3 | Alarm |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Low | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | PAH-7056 | 227.3 | Alarm |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | High | [30 empty] | P | 7056 |  | PIC-7056
S-02115 | PAH-7094 | 227.3 | Alarm |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | High | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | PAL-7094 | 227.3 | Alarm |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | Low | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | PAL-7112 | 227.3 | Alarm |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Low | [30 empty] | P | 7112 |  | PI-7112
S-02115 | PAL-7116 | 227.3 | Alarm |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Low | [30 empty] | P | 7116 |  | PI-7116
S-02115 | PAL-7120 | 227.3 | Alarm |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Low | [30 empty] | P | 7120 |  | PI-7120
S-02115 | PAL-7127 | 227.3 | Alarm |  | U10 |  | 12"-BFW-70-140-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Low | [30 empty] | P | 7127 |  | PI-7127
S-02115 | PAL-7141 | 227.3 | Alarm |  | U11 |  | 8"-BFW-70-164-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Low | [30 empty] | P | 7141 |  | PIC-7141
S-02115 | QAH-2535 | 227.3 | Alarm |  | U01 | [10 empty] | °C | High | [30 empty] | Q | 2535 |  | QIC-2535
S-02115 | QDAH-2535 | 227.3 | Alarm |  | U01 | [10 empty] | °C | Deviation | [30 empty] | Q | 2535 |  | QIC-2535
S-02115 | SAH-2118 | 227.3 | Alarm |  | P11 | [10 empty] | °C | High | [30 empty] | S | 2118 |  | SI-2118
S-02115 | SAL-2118 | 227.3 | Alarm |  | P11 | [10 empty] | °C | Low | [30 empty] | S | 2118 |  | SI-2118
S-02115 | SAH-2168 | 227.3 | Alarm |  | P12 | [10 empty] | °C | High | [30 empty] | S | 2168 |  | SI-2168
S-02115 | SAL-2168 | 227.3 | Alarm |  | P12 | [10 empty] | °C | Low | [30 empty] | S | 2168 |  | SI-2168
S-02115 | TAL-1012 | 227.3 | Alarm |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Low | [30 empty] | T | 1012 |  | TI-1012
S-02115 | TAH-1034 | 227.3 | Alarm |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | High | [30 empty] | T | 1034 |  | TI-1034
S-02115 | TAL-1034 | 227.3 | Alarm |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Low | [30 empty] | T | 1034 |  | TI-1034
S-02115 | TAH-1035 | 227.3 | Alarm |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | High | [30 empty] | T | 1035 |  | TI-1035
S-02115 | TAL-1035 | 227.3 | Alarm |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Low | [30 empty] | T | 1035 |  | TI-1035
S-02115 | TAH-1047 | 227.3 | Alarm |  | P04 |  | 8"-FLG-10-113-B24-P |  |  | 5 |  | bar g |  |  | 410 | °C | High | [30 empty] | T | 1047 |  | TI-1047
S-02115 | TAH-2001 | 227.3 | Alarm |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | High | [30 empty] | T | 2001 |  | TI-2001
S-02115 | TAL-2001 | 227.3 | Alarm |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Low | [30 empty] | T | 2001 |  | TI-2001
S-02115 | TAH-2044 | 227.3 | Alarm |  | P03 |  | 6"-VA-20-104-F70-P |  |  | 45 |  | bar g |  |  | 255 | °C | High | [30 empty] | T | 2044 |  | TI-2044
S-02115 | TAL-2046 | 227.3 | Alarm |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | Low | [30 empty] | T | 2046 |  | TI-2046
S-02115 | TAL-2047 | 227.3 | Alarm |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Low | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TAH-2050 | 227.3 | Alarm |  | P03 |  | 2"-VA-20-101-F70-P |  |  | 4.5 |  | bar g |  |  | 255 | °C | High | [30 empty] | T | 2050 |  | TI-2050
S-02115 | TAL-2112 | 227.3 | Alarm |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | Low | [30 empty] | T | 2112 |  | TI-2112
S-02115 | TAH-2148 | 227.3 | Alarm |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | High | [30 empty] | T | 2148 |  | TI-2148
S-02115 | TAH-2149 | 227.3 | Alarm |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | High | [30 empty] | T | 2149 |  | TI-2149
S-02115 | TAL-2155 | 227.3 | Alarm |  | P12 |  | WHS |  |  |  | -70 | mbar g |  | 150 |  | °C | Low | [30 empty] | T | 2155 |  | TI-2155
S-02115 | TAH-2220 | 227.3 | Alarm |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | High | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | TAL-2220 | 227.3 | Alarm |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Low | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | TAH-2221 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TAH-2226 | 227.3 | Alarm |  | P13 |  | WHS |  |  |  | -0.01 | bar g |  | 1093 |  | °C | High | [30 empty] | T | 2226 |  | TI-2226
S-02115 | TAL-2232 | 227.3 | Alarm |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | Low | [30 empty] | T | 2232 |  | TIC-2232
S-02115 | TAH-2234 | 227.3 | Alarm |  | P13 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | High | [30 empty] | T | 2234 |  | TI-2234
S-02115 | TAH-2253 | 227.3 | Alarm |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | High | [30 empty] | T | 2253 |  | TIC-2253
S-02115 | TAL-2253 | 227.3 | Alarm |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | Low | [30 empty] | T | 2253 |  | TIC-2253
S-02115 | TAH-2268 | 227.3 | Alarm |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | High | [30 empty] | T | 2268 |  | TI-2268
S-02115 | TAL-2268 | 227.3 | Alarm |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | Low | [30 empty] | T | 2268 |  | TI-2268
S-02115 | TAH-2295 | 227.3 | Alarm |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | T | 2295 |  | TI-2295
S-02115 | TDAH-2295 | 227.3 | Alarm |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Rate of change high | [30 empty] | T | 2295 |  | TI-2295
S-02115 | TAH-2297 | 227.3 | Alarm |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | High | [30 empty] | T | 2297 |  | TI-2297
S-02115 | TDAH-2297 | 227.3 | Alarm |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Rate of change high | [30 empty] | T | 2297 |  | TI-2297
S-02115 | TAH-2303 | 227.3 | Alarm |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | High | [30 empty] | T | 2303 |  | TI-2303
S-02115 | TAH-2304 | 227.3 | Alarm |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | High | [30 empty] | T | 2304 |  | TI-2304
S-02115 | TAH-2305 | 227.3 | Alarm |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | High | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TAH-2325 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | High | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TAL-2325 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | Low | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TAH-2326 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | High | [30 empty] | T | 2326 |  | TI-2326
S-02115 | TAH-2327 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | High | [30 empty] | T | 2327 |  | TI-2327
S-02115 | TAH-2328 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | High | [30 empty] | T | 2328 |  | TI-2328
S-02115 | TAH-2329 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | High | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TAH-2330 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | High | [30 empty] | T | 2330 |  | TI-2330
S-02115 | TAH-2331 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | High | [30 empty] | T | 2331 |  | TI-2331
S-02115 | TAH-2332 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C | High | [30 empty] | T | 2332 |  | TI-2332
S-02115 | TAH-2333 | 227.3 | Alarm |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | High | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TAH-2334 | 227.3 | Alarm |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | High | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TAH-2351 | 227.3 | Alarm |  | P17 |  | 24"-RFG-20-110-D34-H |  |  | 30 | 26.3 | bar g |  | 360 | 390 | °C | High | [30 empty] | T | 2351 |  | TI-2351
S-02115 | TAH-2352 | 227.3 | Alarm |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | High | [30 empty] | T | 2352 |  | TI-2352
S-02115 | TAH-2353 | 227.3 | Alarm |  | P17 |  | 24"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | High | [30 empty] | T | 2353 |  | TI-2353
S-02115 | TAH-2354 | 227.3 | Alarm |  | P17 |  | 42"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | High | [30 empty] | T | 2354 |  | TI-2354
S-02115 | TAH-2355 | 227.3 | Alarm |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | High | [30 empty] | T | 2355 |  | TI-2355
S-02115 | TAH-2356 | 227.3 | Alarm |  | P17 |  | 24"-HHPS-20-117-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | High | [30 empty] | T | 2356 |  | TI-2356
S-02115 | TAH-2360 | 227.3 | Alarm |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | High | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TAL-2360 | 227.3 | Alarm |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Low | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TAH-2371 | 227.3 | Alarm |  | P18 |  | 12"-BFW-20-102-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | High | [30 empty] | T | 2371 |  | TI-2371
S-02115 | TAH-2457 | 227.3 | Alarm |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | High | [30 empty] | T | 2457 |  | TIC-2457
S-02115 | TAH-2476 | 227.3 | Alarm |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | High | [30 empty] | T | 2476 |  | TI-2476
S-02115 | TAL-2540 | 227.3 | Alarm |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | Low | [30 empty] | T | 2540 |  | TI-2540
S-02115 | TAH-2572 | 227.3 | Alarm |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | High | [30 empty] | T | 2572 |  | TI-2572
S-02115 | TAH-2579 | 227.3 | Alarm |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | High | [30 empty] | T | 2579 |  | TI-2579
S-02115 | TAH-3045 | 227.3 | Alarm |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | High | [30 empty] | T | 3045 |  | TI-3045
S-02115 | TAH-3072 | 227.3 | Alarm |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | High | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TAH-3073 | 227.3 | Alarm |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | High | [30 empty] | T | 3073 |  | TI-3073
S-02115 | TAL-3073 | 227.3 | Alarm |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | Low | [30 empty] | T | 3073 |  | TI-3073
S-02115 | TAH-3076 | 227.3 | Alarm |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | High | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TAH-3077 | 227.3 | Alarm |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | High | [30 empty] | T | 3077 |  | TI-3077
S-02115 | TAL-3077 | 227.3 | Alarm |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | Low | [30 empty] | T | 3077 |  | TI-3077
S-02115 | TAH-3080 | 227.3 | Alarm |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | High | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TAH-3081 | 227.3 | Alarm |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | High | [30 empty] | T | 3081 |  | TI-3081
S-02115 | TAL-3081 | 227.3 | Alarm |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | Low | [30 empty] | T | 3081 |  | TI-3081
S-02115 | TAH-3084 | 227.3 | Alarm |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | High | [30 empty] | T | 3084 |  | TI-3084
S-02115 | TAH-3113 | 227.3 | Alarm |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | High | [30 empty] | T | 3113 |  | TIC-3113
S-02115 | TAH-3116 | 227.3 | Alarm |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | High | [30 empty] | T | 3116 |  | TIC-3116
S-02115 | TAH-3118 | 227.3 | Alarm |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | High | [30 empty] | T | 3118 |  | TIC-3118
S-02115 | TAH-3142 | 227.3 | Alarm |  | P26 |  | 24"-SG-30-122-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | High | [30 empty] | T | 3142 |  | TI-3142
S-02115 | TAH-3145 | 227.3 | Alarm |  | P26 |  | 24"-SG-30-123-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | High | [30 empty] | T | 3145 |  | TI-3145
S-02115 | TAH-3148 | 227.3 | Alarm |  | P26 |  | 24"-SG-30-124-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | High | [30 empty] | T | 3148 |  | TI-3148
S-02115 | TAH-3164 | 227.3 | Alarm |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | High | [30 empty] | T | 3164 |  | TI-3164
S-02115 | TAH-5064 | 227.3 | Alarm |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | High | [30 empty] | T | 5064 |  | TIC-5064
S-02115 | TAH-5261 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5261 |  | TI-5261
S-02115 | TAL-5261 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5261 |  | TI-5261
S-02115 | TAH-5262 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5262 |  | TI-5262
S-02115 | TAL-5262 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5262 |  | TI-5262
S-02115 | TAH-5263 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5263 |  | TI-5263
S-02115 | TAL-5263 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5263 |  | TI-5263
S-02115 | TAH-5264 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5264 |  | TI-5264
S-02115 | TAL-5264 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5264 |  | TI-5264
S-02115 | TAH-5265 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5265 |  | TI-5265
S-02115 | TAL-5265 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5265 |  | TI-5265
S-02115 | TAH-5266 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5266 |  | TIC-5266
S-02115 | TAL-5266 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5266 |  | TIC-5266
S-02115 | TAH-5267 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5267 |  | TIC-5267
S-02115 | TAL-5267 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5267 |  | TIC-5267
S-02115 | TAH-5268 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5268 |  | TIC-5268
S-02115 | TAL-5268 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5268 |  | TIC-5268
S-02115 | TAH-5269 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | High | [30 empty] | T | 5269 |  | TI-5269
S-02115 | TAL-5269 | 227.3 | Alarm |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | Low | [30 empty] | T | 5269 |  | TI-5269
S-02115 | TAH-5277 | 227.3 | Alarm |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | High | [30 empty] | T | 5277 |  | TIC-5277
S-02115 | TAH-5280 | 227.3 | Alarm |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | High | [30 empty] | T | 5280 |  | TI-5280
S-02115 | TAL-5280 | 227.3 | Alarm |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | Low | [30 empty] | T | 5280 |  | TI-5280
S-02115 | TAH-5381 | 227.3 | Alarm |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | High | [30 empty] | T | 5381 |  | TI-5381
S-02115 | TAH-5443 | 227.3 | Alarm |  | P45 |  | 2"-LOS-50-114-B24-N |  |  | 7.5 | 2 | bar g |  | 48 | 75 | °C | High | [30 empty] | T | 5443 |  | TI-5443
S-02115 | TAH-7002 | 227.3 | Alarm |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | High | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | TAL-7002 | 227.3 | Alarm |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | TAH-7003 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | High | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | TAL-7003 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | TAH-7004 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | High | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | TAL-7004 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | TAH-7007 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | High | [30 empty] | T | 7007 |  | TI-7007
S-02115 | TAL-7007 | 227.3 | Alarm |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Low | [30 empty] | T | 7007 |  | TI-7007
S-02115 | TAH-7021 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | High | [30 empty] | T | 7021 |  | TI-7021
S-02115 | TAL-7021 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | Low | [30 empty] | T | 7021 |  | TI-7021
S-02115 | TAH-7025 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | High | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | TAL-7025 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | Low | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | TAH-7026 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | High | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | TAL-7026 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | Low | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | TAH-7027 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | High | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | TAL-7027 | 227.3 | Alarm |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | Low | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | TAH-7031 | 227.3 | Alarm |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | High | [30 empty] | T | 7031 |  | TI-7031
S-02115 | TAH-7032 | 227.3 | Alarm |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | High | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | TAL-7032 | 227.3 | Alarm |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | Low | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | TAH-7033 | 227.3 | Alarm |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | High | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | TAL-7033 | 227.3 | Alarm |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | Low | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | TAH-7052 | 227.3 | Alarm |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | High | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | TAL-7052 | 227.3 | Alarm |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | Low | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | TAH-7053 | 227.3 | Alarm |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | High | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | TAL-7053 | 227.3 | Alarm |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | Low | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | TAH-7056 | 227.3 | Alarm |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | High | [30 empty] | T | 7056 |  | TI-7056
S-02115 | TAH-7071 | 227.3 | Alarm |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | High | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TAL-7071 | 227.3 | Alarm |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Low | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | XA-2124 | 227.3 | Alarm |  | P11 | [10 empty] | °C | Common | [30 empty] | X | 2124 |  | XA-2124
S-02115 | XA-2159 | 227.3 | Alarm |  | P12 | [10 empty] | °C | Common | [30 empty] | X | 2159 |  | XA-2159
S-02115 | XA-2410 | 227.3 | Alarm |  | P19 | [10 empty] | °C | Common | [30 empty] | X | 2410 |  | XA-2410
S-02115 | XA-2414 | 227.3 | Alarm |  | P19 | [10 empty] | °C | Common | [30 empty] | X | 2414 |  | XA-2414
S-02115 | XA-2447 | 227.3 | Alarm |  | P20 | [10 empty] | °C | Common | [30 empty] | X | 2447 |  | XA-2447
S-02115 | XA-2451 | 227.3 | Alarm |  | P20 | [10 empty] | °C | Common | [30 empty] | X | 2451 |  | XA-2451
S-02115 | XA-2487 | 227.3 | Alarm |  | P21 | [10 empty] | °C | Common | [30 empty] | X | 2487 |  | XA-2487
S-02115 | XA-2491 | 227.3 | Alarm |  | P21 | [10 empty] | °C | Common | [30 empty] | X | 2491 |  | XA-2491
S-02115 | XA-2577 | 227.3 | Alarm |  | U02 | [10 empty] | °C | Common | [30 empty] | X | 2577 |  | XA-2577
S-02115 | XA-3141 | 227.3 | Alarm |  | P26 | [10 empty] | °C | Common | [30 empty] | X | 3141 |  | XA-3141
S-02115 | XA-3144 | 227.3 | Alarm |  | P26 | [10 empty] | °C | Common | [30 empty] | X | 3144 |  | XA-3144
S-02115 | XA-3147 | 227.3 | Alarm |  | P26 | [10 empty] | °C | Common | [30 empty] | X | 3147 |  | XA-3147
S-02115 | XA-5013 | 227.3 | Alarm |  | P29 | [10 empty] | °C | Common | [30 empty] | X | 5013 |  | XA-5013
S-02115 | XA-5017 | 227.3 | Alarm |  | P29 | [10 empty] | °C | Common | [30 empty] | X | 5017 |  | XA-5017
S-02115 | XA-5077 | 227.3 | Alarm |  | P31 | [10 empty] | °C | Common | [30 empty] | X | 5077 |  | XA-5077
S-02115 | XA-5081 | 227.3 | Alarm |  | P31 | [10 empty] | °C | Common | [30 empty] | X | 5081 |  | XA-5081
S-02115 | XA-5092 | 227.3 | Alarm |  | P32 | [10 empty] | °C | Common | [30 empty] | X | 5092 |  | XA-5092
S-02115 | XA-5101 | 227.3 | Alarm |  | P32 | [10 empty] | °C | Common | [30 empty] | X | 5101 |  | XA-5101
S-02115 | XA-5105 | 227.3 | Alarm |  | P32 | [10 empty] | °C | Common | [30 empty] | X | 5105 |  | XA-5105
S-02115 | XA-5133 | 227.3 | Alarm |  | P33 | [10 empty] | °C | Common | [30 empty] | X | 5133 |  | XA-5133
S-02115 | XA-5137 | 227.3 | Alarm |  | P33 | [10 empty] | °C | Common | [30 empty] | X | 5137 |  | XA-5137
S-02115 | XA-5201 | 227.3 | Alarm |  | P36 | [10 empty] | °C | Common | [30 empty] | X | 5201 |  | XA-5201
S-02115 | XA-5212 | 227.3 | Alarm |  | P36 | [10 empty] | °C | Common | [30 empty] | X | 5212 |  | XA-5212
S-02115 | XA-5216 | 227.3 | Alarm |  | P36 | [10 empty] | °C | Common | [30 empty] | X | 5216 |  | XA-5216
S-02115 | XA-5232 | 227.3 | Alarm |  | U15 | [10 empty] | °C | Common | [30 empty] | X | 5232 |  | XA-5232
S-02115 | XA-5233 | 227.3 | Alarm |  | P37 | [10 empty] | °C | Common | [30 empty] | X | 5233 |  | XA-5233
S-02115 | XA-5236 | 227.3 | Alarm |  | U15 | [10 empty] | °C | Common | [30 empty] | X | 5236 |  | XA-5236
S-02115 | XA-5237 | 227.3 | Alarm |  | P37 | [10 empty] | °C | Common | [30 empty] | X | 5237 |  | XA-5237
S-02115 | XA-5329 | 227.3 | Alarm |  | P40 | [10 empty] | °C | Common | [30 empty] | X | 5329 |  | XA-5329
S-02115 | XA-5333 | 227.3 | Alarm |  | P40 | [10 empty] | °C | Common | [30 empty] | X | 5333 |  | XA-5333
S-02115 | XA-5353 | 227.3 | Alarm |  | P41 | [10 empty] | °C | Common | [30 empty] | X | 5353 |  | XA-5353
S-02115 | XA-5357 | 227.3 | Alarm |  | P41 | [10 empty] | °C | Common | [30 empty] | X | 5357 |  | XA-5357
S-02115 | XA-5361 | 227.3 | Alarm |  | P41 | [10 empty] | °C | Common | [30 empty] | X | 5361 |  | XA-5361
S-02115 | XA-5365 | 227.3 | Alarm |  | P41 | [10 empty] | °C | Common | [30 empty] | X | 5365 |  | XA-5365
S-02115 | XA-5368 | 227.3 | Alarm |  | P41 | [10 empty] | °C | Common | [30 empty] | X | 5368 |  | XA-5368
S-02115 | XA-5425 | 227.3 | Alarm |  | P44 | [10 empty] | °C | Common | [30 empty] | X | 5425 |  | XA-5425
S-02115 | XA-5429 | 227.3 | Alarm |  | P44 | [10 empty] | °C | Common | [30 empty] | X | 5429 |  | XA-5429
S-02115 | XA-5455 | 227.3 | Alarm |  | P45 | [10 empty] | °C | Common | [30 empty] | X | 5455 |  | XA-5455
S-02115 | XA-5459 | 227.3 | Alarm |  | P45 | [10 empty] | °C | Common | [30 empty] | X | 5459 |  | XA-5459
S-02115 | XA-5511 | 227.3 | Alarm |  | U24 | [10 empty] | °C | Common | [30 empty] | X | 5511 |  | XA-5511
S-02115 | XA-5512 | 227.3 | Alarm |  | U24 | [10 empty] | °C | Common | [30 empty] | X | 5512 |  | XA-5512
S-02115 | XA-6004 | 227.3 | Alarm |  | P05 | [10 empty] | °C | Common | [30 empty] | X | 6004 |  | XA-6004
S-02115 | XA-6008 | 227.3 | Alarm |  | P05 | [10 empty] | °C | Common | [30 empty] | X | 6008 |  | XA-6008
S-02115 | XA-6062 | 227.3 | Alarm |  | P07 | [10 empty] | °C | Common | [30 empty] | X | 6062 |  | XA-6062
S-02115 | XA-6066 | 227.3 | Alarm |  | P07 | [10 empty] | °C | Common | [30 empty] | X | 6066 |  | XA-6066
S-02115 | XA-7005 | 227.3 | Alarm |  | U18 | [10 empty] | °C | Common | [30 empty] | X | 7005 |  | XA-7005
S-02115 | XA-7006 | 227.3 | Alarm |  | U18 | [10 empty] | °C | Common | [30 empty] | X | 7006 |  | XA-7006
S-02115 | XA-7101 | 227.3 | Alarm |  | U22 | [10 empty] | °C | Common | [30 empty] | X | 7101 |  | XA-7101
S-02115 | XA-7103 | 227.3 | Alarm |  | U22 | [10 empty] | °C | Common | [30 empty] | X | 7103 |  | XA-7103
S-02115 | XA-7122 | 227.3 | Alarm |  | U10 | [10 empty] | °C | Common | [30 empty] | X | 7122 |  | XA-7122
S-02115 | XA-7163 | 227.3 | Alarm |  | U12 | [10 empty] | °C | Common | [30 empty] | X | 7163 |  | XA-7163
S-02115 | XA-7166 | 227.3 | Alarm |  | U12 | [10 empty] | °C | Common | [30 empty] | X | 7166 |  | XA-7166
S-02115 | XA-7169 | 227.3 | Alarm |  | U12 | [10 empty] | °C | Common | [30 empty] | X | 7169 |  | XA-7169
S-02115 | XA-7172 | 227.3 | Alarm |  | U12 | [10 empty] | °C | Common | [30 empty] | X | 7172 |  | XA-7172
S-02115 | XA-7193 | 227.3 | Alarm |  | U13 | [10 empty] | °C | Common | [30 empty] | X | 7193 |  | XA-7193
S-02115 | XA-7196 | 227.3 | Alarm |  | U13 | [10 empty] | °C | Common | [30 empty] | X | 7196 |  | XA-7196
S-02115 | XA-7213 | 227.3 | Alarm |  | U14 | [10 empty] | °C | Common | [30 empty] | X | 7213 |  | XA-7213
S-02115 | XA-7216 | 227.3 | Alarm |  | U14 | [10 empty] | °C | Common | [30 empty] | X | 7216 |  | XA-7216
S-02115 | FALL-6070 | 227.35 | Interlock Circuit |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | I-20 | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | LALL-5447 | 227.35 | Interlock Circuit |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | I-52 | [30 empty] | L | 5447 |  | LI-5447
S-02115 | LAHH-6083 | 227.35 | Interlock Circuit |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | I-36 | [30 empty] | L | 6083 |  | LI-6083
S-02115 | LALL-6083 | 227.35 | Interlock Circuit |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | I-37 | [30 empty] | L | 6083 |  | LI-6083
S-02115 | LAHH-7102 | 227.35 | Interlock Circuit |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | I-37 | [30 empty] | L | 7102 |  | LI-7102
S-02115 | LALL-7102 | 227.35 | Interlock Circuit |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | I-38 | [30 empty] | L | 7102 |  | LI-7102
S-02115 | MA-2577 | 227.35 | Interlock Circuit |  | U02 | [10 empty] | °C | I-16 | [30 empty] | M | 2577 |  | ML-2577
S-02115 | PAHH-2224 | 227.35 | Interlock Circuit |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | I-15 | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PDAHH-2575 | 227.35 | Interlock Circuit |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | I-16 | [30 empty] | P | 2575 |  | PDIC-2575
S-02115 | TALL-2232 | 227.35 | Interlock Circuit |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | I-17 | [30 empty] | T | 2232 |  | TIC-2232
S-02115 | TAHH-2579 | 227.35 | Interlock Circuit |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | I-16 | [30 empty] | T | 2579 |  | TI-2579
S-02115 | TAHH-3072 | 227.35 | Interlock Circuit |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | I-45 | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TAHH-3076 | 227.35 | Interlock Circuit |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | I-46 | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TAHH-3080 | 227.35 | Interlock Circuit |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | I-47 | [30 empty] | T | 3080 |  | TI-3080
S-02115 | FZLL-2007 | 227.4 | Digital Indicator |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Valve closed | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FZLL-2009 | 227.4 | Digital Indicator |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Valve closed | [30 empty] | F | 2009 |  | FIC-2009
S-02115 | FZLL-2061 | 227.4 | Digital Indicator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Valve closed | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FZLL-2072 | 227.4 | Digital Indicator |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Valve closed | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FZLL-2079 | 227.4 | Digital Indicator |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Valve closed | [30 empty] | F | 2079 |  | FIC-2079
S-02115 | FZLL-2091 | 227.4 | Digital Indicator |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Valve closed | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | FZLL-2150 | 227.4 | Digital Indicator |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Valve closed | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FZLL-2536 | 227.4 | Digital Indicator |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Valve closed | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | FZLL-3171 | 227.4 | Digital Indicator |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Valve closed | [30 empty] | F | 3171 |  | FIC-3171
S-02115 | HZLH-1003 | 227.4 | Digital Indicator |  | P01 | [10 empty] | °C | Valve open | [30 empty] | H | 1003 |  | HS-1003
S-02115 | HZLL-1003 | 227.4 | Digital Indicator |  | P01 | [10 empty] | °C | Valve closed | [30 empty] | H | 1003 |  | HS-1003
S-02115 | HZLH-2003 | 227.4 | Digital Indicator |  | P02 | [10 empty] | °C | Valve open | [30 empty] | H | 2003 |  | HS-2003
S-02115 | HZLL-2003 | 227.4 | Digital Indicator |  | P02 | [10 empty] | °C | Valve closed | [30 empty] | H | 2003 |  | HS-2003
S-02115 | HZLH-2098 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve open | [30 empty] | H | 2098 |  | HS-2098
S-02115 | HZLL-2098 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve closed | [30 empty] | H | 2098 |  | HS-2098
S-02115 | HZLL/1-2225 | 227.4 | Digital Indicator |  | P13 | [10 empty] | °C | Valve closed | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | HZLL/2-2225 | 227.4 | Digital Indicator |  | P13 | [10 empty] | °C | Valve closed | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | LZLL-2403 | 227.4 | Digital Indicator |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Valve closed | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LZLL/A-3161 | 227.4 | Digital Indicator |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | Valve closed | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LZLL/B-3161 | 227.4 | Digital Indicator |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | Valve closed | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LZLL-5501 | 227.4 | Digital Indicator |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | Valve closed | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | ML-2124 | 227.4 | Digital Indicator |  | P11 | [10 empty] | °C | Running | [30 empty] | M | 2124 |  | ML-2124
S-02115 | ML-2159 | 227.4 | Digital Indicator |  | P12 | [10 empty] | °C | Running | [30 empty] | M | 2159 |  | ML-2159
S-02115 | ML-2410 | 227.4 | Digital Indicator |  | P19 | [10 empty] | °C | Running | [30 empty] | M | 2410 |  | ML-2410
S-02115 | ML-2414 | 227.4 | Digital Indicator |  | P19 | [10 empty] | °C | Running | [30 empty] | M | 2414 |  | ML-2414
S-02115 | ML-2447 | 227.4 | Digital Indicator |  | P20 | [10 empty] | °C | Running | [30 empty] | M | 2447 |  | ML-2447
S-02115 | ML-2451 | 227.4 | Digital Indicator |  | P20 | [10 empty] | °C | Running | [30 empty] | M | 2451 |  | ML-2451
S-02115 | ML-2471 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Running | [30 empty] | M | 2471 |  | ML-2471
S-02115 | ML-2487 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Running | [30 empty] | M | 2487 |  | ML-2487
S-02115 | ML-2491 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Running | [30 empty] | M | 2491 |  | ML-2491
S-02115 | ML-2577 | 227.4 | Digital Indicator |  | U02 | [10 empty] | °C | Running | [30 empty] | M | 2577 |  | ML-2577
S-02115 | ML-3141 | 227.4 | Digital Indicator |  | P26 | [10 empty] | °C | Running | [30 empty] | M | 3141 |  | ML-3141
S-02115 | ML-3144 | 227.4 | Digital Indicator |  | P26 | [10 empty] | °C | Running | [30 empty] | M | 3144 |  | ML-3144
S-02115 | ML-3147 | 227.4 | Digital Indicator |  | P26 | [10 empty] | °C | Running | [30 empty] | M | 3147 |  | ML-3147
S-02115 | ML-5013 | 227.4 | Digital Indicator |  | P29 | [10 empty] | °C | Running | [30 empty] | M | 5013 |  | ML-5013
S-02115 | ML-5017 | 227.4 | Digital Indicator |  | P29 | [10 empty] | °C | Running | [30 empty] | M | 5017 |  | ML-5017
S-02115 | ML-5077 | 227.4 | Digital Indicator |  | P31 | [10 empty] | °C | Running | [30 empty] | M | 5077 |  | ML-5077
S-02115 | ML-5081 | 227.4 | Digital Indicator |  | P31 | [10 empty] | °C | Running | [30 empty] | M | 5081 |  | ML-5081
S-02115 | ML-5092 | 227.4 | Digital Indicator |  | P32 | [10 empty] | °C | Running | [30 empty] | M | 5092 |  | ML-5092
S-02115 | ML-5101 | 227.4 | Digital Indicator |  | P32 | [10 empty] | °C | Running | [30 empty] | M | 5101 |  | ML-5101
S-02115 | ML-5105 | 227.4 | Digital Indicator |  | P32 | [10 empty] | °C | Running | [30 empty] | M | 5105 |  | ML-5105
S-02115 | ML-5133 | 227.4 | Digital Indicator |  | P33 | [10 empty] | °C | Running | [30 empty] | M | 5133 |  | ML-5133
S-02115 | ML-5137 | 227.4 | Digital Indicator |  | P33 | [10 empty] | °C | Running | [30 empty] | M | 5137 |  | ML-5137
S-02115 | ML-5201 | 227.4 | Digital Indicator |  | P36 | [10 empty] | °C | Running | [30 empty] | M | 5201 |  | ML-5201
S-02115 | ML-5212 | 227.4 | Digital Indicator |  | P36 | [10 empty] | °C | Running | [30 empty] | M | 5212 |  | ML-5212
S-02115 | ML-5216 | 227.4 | Digital Indicator |  | P36 | [10 empty] | °C | Running | [30 empty] | M | 5216 |  | ML-5216
S-02115 | ML-5231 | 227.4 | Digital Indicator |  | U15 | [10 empty] | °C | Running | [30 empty] | M | 5231 |  | ML-5231
S-02115 | ML-5232 | 227.4 | Digital Indicator |  | U15 | [10 empty] | °C | Running | [30 empty] | M | 5232 |  | ML-5232
S-02115 | ML-5233 | 227.4 | Digital Indicator |  | P37 | [10 empty] | °C | Running | [30 empty] | M | 5233 |  | ML-5233
S-02115 | ML-5236 | 227.4 | Digital Indicator |  | U15 | [10 empty] | °C | Running | [30 empty] | M | 5236 |  | ML-5236
S-02115 | ML-5237 | 227.4 | Digital Indicator |  | P37 | [10 empty] | °C | Running | [30 empty] | M | 5237 |  | ML-5237
S-02115 | ML-5329 | 227.4 | Digital Indicator |  | P40 | [10 empty] | °C | Running | [30 empty] | M | 5329 |  | ML-5329
S-02115 | ML-5333 | 227.4 | Digital Indicator |  | P40 | [10 empty] | °C | Running | [30 empty] | M | 5333 |  | ML-5333
S-02115 | ML-5353 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Running | [30 empty] | M | 5353 |  | ML-5353
S-02115 | ML-5357 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Running | [30 empty] | M | 5357 |  | ML-5357
S-02115 | ML-5361 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Running | [30 empty] | M | 5361 |  | ML-5361
S-02115 | ML-5365 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Running | [30 empty] | M | 5365 |  | ML-5365
S-02115 | ML-5368 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Running | [30 empty] | M | 5368 |  | ML-5368
S-02115 | ML-5404 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Running | [30 empty] | M | 5404 |  | ML-5404
S-02115 | ML-5425 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Running | [30 empty] | M | 5425 |  | ML-5425
S-02115 | ML-5429 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Running | [30 empty] | M | 5429 |  | ML-5429
S-02115 | ML-5455 | 227.4 | Digital Indicator |  | P45 | [10 empty] | °C | Running | [30 empty] | M | 5455 |  | ML-5455
S-02115 | ML-5459 | 227.4 | Digital Indicator |  | P45 | [10 empty] | °C | Running | [30 empty] | M | 5459 |  | ML-5459
S-02115 | ML-5511 | 227.4 | Digital Indicator |  | U24 | [10 empty] | °C | Running | [30 empty] | M | 5511 |  | ML-5511
S-02115 | ML-5512 | 227.4 | Digital Indicator |  | U24 | [10 empty] | °C | Running | [30 empty] | M | 5512 |  | ML-5512
S-02115 | ML-5513 | 227.4 | Digital Indicator |  | U24 | [10 empty] | °C | Running | [30 empty] | M | 5513 |  | ML-5513
S-02115 | ML-6004 | 227.4 | Digital Indicator |  | P05 | [10 empty] | °C | Running | [30 empty] | M | 6004 |  | ML-6004
S-02115 | ML-6008 | 227.4 | Digital Indicator |  | P05 | [10 empty] | °C | Running | [30 empty] | M | 6008 |  | ML-6008
S-02115 | ML-6062 | 227.4 | Digital Indicator |  | P07 | [10 empty] | °C | Running | [30 empty] | M | 6062 |  | ML-6062
S-02115 | ML-6066 | 227.4 | Digital Indicator |  | P07 | [10 empty] | °C | Running | [30 empty] | M | 6066 |  | ML-6066
S-02115 | ML-6081 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Running | [30 empty] | M | 6081 |  | ML-6081
S-02115 | ML-6086 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Running | [30 empty] | M | 6086 |  | ML-6086
S-02115 | ML-7005 | 227.4 | Digital Indicator |  | U18 | [10 empty] | °C | Running | [30 empty] | M | 7005 |  | ML-7005
S-02115 | ML-7006 | 227.4 | Digital Indicator |  | U18 | [10 empty] | °C | Running | [30 empty] | M | 7006 |  | ML-7006
S-02115 | ML-7101 | 227.4 | Digital Indicator |  | U22 | [10 empty] | °C | Running | [30 empty] | M | 7101 |  | ML-7101
S-02115 | ML-7103 | 227.4 | Digital Indicator |  | U22 | [10 empty] | °C | Running | [30 empty] | M | 7103 |  | ML-7103
S-02115 | ML-7122 | 227.4 | Digital Indicator |  | U10 | [10 empty] | °C | Running | [30 empty] | M | 7122 |  | ML-7122
S-02115 | ML-7161 | 227.4 | Digital Indicator |  | U12 | [10 empty] | °C | Running | [30 empty] | M | 7161 |  | ML-7161
S-02115 | ML-7163 | 227.4 | Digital Indicator |  | U12 | [10 empty] | °C | Running | [30 empty] | M | 7163 |  | ML-7163
S-02115 | ML-7166 | 227.4 | Digital Indicator |  | U12 | [10 empty] | °C | Running | [30 empty] | M | 7166 |  | ML-7166
S-02115 | ML-7169 | 227.4 | Digital Indicator |  | U12 | [10 empty] | °C | Running | [30 empty] | M | 7169 |  | ML-7169
S-02115 | ML-7172 | 227.4 | Digital Indicator |  | U12 | [10 empty] | °C | Running | [30 empty] | M | 7172 |  | ML-7172
S-02115 | ML-7191 | 227.4 | Digital Indicator |  | U13 | [10 empty] | °C | Running | [30 empty] | M | 7191 |  | ML-7191
S-02115 | ML-7193 | 227.4 | Digital Indicator |  | U13 | [10 empty] | °C | Running | [30 empty] | M | 7193 |  | ML-7193
S-02115 | ML-7196 | 227.4 | Digital Indicator |  | U13 | [10 empty] | °C | Running | [30 empty] | M | 7196 |  | ML-7196
S-02115 | ML-7211 | 227.4 | Digital Indicator |  | U14 | [10 empty] | °C | Running | [30 empty] | M | 7211 |  | ML-7211
S-02115 | ML-7213 | 227.4 | Digital Indicator |  | U14 | [10 empty] | °C | Running | [30 empty] | M | 7213 |  | ML-7213
S-02115 | ML-7216 | 227.4 | Digital Indicator |  | U14 | [10 empty] | °C | Running | [30 empty] | M | 7216 |  | ML-7216
S-02115 | PZLL1-2073 | 227.4 | Digital Indicator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Valve closed | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | PZLL2-2073 | 227.4 | Digital Indicator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Valve closed | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | UZLH-1001 | 227.4 | Digital Indicator |  | P01 | [10 empty] | °C | Valve open | [30 empty] | U | 1001 |  | USY-1001
S-02115 | UZLL-1001 | 227.4 | Digital Indicator |  | P01 | [10 empty] | °C | Valve closed | [30 empty] | U | 1001 |  | USY-1001
S-02115 | UZLH-2010 | 227.4 | Digital Indicator |  | P02 | [10 empty] | °C | Valve open | [30 empty] | U | 2010 |  | USY-2010
S-02115 | UZLL-2010 | 227.4 | Digital Indicator |  | P02 | [10 empty] | °C | Valve closed | [30 empty] | U | 2010 |  | USY-2010
S-02115 | UZLH-2021 | 227.4 | Digital Indicator |  | P02 | [10 empty] | °C | Valve open | [30 empty] | U | 2021 |  | USY-2021
S-02115 | UZLL-2021 | 227.4 | Digital Indicator |  | P02 | [10 empty] | °C | Valve closed | [30 empty] | U | 2021 |  | USY-2021
S-02115 | UZLH-2038 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve open | [30 empty] | U | 2038 |  | USY-2038
S-02115 | UZLL-2038 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve closed | [30 empty] | U | 2038 |  | USY-2038
S-02115 | UZLH-2043 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve open | [30 empty] | U | 2043 |  | USY-2043
S-02115 | UZLL-2043 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve closed | [30 empty] | U | 2043 |  | USY-2043
S-02115 | UZLH-2045 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve open | [30 empty] | U | 2045 |  | USY-2045
S-02115 | UZLL-2045 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve closed | [30 empty] | U | 2045 |  | USY-2045
S-02115 | UZLH-2048 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve open | [30 empty] | U | 2048 |  | USY-2048
S-02115 | UZLL-2048 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve closed | [30 empty] | U | 2048 |  | USY-2048
S-02115 | UZLH-2049 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve open | [30 empty] | U | 2049 |  | USY-2049
S-02115 | UZLL-2049 | 227.4 | Digital Indicator |  | P03 | [10 empty] | °C | Valve closed | [30 empty] | U | 2049 |  | USY-2049
S-02115 | UZLH-2092 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve open | [30 empty] | U | 2092 |  | USY-2092
S-02115 | UZLL-2092 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve closed | [30 empty] | U | 2092 |  | USY-2092
S-02115 | UZLH-2093 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve open | [30 empty] | U | 2093 |  | USY-2093
S-02115 | UZLL-2093 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve closed | [30 empty] | U | 2093 |  | USY-2093
S-02115 | UZLH-2094 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve open | [30 empty] | U | 2094 |  | USY-2094
S-02115 | UZLL-2094 | 227.4 | Digital Indicator |  | P10 | [10 empty] | °C | Valve closed | [30 empty] | U | 2094 |  | USY-2094
S-02115 | UZLH-2117 | 227.4 | Digital Indicator |  | P11 | [10 empty] | °C | Valve open | [30 empty] | U | 2117 |  | USY-2117
S-02115 | UZLL-2117 | 227.4 | Digital Indicator |  | P11 | [10 empty] | °C | Valve closed | [30 empty] | U | 2117 |  | USY-2117
S-02115 | UZLH-2125 | 227.4 | Digital Indicator |  | P11 | [10 empty] | °C | Valve open | [30 empty] | U | 2125 |  | UY-2125
S-02115 | UZLL-2125 | 227.4 | Digital Indicator |  | P11 | [10 empty] | °C | Valve closed | [30 empty] | U | 2125 |  | UY-2125
S-02115 | UZLH-2166 | 227.4 | Digital Indicator |  | P12 | [10 empty] | °C | Valve open | [30 empty] | U | 2166 |  | USY-2166
S-02115 | UZLL-2166 | 227.4 | Digital Indicator |  | P12 | [10 empty] | °C | Valve closed | [30 empty] | U | 2166 |  | USY-2166
S-02115 | UZLH-2233 | 227.4 | Digital Indicator |  | P13 | [10 empty] | °C | Valve open | [30 empty] | U | 2233 |  | UY-2233
S-02115 | UZLL-2233 | 227.4 | Digital Indicator |  | P13 | [10 empty] | °C | Valve closed | [30 empty] | U | 2233 |  | UY-2233
S-02115 | UZLH-2381 | 227.4 | Digital Indicator |  | P18 | [10 empty] | °C | Valve open | [30 empty] | U | 2381 |  | USY-2381
S-02115 | UZLL-2381 | 227.4 | Digital Indicator |  | P18 | [10 empty] | °C | Valve closed | [30 empty] | U | 2381 |  | USY-2381
S-02115 | UZLH-2482 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Valve open | [30 empty] | U | 2482 |  | USY-2482
S-02115 | UZLL-2482 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Valve closed | [30 empty] | U | 2482 |  | USY-2482
S-02115 | UUZLH-2541 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2541 |  | USY-2541
S-02115 | UZLL-2541 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2541 |  | USY-2541
S-02115 | UZLH-2542 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2542 |  | USY-2542
S-02115 | UZLL-2542 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2542 |  | USY-2542
S-02115 | UZLH-2543 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2543 |  | USY-2543
S-02115 | UZLL-2543 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2543 |  | USY-2543
S-02115 | UUZLH-2544 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2544 |  | USY-2544
S-02115 | UZLL-2544 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2544 |  | USY-2544
S-02115 | UUZLH-2545 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2545 |  | USY-2545
S-02115 | UZLL-2545 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2545 |  | USY-2545
S-02115 | UZLH-2547 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2547 |  | USY-2547
S-02115 | UZLL-2547 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2547 |  | USY-2547
S-02115 | UZLH-2548 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2548 |  | USY-2548
S-02115 | UZLL-2548 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2548 |  | USY-2548
S-02115 | UZLH-2549 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve open | [30 empty] | U | 2549 |  | USY-2549
S-02115 | UZLL-2549 | 227.4 | Digital Indicator |  | U01 | [10 empty] | °C | Valve closed | [30 empty] | U | 2549 |  | USY-2549
S-02115 | UZLH-3018 | 227.4 | Digital Indicator |  | P22 | [10 empty] | °C | Valve open | [30 empty] | U | 3018 |  | USY-3018
S-02115 | UZLL-3018 | 227.4 | Digital Indicator |  | P22 | [10 empty] | °C | Valve closed | [30 empty] | U | 3018 |  | USY-3018
S-02115 | UZLH-3052 | 227.4 | Digital Indicator |  | P23 | [10 empty] | °C | Valve open | [30 empty] | U | 3052 |  | USY-3052
S-02115 | UZLL-3052 | 227.4 | Digital Indicator |  | P23 | [10 empty] | °C | Valve closed | [30 empty] | U | 3052 |  | USY-3052
S-02115 | UZLH-3172 | 227.4 | Digital Indicator |  | P27 | [10 empty] | °C | Valve open | [30 empty] | U | 3172 |  | USY-3172
S-02115 | UZLL-3172 | 227.4 | Digital Indicator |  | P27 | [10 empty] | °C | Valve closed | [30 empty] | U | 3172 |  | USY-3172
S-02115 | UZLH-5021 | 227.4 | Digital Indicator |  | P29 | [10 empty] | °C | Valve open | [30 empty] | U | 5021 |  | UY-5021
S-02115 | UZLL-5021 | 227.4 | Digital Indicator |  | P29 | [10 empty] | °C | Valve closed | [30 empty] | U | 5021 |  | UY-5021
S-02115 | UZLH-5302 | 227.4 | Digital Indicator |  | P39 | [10 empty] | °C | Valve open | [30 empty] | U | 5302 |  | USY-5302
S-02115 | UZLL-5302 | 227.4 | Digital Indicator |  | P39 | [10 empty] | °C | Valve closed | [30 empty] | U | 5302 |  | USY-5302
S-02115 | UZLH-5391 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Valve open | [30 empty] | U | 5391 |  | USY-5391
S-02115 | UZLL-5391 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Valve closed | [30 empty] | U | 5391 |  | USY-5391
S-02115 | UZLH-5392 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Valve open | [30 empty] | U | 5392 |  | USY-5392
S-02115 | UZLL-5392 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Valve closed | [30 empty] | U | 5392 |  | USY-5392
S-02115 | UZLH-5393 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Valve open | [30 empty] | U | 5393 |  | USY-5393
S-02115 | UZLL-5393 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Valve closed | [30 empty] | U | 5393 |  | USY-5393
S-02115 | UZLH-5420 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Valve open | [30 empty] | U | 5420 |  | USY-5420
S-02115 | UZLL-5420 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Valve closed | [30 empty] | U | 5420 |  | USY-5420
S-02115 | UZLH-5421 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Valve open | [30 empty] | U | 5421 |  | USY-5421
S-02115 | UZLL-5421 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Valve closed | [30 empty] | U | 5421 |  | USY-5421
S-02115 | UZLH-5422 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Valve open | [30 empty] | U | 5422 |  | USY-5422
S-02115 | UZLL-5422 | 227.4 | Digital Indicator |  | P44 | [10 empty] | °C | Valve closed | [30 empty] | U | 5422 |  | USY-5422
S-02115 | UZLH-6035 | 227.4 | Digital Indicator |  | P06 | [10 empty] | °C | Valve open | [30 empty] | U | 6035 |  | UY-6035
S-02115 | UZLL-6035 | 227.4 | Digital Indicator |  | P06 | [10 empty] | °C | Valve closed | [30 empty] | U | 6035 |  | UY-6035
S-02115 | UZLH-6081 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Valve open | [30 empty] | U | 6081 |  | USY-6081
S-02115 | UZLL-6081 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Valve closed | [30 empty] | U | 6081 |  | USY-6081
S-02115 | UZLH-6082 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Valve open | [30 empty] | U | 6082 |  | USY-6082
S-02115 | UZLL-6082 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Valve closed | [30 empty] | U | 6082 |  | USY-6082
S-02115 | UZLH-7130 | 227.4 | Digital Indicator |  | U10 | [10 empty] | °C | Valve open | [30 empty] | U | 7130 |  | USY-7130
S-02115 | UZLL-7130 | 227.4 | Digital Indicator |  | U10 | [10 empty] | °C | Valve closed | [30 empty] | U | 7130 |  | USY-7130
S-02115 | UZLH-7135 | 227.4 | Digital Indicator |  | U10 | [10 empty] | °C | Valve open | [30 empty] | U | 7135 |  | USY-7135
S-02115 | UZLL-7135 | 227.4 | Digital Indicator |  | U10 | [10 empty] | °C | Valve closed | [30 empty] | U | 7135 |  | USY-7135
S-02115 | YL-2124 | 227.4 | Digital Indicator |  | P11 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2124 |  | YL-2124
S-02115 | YL-2159 | 227.4 | Digital Indicator |  | P12 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2159 |  | YL-2159
S-02115 | YL-2410 | 227.4 | Digital Indicator |  | P19 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2410 |  | YL-2410
S-02115 | YL-2414 | 227.4 | Digital Indicator |  | P19 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2414 |  | YL-2414
S-02115 | YL-2447 | 227.4 | Digital Indicator |  | P20 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2447 |  | YL-2447
S-02115 | YL-2451 | 227.4 | Digital Indicator |  | P20 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2451 |  | YL-2451
S-02115 | YL-2471 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2471 |  | YL-2471
S-02115 | YL-2487 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2487 |  | YL-2487
S-02115 | YL-2491 | 227.4 | Digital Indicator |  | P21 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 2491 |  | YL-2491
S-02115 | YL-5013 | 227.4 | Digital Indicator |  | P29 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5013 |  | YL-5013
S-02115 | YL-5017 | 227.4 | Digital Indicator |  | P29 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5017 |  | YL-5017
S-02115 | YL-5077 | 227.4 | Digital Indicator |  | P31 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5077 |  | YL-5077
S-02115 | YL-5081 | 227.4 | Digital Indicator |  | P31 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5081 |  | YL-5081
S-02115 | YL-5101 | 227.4 | Digital Indicator |  | P32 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5101 |  | YL-5101
S-02115 | YL-5105 | 227.4 | Digital Indicator |  | P32 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5105 |  | YL-5105
S-02115 | YL-5133 | 227.4 | Digital Indicator |  | P33 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5133 |  | YL-5133
S-02115 | YL-5137 | 227.4 | Digital Indicator |  | P33 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5137 |  | YL-5137
S-02115 | YL-5212 | 227.4 | Digital Indicator |  | P36 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5212 |  | YL-5212
S-02115 | YL-5216 | 227.4 | Digital Indicator |  | P36 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5216 |  | YL-5216
S-02115 | YL-5233 | 227.4 | Digital Indicator |  | P37 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5233 |  | YL-5233
S-02115 | YL-5237 | 227.4 | Digital Indicator |  | P37 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5237 |  | YL-5237
S-02115 | YL-5329 | 227.4 | Digital Indicator |  | P40 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5329 |  | YL-5329
S-02115 | YL-5333 | 227.4 | Digital Indicator |  | P40 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5333 |  | YL-5333
S-02115 | YL-5353 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5353 |  | YL-5353
S-02115 | YL-5357 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5357 |  | YL-5357
S-02115 | YL-5361 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5361 |  | YL-5361
S-02115 | YL-5365 | 227.4 | Digital Indicator |  | P41 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5365 |  | YL-5365
S-02115 | YL-5404 | 227.4 | Digital Indicator |  | P43 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 5404 |  | YL-5404
S-02115 | YL-6004 | 227.4 | Digital Indicator |  | P05 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 6004 |  | YL-6004
S-02115 | YL-6008 | 227.4 | Digital Indicator |  | P05 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 6008 |  | YL-6008
S-02115 | YL-6062 | 227.4 | Digital Indicator |  | P07 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 6062 |  | YL-6062
S-02115 | YL-6066 | 227.4 | Digital Indicator |  | P07 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 6066 |  | YL-6066
S-02115 | YL-6081 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 6081 |  | YL-6081
S-02115 | YL-6086 | 227.4 | Digital Indicator |  | P08 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 6086 |  | YL-6086
S-02115 | YL-7005 | 227.4 | Digital Indicator |  | U18 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 7005 |  | YL-7005
S-02115 | YL-7006 | 227.4 | Digital Indicator |  | U18 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 7006 |  | YL-7006
S-02115 | YL-7122 | 227.4 | Digital Indicator |  | U10 | [10 empty] | °C | Ready to Start | [30 empty] | Y | 7122 |  | YL-7122
S-02115 | FQI-1006 | 227.55 | Totalizer |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Totalization | [30 empty] | F | 1006 |  | FI-1006
S-02115 | FQI-2007 | 227.55 | Totalizer |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Totalization | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FQI-2040 | 227.55 | Totalizer |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Totalization | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FQI-2150 | 227.55 | Totalizer |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Totalization | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FQI-2151 | 227.55 | Totalizer |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Totalization | [30 empty] | F | 2151 |  | FI-2151
S-02115 | FQI-2476 | 227.55 | Totalizer |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Totalization | [30 empty] | F | 2476 |  | FI-2476
S-02115 | FQI-2531 | 227.55 | Totalizer |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Totalization | [30 empty] | F | 2531 |  | FIC-2531
S-02115 | FQI-2536 | 227.55 | Totalizer |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Totalization | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | FQI-3198 | 227.55 | Totalizer |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | Totalization | [30 empty] | F | 3198 |  | FI-3198
S-02115 | FQI-5338 | 227.55 | Totalizer |  | P40 | [10 empty] | °C | Totalization | [30 empty] | F | 5338 |  | FI-5338
S-02115 | FQI-5421 | 227.55 | Totalizer |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | Totalization | [30 empty] | F | 5421 |  | FI-5421
S-02115 | FQI-6057 | 227.55 | Totalizer |  | P07 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | Totalization | [30 empty] | F | 6057 |  | FI-6057
S-02115 | FQI-7029 | 227.55 | Totalizer |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | Totalization | [30 empty] | F | 7029 |  | FI-7029
S-02115 | FQI-7030 | 227.55 | Totalizer |  | U04 |  | 24"-HPS-70-136-F34-H |  |  | 52 | 42 | bar g |  | 410 | 470 | °C | Totalization | [30 empty] | F | 7030 |  | FI-7030
S-02115 | AY-1001 | 227.6 | Calculation |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Median | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AFY-3004 | 227.6 | Calculation |  | P22 | [10 empty] | °C |  | AI-3001 (a), AI-3002 (b) | AI-3003 (c) |  |  |  | d = (a-c)/(b-c) | [24 empty] | A | 3004 |  | AFI-3004
S-02115 | FY-2007 | 227.6 | Calculation |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Median | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FFY-2020 | 227.6 | Calculation |  | P02 | [10 empty] | °C |  | FIC-2007, FIC-6070 | [29 empty] | F | 2020 |  | FFI-2020
S-02115 | FY-2040 | 227.6 | Calculation |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Median |  |  |  |  | FFI-2042 | [25 empty] | F | 2040 |  | FIC-2040
S-02115 | FFY-2042 | 227.6 | Calculation |  | P03 | [10 empty] | °C | Division | FIC-2007, FY-2040 | [29 empty] | F | 2042 |  | FFI-2042
S-02115 | FY-2061 | 227.6 | Calculation |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Median |  |  |  |  | FY-2065 | [25 empty] | F | 2061 |  | FIC-2061
S-02115 | FY-2065 | 227.6 | Calculation |  | P09 | [10 empty] | °C | Addition | FIC-6070, HIC-6068, FY-2061 |  |  |  | LY-6031, FY-2070/1 | [25 empty] | F | 2065 |  | FI-2065
S-02115 | FFY-2069 | 227.6 | Calculation |  | P09 | [10 empty] | °C | Division | [30 empty] | F | 2069 |  | FFI-2069
S-02115 | FY/1-2069 | 227.6 | Calculation |  | P09 | [10 empty] | °C | Addition | FY-2070/1, FY-2072 | [29 empty] | F | 2069 |  | FFI-2069
S-02115 | FY/2-2069 | 227.6 | Calculation |  | P09 | [10 empty] | °C | Multiplication | HSIC-2063, FIC-6070 | [29 empty] | F | 2069 |  | FFI-2069
S-02115 | FY/1-2070 | 227.6 | Calculation |  | P09 | [10 empty] | °C |  | FY-2065, FIC-2233 |  |  |  | FY-2069/1 | [25 empty] | F | 2070 |  | FHIC-2070
S-02115 | FY/2-2070 | 227.6 | Calculation |  | P09 | [10 empty] | °C | [5 empty] | FIC-2072 | [25 empty] | F | 2070 |  | FHIC-2070
S-02115 | FY/3-2070 | 227.6 | Calculation |  | P09 | [10 empty] | °C |  | FY-2069/2 | [29 empty] | F | 2070 |  | FHIC-2070
S-02115 | FY-2072 | 227.6 | Calculation |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Median |  |  |  |  | FY-2069/1 | [25 empty] | F | 2072 |  | FIC-2072
S-02115 | FY-2111 | 227.6 | Calculation |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | High Selector | PIC-2163 | [29 empty] | F | 2111 |  | FIC-2111
S-02115 | FY-2151 | 227.6 | Calculation |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Multiplier | HIC-2151 |  |  |  | FIC-2150 | [25 empty] | F | 2151 |  | FI-2151
S-02115 | FFY-2152 | 227.6 | Calculation |  | P12 | [10 empty] | °C | Division | FIC-2150, FI-2151 | [29 empty] | F | 2152 |  | FFI-2152
S-02115 | FY/1-2233 | 227.6 | Calculation |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | Median | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FY/2-2233 | 227.6 | Calculation |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | Low Selector | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FY/1-2531 | 227.6 | Calculation |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | High Selector | [30 empty] | F | 2531 |  | FIC-2531
S-02115 | FY/2-2531 | 227.6 | Calculation |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | High Selector | HIC-2534 | [29 empty] | F | 2531 |  | FIC-2531
S-02115 | FY/3-2531 | 227.6 | Calculation |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | High Selector | PIC-2554 | [29 empty] | F | 2531 |  | FIC-2531
S-02115 | FY/4-2531 | 227.6 | Calculation |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C |  | HIC-2533 |  |  |  | FY-2111/1 | [25 empty] | F | 2531 |  | FIC-2531
S-02115 | FY/1-2536 | 227.6 | Calculation |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Min. Select | PIC-2536 A | [29 empty] | F | 2536 |  | FIC-2536
S-02115 | FY/2-2536 | 227.6 | Calculation |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C |  | HIC-2538 |  |  |  | FY-2111/1 | [25 empty] | F | 2536 |  | FIC-2536
S-02115 | FY-3168 | 227.6 | Calculation |  | P27 | [10 empty] | °C | Addition | FI-3167, FI-3020 | [29 empty] | F | 3168 |  | FI-3168
S-02115 | FY-5301 | 227.6 | Calculation |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Multiplication | FI-3198 | [29 empty] | F | 5301 |  | FIC-5301
S-02115 | FY/1-5336 | 227.6 | Calculation |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Divider | FIC-5321, HIC-5336 | [29 empty] | F | 5336 |  | FIC-5336
S-02115 | FY/2-5336 | 227.6 | Calculation |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Subtraction | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | FY/3-5336 | 227.6 | Calculation |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Low Selector | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | FY/1-5337 | 227.6 | Calculation |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Divider | FIC-5203, HIC-5337 | [29 empty] | F | 5337 |  | FIC-5337
S-02115 | FY/2-5337 | 227.6 | Calculation |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Subtraction | FIC-5203 | [29 empty] | F | 5337 |  | FIC-5337
S-02115 | FY/3-5337 | 227.6 | Calculation |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Low Selector | [30 empty] | F | 5337 |  | FIC-5337
S-02115 | FY-5338 | 227.6 | Calculation |  | P40 | [10 empty] | °C | Addition | FIC-5336, FIC-5337 | [29 empty] | F | 5338 |  | FI-5338
S-02115 | FY-6070 | 227.6 | Calculation |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | Median | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FY-6081 | 227.6 | Calculation |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | High Selector | LIC-6051 | [29 empty] | F | 6081 |  | FIC-6081
S-02115 | FY-6082 | 227.6 | Calculation |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | Low Selector | LIC-6082 | [29 empty] | F | 6082 |  | FIC-6082
S-02115 | FY/1-7001 | 227.6 | Calculation |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | Equivalent valve opening | [30 empty] | F | 7001 |  | FI-7001
S-02115 | FY/2-7001 | 227.6 | Calculation |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | Lock-up | [30 empty] | F | 7001 |  | FI-7001
S-02115 | LY/1-2372 | 227.6 | Calculation |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Median | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LY/2-2372 | 227.6 | Calculation |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Density Compensation | PY-2372 | [29 empty] | L | 2372 |  | LIC-2372
S-02115 | LY/3-2372 | 227.6 | Calculation |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 3-element level control | FI-2372 | [29 empty] | L | 2372 |  | LIC-2372
S-02115 | LY-2474 | 227.6 | Calculation |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Median | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LY/1-3042 | 227.6 | Calculation |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Median | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LY/2-3042 | 227.6 | Calculation |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Density Compensation | PY-3042 | [29 empty] | L | 3042 |  | LIC-3042
S-02115 | LY/3-3042 | 227.6 | Calculation |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 3-element level control | FI-3050 | [29 empty] | L | 3042 |  | LIC-3042
S-02115 | LY-3161 | 227.6 | Calculation |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | Median | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LY-3192 | 227.6 | Calculation |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Median | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LY-5041 | 227.6 | Calculation |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | 3-element level control | FIC-5161 |  |  |  | FIC-5041 | [25 empty] | L | 5041 |  | LIC-5041
S-02115 | LY-5161 | 227.6 | Calculation |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | 3-element level control | FIC-5239 |  |  |  | FIC-5161 | [25 empty] | L | 5161 |  | LIC-5161
S-02115 | LY-5501 | 227.6 | Calculation |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | Median | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LY-6021 | 227.6 | Calculation |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | Low Selector | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LY-6051 | 227.6 | Calculation |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | Median | FY-2065 |  |  |  | FIC-6031 | [25 empty] | L | 6051 |  | LIC-6051
S-02115 | LY/1-6051 | 227.6 | Calculation |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 3-element level control | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LY-7091 | 227.6 | Calculation |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | Median | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | PY-2163 | 227.6 | Calculation |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | Median | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PY-2224 | 227.6 | Calculation |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Median | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PDY-2320 | 227.6 | Calculation |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | Subtraction | PI-2046 (a), PI-2322 (b) |  |  |  |  | b - a = c | [24 empty] | P | 2320 |  | PDI-2320
S-02115 | PY-2372 | 227.6 | Calculation |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Median |  |  |  |  | LY-2372 2 | [25 empty] | P | 2372 |  | PI-2372
S-02115 | PY-2554 | 227.6 | Calculation |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Median | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PY-3042 | 227.6 | Calculation |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Median |  |  |  |  | LY-3042/2 | [25 empty] | P | 3042 |  | PIC-3042
S-02115 | PDY-5048 | 227.6 | Calculation |  | P30 | [10 empty] | °C | Subtraction | PI-5047, PI-5049 | [29 empty] | P | 5048 |  | PDI-5048
S-02115 | PDY-5050 | 227.6 | Calculation |  | P30 | [10 empty] | °C | Subtraction | PI-5049, PI-5051 | [29 empty] | P | 5050 |  | PDI-5050
S-02115 | PDY-5167 | 227.6 | Calculation |  | P34 | [10 empty] | °C | Subtraction | PI-5166, PI-5176 | [29 empty] | P | 5167 |  | PDI-5167
S-02115 | PDY-5169 | 227.6 | Calculation |  | P34 | [10 empty] | °C | Subtraction | PI-5168, PI-5170 | [29 empty] | P | 5169 |  | PDI-5169
S-02115 | PDY-5171 | 227.6 | Calculation |  | P34 | [10 empty] | °C | Subtraction | PI-5170, PI-5172 | [29 empty] | P | 5171 |  | PDI-5171
S-02115 | PDY-5173 | 227.6 | Calculation |  | P34 | [10 empty] | °C | Subtraction | PI-5168, PI-5176 | [29 empty] | P | 5173 |  | PDI-5173
S-02115 | PY-5207 | 227.6 | Calculation |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Median | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PDY-5253 | 227.6 | Calculation |  | P38 | [10 empty] | °C | Subtraction | PI-3252, PI-3254 | [29 empty] | P | 5253 |  | PDI-5253
S-02115 | PDY-5255 | 227.6 | Calculation |  | P38 | [10 empty] | °C | Subtraction | PI-5254, PI-5256 | [29 empty] | P | 5255 |  | PDI-5255
S-02115 | PDY-5257 | 227.6 | Calculation |  | P38 | [10 empty] | °C | Subtraction | PI-5256, PI-5258 | [29 empty] | P | 5257 |  | PDI-5257
S-02115 | PDY-5259 | 227.6 | Calculation |  | P38 | [10 empty] | °C | Subtraction | PI-5258, PI-5260 | [29 empty] | P | 5259 |  | PDI-5259
S-02115 | PY/1-7002 | 227.6 | Calculation |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | High Selector | PIC-7003 | [29 empty] | P | 7002 |  | PIC-7002
S-02115 | PY/2-7002 | 227.6 | Calculation |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | High Selector | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PY/3-7002 | 227.6 | Calculation |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Sum | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | QY/1-2535 | 227.6 | Calculation |  | U01 | [10 empty] | °C | Multiplication | FIC-2536 | [29 empty] | Q | 2535 |  | QIC-2535
S-02115 | QY/2-2535 | 227.6 | Calculation |  | U01 | [10 empty] | °C | Multiplication | FIC-2531, HIC-2532 | [29 empty] | Q | 2535 |  | QIC-2535
S-02115 | QY/3-2535 | 227.6 | Calculation |  | U01 | [10 empty] | °C | Addition | [30 empty] | Q | 2535 |  | QIC-2535
S-02115 | TY-2295 | 227.6 | Calculation |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Rate of change calculation | [30 empty] | T | 2295 |  | TI-2295
S-02115 | TY-2297 | 227.6 | Calculation |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | Rate of change calculation | [30 empty] | T | 2297 |  | TI-2297
S-02115 | TY-2360 | 227.6 | Calculation |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Median | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TY-2457 | 227.6 | Calculation |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | High Selector | PIC-7094 | [29 empty] | T | 2457 |  | TIC-2457
S-02115 | TY-7003 | 227.6 | Calculation |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C |  | PZT-7002 B | [29 empty] | T | 7003 |  | TIC-7003
S-02115 | TY-7004 | 227.6 | Calculation |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C |  | PZT-7002 C | [29 empty] | T | 7004 |  | TIC-7004
S-02115 | TY-7071 | 227.6 | Calculation |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Median | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | FHIC-2070 | 227.7 | Manual Loader |  | P09 | [10 empty] | °C | 1.5-3 S/C ratio | [30 empty] | F | 2070 |  | FHIC-2070
S-02115 | HIC-2031 | 227.7 | Manual Loader |  | P03 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2031 |  | HIC-2031
S-02115 | HIC-2076 | 227.7 | Manual Loader |  | P09 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2076 |  | HIC-2076
S-02115 | HIC-2097 | 227.7 | Manual Loader |  | P10 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2097 |  | HIC-2097
S-02115 | HIC-2119 | 227.7 | Manual Loader |  | P11 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2119 |  | HIC-2119
S-02115 | HIC-2151 | 227.7 | Manual Loader |  | P12 | [10 empty] | °C | 0.01-0.04 Nm3/Nm3 | H2/NG | FY-2151 | [28 empty] | H | 2151 |  | HIC-2151
S-02115 | HIC-2167 | 227.7 | Manual Loader |  | P12 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2167 |  | HIC-2167
S-02115 | HIC-2225 | 227.7 | Manual Loader |  | P13 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | HIC-2371 | 227.7 | Manual Loader |  | P18 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2371 |  | HIC-2371
S-02115 | HIC-2472 | 227.7 | Manual Loader |  | P21 | [10 empty] | °C | 0-100 % | [30 empty] | H | 2472 |  | HIC-2472
S-02115 | HIC-2532 | 227.7 | Manual Loader |  | U01 | [10 empty] | °C | 30-40 MJ/Nm3 |  | QY-2535/2 | [28 empty] | H | 2532 |  | HIC-2532
S-02115 | HIC-2533 | 227.7 | Manual Loader |  | U01 | [10 empty] | °C | 9-15 mole/mole |  | FY-2531/4 | [28 empty] | H | 2533 |  | HIC-2533
S-02115 | HIC-2534 | 227.7 | Manual Loader |  | U01 | [10 empty] | °C | 2500-5000 Nm3/h |  | FY-2531/2 | [28 empty] | H | 2534 |  | HIC-2534
S-02115 | HIC-2537 | 227.7 | Manual Loader |  | U01 | [10 empty] | °C | 9-11 MJ/Nm3 |  | QY-2535/1 | [28 empty] | H | 2537 |  | HIC-2537
S-02115 | HIC-2538 | 227.7 | Manual Loader |  | U01 | [10 empty] | °C | 2-3.5 mole/mole |  | FY-2536/2 | [28 empty] | H | 2538 |  | HIC-2538
S-02115 | HIC-3011 | 227.7 | Manual Loader |  | P22 | [10 empty] | °C | 0-100 % | [30 empty] | H | 3011 |  | HIC-3011
S-02115 | HIC-3020 | 227.7 | Manual Loader |  | P22 | [10 empty] | °C | 10.75-11.75 MW |  | FI-3020 | [28 empty] | H | 3020 |  | HIC-3020
S-02115 | HIC-3142 | 227.7 | Manual Loader |  | P26 | [10 empty] | °C | 0-100 % | [30 empty] | H | 3142 |  | HIC-3142
S-02115 | HIC-3145 | 227.7 | Manual Loader |  | P26 | [10 empty] | °C | 0-100 % | [30 empty] | H | 3145 |  | HIC-3145
S-02115 | HIC-3148 | 227.7 | Manual Loader |  | P26 | [10 empty] | °C | 0-100 % | [30 empty] | H | 3148 |  | HIC-3148
S-02115 | HIC-3167 | 227.7 | Manual Loader |  | P27 | [10 empty] | °C | 9-12 MW |  | FI-3167 | [28 empty] | H | 3167 |  | HIC-3167
S-02115 | HIC-5093 | 227.7 | Manual Loader |  | P32 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5093 |  | HIC-5093
S-02115 | HIC-5202 | 227.7 | Manual Loader |  | P36 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5202 |  | HIC-5202
S-02115 | HIC-5336 | 227.7 | Manual Loader |  | P40 | [10 empty] | °C | 2.9-6 Ratio | [30 empty] | H | 5336 |  | HIC-5336
S-02115 | HIC-5337 | 227.7 | Manual Loader |  | P40 | [10 empty] | °C | 1.8-3.0 Ratio | [30 empty] | H | 5337 |  | HIC-5337
S-02115 | HIC-5338 | 227.7 | Manual Loader |  | P40 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5338 |  | HIC-5338
S-02115 | HIC-5369 | 227.7 | Manual Loader |  | P41 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5369 |  | HIC-5369
S-02115 | HIC-5403 | 227.7 | Manual Loader |  | P43 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5403 |  | HIC-5403
S-02115 | HIC-5454 | 227.7 | Manual Loader |  | P45 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5454 |  | HIC-5454
S-02115 | HIC-5458 | 227.7 | Manual Loader |  | P45 | [10 empty] | °C | 0-100 % | [30 empty] | H | 5458 |  | HIC-5458
S-02115 | HIC-6068 | 227.7 | Manual Loader |  | P07 | [10 empty] | °C | 16-19 MW | MW | FIC-6070, FY-2065 | [28 empty] | H | 6068 |  | HIC-6068
S-02115 | HIC-6069 | 227.7 | Manual Loader |  | P07 | [10 empty] | °C | 0-100 % | [30 empty] | H | 6069 |  | HIC-6069
S-02115 | HIC-7102 | 227.7 | Manual Loader |  | U22 | [10 empty] | °C | 0-100 % | [30 empty] | H | 7102 |  | HIC-7102
S-02115 | HIC-7104 | 227.7 | Manual Loader |  | U22 | [10 empty] | °C | 0-100 % | [30 empty] | H | 7104 |  | HIC-7104
S-02115 | HS-1003 | 227.71 | Hand Switch |  | P01 | [10 empty] | °C | Open/Close valve | [30 empty] | H | 1003 |  | HS-1003
S-02115 | HS-2003 | 227.71 | Hand Switch |  | P02 | [10 empty] | °C | Open/Close valve | [30 empty] | H | 2003 |  | HS-2003
S-02115 | HS-2410 | 227.71 | Hand Switch |  | P19 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2410 |  | HS-2410
S-02115 | HS-2414 | 227.71 | Hand Switch |  | P19 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2414 |  | HS-2414
S-02115 | HS-2447 | 227.71 | Hand Switch |  | P20 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2447 |  | HS-2447
S-02115 | HS-2451 | 227.71 | Hand Switch |  | P20 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2451 |  | HS-2451
S-02115 | HS-2471 | 227.71 | Hand Switch |  | P21 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2471 |  | HS-2471
S-02115 | HS-2487 | 227.71 | Hand Switch |  | P21 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2487 |  | HS-2487
S-02115 | HS-2491 | 227.71 | Hand Switch |  | P21 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2491 |  | HS-2491
S-02115 | HS-2550 | 227.71 | Hand Switch |  | U01 | [10 empty] | °C | Open/Close | [30 empty] | H | 2550 |  | HS-2550
S-02115 | HS-2577 | 227.71 | Hand Switch |  | U02 | [10 empty] | °C | Start/Stop | [30 empty] | H | 2577 |  | HS-2577
S-02115 | HS-3141 | 227.71 | Hand Switch |  | P26 | [10 empty] | °C | Start/Stop | [30 empty] | H | 3141 |  | HS-3141
S-02115 | HS-3144 | 227.71 | Hand Switch |  | P26 | [10 empty] | °C | Start/Stop | [30 empty] | H | 3144 |  | HS-3144
S-02115 | HS-3147 | 227.71 | Hand Switch |  | P26 | [10 empty] | °C | Start/Stop | [30 empty] | H | 3147 |  | HS-3147
S-02115 | HS-5013 | 227.71 | Hand Switch |  | P29 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5013 |  | HS-5013
S-02115 | HS-5017 | 227.71 | Hand Switch |  | P29 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5017 |  | HS-5017
S-02115 | HS-5077 | 227.71 | Hand Switch |  | P31 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5077 |  | HS-5077
S-02115 | HS-5081 | 227.71 | Hand Switch |  | P31 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5081 |  | HS-5081
S-02115 | HS-5092 | 227.71 | Hand Switch |  | P32 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5092 |  | HS-5092
S-02115 | HS-5101 | 227.71 | Hand Switch |  | P32 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5101 |  | HS-5101
S-02115 | HS-5105 | 227.71 | Hand Switch |  | P32 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5105 |  | HS-5105
S-02115 | HS-5133 | 227.71 | Hand Switch |  | P33 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5133 |  | HS-5133
S-02115 | HS-5137 | 227.71 | Hand Switch |  | P33 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5137 |  | HS-5137
S-02115 | HS-5201 | 227.71 | Hand Switch |  | P36 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5201 |  | HS-5201
S-02115 | HS-5212 | 227.71 | Hand Switch |  | P36 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5212 |  | HS-5212
S-02115 | HS-5216 | 227.71 | Hand Switch |  | P36 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5216 |  | HS-5216
S-02115 | HS-5232 | 227.71 | Hand Switch |  | U15 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5232 |  | HS-5232
S-02115 | HS-5233 | 227.71 | Hand Switch |  | P37 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5233 |  | HS-5233
S-02115 | HS-5236 | 227.71 | Hand Switch |  | U15 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5236 |  | HS-5236
S-02115 | HS-5237 | 227.71 | Hand Switch |  | P37 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5237 |  | HS-5237
S-02115 | HS-5329 | 227.71 | Hand Switch |  | P40 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5329 |  | HS-5329
S-02115 | HS-5333 | 227.71 | Hand Switch |  | P40 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5333 |  | HS-5333
S-02115 | HS-5353 | 227.71 | Hand Switch |  | P41 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5353 |  | HS-5353
S-02115 | HS-5357 | 227.71 | Hand Switch |  | P41 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5357 |  | HS-5357
S-02115 | HS-5361 | 227.71 | Hand Switch |  | P41 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5361 |  | HS-5361
S-02115 | HS-5365 | 227.71 | Hand Switch |  | P41 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5365 |  | HS-5365
S-02115 | HS-5368 | 227.71 | Hand Switch |  | P41 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5368 |  | HS-5368
S-02115 | HS-5404 | 227.71 | Hand Switch |  | P43 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5404 |  | HS-5404
S-02115 | HS-5425 | 227.71 | Hand Switch |  | P44 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5425 |  | HS-5425
S-02115 | HS-5429 | 227.71 | Hand Switch |  | P44 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5429 |  | HS-5429
S-02115 | HS-5455 | 227.71 | Hand Switch |  | P45 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5455 |  | HS-5455
S-02115 | HS-5459 | 227.71 | Hand Switch |  | P45 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5459 |  | HS-5459
S-02115 | HS-5511 | 227.71 | Hand Switch |  | U24 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5511 |  | HS-5511
S-02115 | HS-5517 | 227.71 | Hand Switch |  | U24 | [10 empty] | °C | Start/Stop | [30 empty] | H | 5517 |  | HS-5517
S-02115 | HS-6004 | 227.71 | Hand Switch |  | P05 | [10 empty] | °C | Start/Stop | [30 empty] | H | 6004 |  | HS-6004
S-02115 | HS-6008 | 227.71 | Hand Switch |  | P05 | [10 empty] | °C | Start/Stop | [30 empty] | H | 6008 |  | HS-6008
S-02115 | HS-6062 | 227.71 | Hand Switch |  | P07 | [10 empty] | °C | Start/Stop | [30 empty] | H | 6062 |  | HS-6062
S-02115 | HS-6066 | 227.71 | Hand Switch |  | P07 | [10 empty] | °C | Start/Stop | [30 empty] | H | 6066 |  | HS-6066
S-02115 | HS-6081 | 227.71 | Hand Switch |  | P08 | [10 empty] | °C | Start/Stop | [30 empty] | H | 6081 |  | HS-6081
S-02115 | HS-6086 | 227.71 | Hand Switch |  | P08 | [10 empty] | °C | Start/Stop | [30 empty] | H | 6086 |  | HS-6086
S-02115 | HS-7005 | 227.71 | Hand Switch |  | U18 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7005 |  | HS-7005
S-02115 | HS-7006 | 227.71 | Hand Switch |  | U18 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7006 |  | HS-7006
S-02115 | HS-7101 | 227.71 | Hand Switch |  | U22 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7101 |  | HS-7101
S-02115 | HS-7103 | 227.71 | Hand Switch |  | U22 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7103 |  | HS-7103
S-02115 | HS-7122 | 227.71 | Hand Switch |  | U10 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7122 |  | HS-7122
S-02115 | HS-7163 | 227.71 | Hand Switch |  | U12 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7163 |  | HS-7163
S-02115 | HS-7166 | 227.71 | Hand Switch |  | U12 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7166 |  | HS-7166
S-02115 | HS-7169 | 227.71 | Hand Switch |  | U12 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7169 |  | HS-7169
S-02115 | HS-7172 | 227.71 | Hand Switch |  | U12 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7172 |  | HS-7172
S-02115 | HS-7193 | 227.71 | Hand Switch |  | U13 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7193 |  | HS-7193
S-02115 | HS-7196 | 227.71 | Hand Switch |  | U13 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7196 |  | HS-7196
S-02115 | HS-7213 | 227.71 | Hand Switch |  | U14 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7213 |  | HS-7213
S-02115 | HS-7216 | 227.71 | Hand Switch |  | U14 | [10 empty] | °C | Start/Stop | [30 empty] | H | 7216 |  | HS-7216
S-02115 | FHIC-2111 | 227.76 | Auto/manual station |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 0-100 % | [30 empty] | F | 2111 |  | FIC-2111
S-02115 | FHIC/1-2233 | 227.76 | Auto/manual station |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 0-100 % | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FHIC/2-2233 | 227.76 | Auto/manual station |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 0-100 % | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FHIC-3041 | 227.76 | Auto/manual station |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | 0-100 % | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | FHIC-6031 | 227.76 | Auto/manual station |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 0-100 % | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | FHIC-7001 | 227.76 | Auto/manual station |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 0-100 % | [30 empty] | F | 7001 |  | FI-7001
S-02115 | HIC-7131 | 227.76 | Auto/manual station |  | U10 | [10 empty] | °C | 0-100 % | [30 empty] | H | 7131 |  | HIC-7131
S-02115 | HIC-7136 | 227.76 | Auto/manual station |  | U10 | [10 empty] | °C | 0-100 % | [30 empty] | H | 7136 |  | HIC-7136
S-02115 | LHIC-2372 | 227.76 | Auto/manual station |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-100 % | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LHIC/A-3161 | 227.76 | Auto/manual station |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 0-100 % | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LHIC/B-3161 | 227.76 | Auto/manual station |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 0-100 % | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LHIC-6021 | 227.76 | Auto/manual station |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | 0-100 % | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LHIC-6082 | 227.76 | Auto/manual station |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | 0-100 % | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | PHIC/A-5091 | 227.76 | Auto/manual station |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-100 % | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | PHIC/B-5091 | 227.76 | Auto/manual station |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 0-100 % | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | PHIC/A-7002 | 227.76 | Auto/manual station |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PHIC/B-7002 | 227.76 | Auto/manual station |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PHIC/C-7002 | 227.76 | Auto/manual station |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PHIC/A-7025 | 227.76 | Auto/manual station |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | PHIC/B-7025 | 227.76 | Auto/manual station |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-100 % | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | PHIC/A-7031 | 227.76 | Auto/manual station |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-100 % | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PHIC/B-7031 | 227.76 | Auto/manual station |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-100 % | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PHIC/C-7031 | 227.76 | Auto/manual station |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-100 % | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PHIC/D-7031 | 227.76 | Auto/manual station |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-100 % | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PHIC/A-7051 | 227.76 | Auto/manual station |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-100 % | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | PHIC/B-7051 | 227.76 | Auto/manual station |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-100 % | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | PHIC-7094 | 227.76 | Auto/manual station |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-100 % | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | THIC/1-2335 | 227.76 | Auto/manual station |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-100 % | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | THIC/2-2335 | 227.76 | Auto/manual station |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-100 % | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | THIC/1-2336 | 227.76 | Auto/manual station |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-100 % | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | THIC/2-2336 | 227.76 | Auto/manual station |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 0-100 % | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | FHS-2417 | 227.85 | Selector switch |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | LIC-2372 | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | FHS-3041 | 227.85 | Selector switch |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | LIC-3042 | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | FHS-5041 | 227.85 | Selector switch |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | LIC-5041 | [30 empty] | F | 5041 |  | FIC-5041
S-02115 | FHS-5161 | 227.85 | Selector switch |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | LY-5161 | [30 empty] | F | 5161 |  | FIC-5161
S-02115 | FHS-5239 | 227.85 | Selector switch |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | TIC-5266, -5267 & -5268 | [30 empty] | F | 5239 |  | FIC-5239
S-02115 | FHS-6031 | 227.85 | Selector switch |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | LIC-6051 | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | HS-7001 | 227.85 | Selector switch |  | U03 | [10 empty] | °C | PY-7002/2, PHIC-7002/2 | [30 empty] | H | 7001 |  | HS-7001
S-02115 | LHS-7091 | 227.85 | Selector switch |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | FIC-7091 | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | THS-7025 | 227.85 | Selector switch |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C |  | TV-7025/A or TV-7025/B | [29 empty] | T | 7025 |  | TIC-7025
S-02115 | THS-7071 | 227.85 | Selector switch |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C |  | TV-7071/A or TV-7071/B | [29 empty] | T | 7071 |  | TIC-7071
S-02115 | FV-2007 | 243 | Control Valve |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FV-2007 | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FV-2009 | 243 | Control Valve |  | P02 |  | 6"-PO-20-104-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | FV-2009 | [30 empty] | F | 2009 |  | FIC-2009
S-02115 | FV-2040 | 243 | Control Valve |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FV-2040 | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FV-2061 | 243 | Control Valve |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FV-2061 | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FV-2072 | 243 | Control Valve |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FV-2072 | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FV-2079 | 243 | Control Valve |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FV-2079 | [30 empty] | F | 2079 |  | FIC-2079
S-02115 | FV-2091 | 243 | Control Valve |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FV-2009 | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | FV-2111 | 243 | Control Valve |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C |  | and supplied by F 2002 vendor | [29 empty] | F | 2111 |  | FIC-2111
S-02115 | FV-2150 | 243 | Control Valve |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FV-2150 | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FV/1-2233 | 243 | Control Valve |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | FV-2233/1 | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FV/2-2233 | 243 | Control Valve |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | FV-2233/2 | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FV-2417 | 243 | Control Valve |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FV-2417 | [30 empty] | F | 2417 |  | FIC-2417
S-02115 | FV/1-2531 | 243 | Control Valve |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FV-2531/1 | [30 empty] | F | 2531 |  | FIC-2531
S-02115 | FV/2-2531 | 243 | Control Valve |  | U01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FV-2531/2 | [30 empty] | F | 2531 |  | FIC-2531
S-02115 | FV-2536 | 243 | Control Valve |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FV-2536 | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | FV-3041 | 243 | Control Valve |  | P23 |  | 10"-MPC-30-102-F24-H |  |  | 47 | 33.7 | bar g |  | 230 | 260 | °C | FV-3041 | [30 empty] | F | 3041 |  | FIC-3041
S-02115 | FV-3169 | 243 | Control Valve |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FV-3169 | [30 empty] | F | 3169 |  | FIC-3169
S-02115 | FV-3171 | 243 | Control Valve |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FV-3171 | [30 empty] | F | 3171 |  | FIC-3171
S-02115 | FV-5020 | 243 | Control Valve |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | FV-5020 | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | FV-5041 | 243 | Control Valve |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | FV-5041 | [30 empty] | F | 5041 |  | FIC-5041
S-02115 | FV-5093 | 243 | Control Valve |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FV-5093 | [30 empty] | F | 5093 |  | FIC-5093
S-02115 | FV-5107 | 243 | Control Valve |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FV-5107 | [30 empty] | F | 5107 |  | FIC-5107
S-02115 | FV-5161 | 243 | Control Valve |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | FV-5161 | [30 empty] | F | 5161 |  | FIC-5161
S-02115 | FV-5203 | 243 | Control Valve |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | FV-5203 | [30 empty] | F | 5203 |  | FIC-5203
S-02115 | FV-5239 | 243 | Control Valve |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | FV-5239 | [30 empty] | F | 5239 |  | FIC-5239
S-02115 | FV-5301 | 243 | Control Valve |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FV-5301 | [30 empty] | F | 5301 |  | FIC-5301
S-02115 | FV-5321 | 243 | Control Valve |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | FV-5321 | [30 empty] | F | 5321 |  | FIC-5321
S-02115 | FV-5336 | 243 | Control Valve |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | FV-5340 | [30 empty] | F | 5336 |  | FIC-5336
S-02115 | FV-5337 | 243 | Control Valve |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | FV-5337 | [30 empty] | F | 5337 |  | FIC-5337
S-02115 | FV-5367 | 243 | Control Valve |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | FV-5367 | [30 empty] | F | 5367 |  | FIC-5367
S-02115 | FV-5383 | 243 | Control Valve |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | FV-5383 | [30 empty] | F | 5383 |  | FIC-5383
S-02115 | FV-5441 | 243 | Control Valve |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | FV-5441 | [30 empty] | F | 5441 |  | FIC-5441
S-02115 | FV-5501 | 243 | Control Valve |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | FV-5501 | [30 empty] | F | 5501 |  | FIC-5501
S-02115 | FV-6031 | 243 | Control Valve |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | FV-6031 | [30 empty] | F | 6031 |  | FIC-6031
S-02115 | FV-6070 | 243 | Control Valve |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | FV-6070 | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FV-6081 | 243 | Control Valve |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | FV-6081 | [30 empty] | F | 6081 |  | FIC-6081
S-02115 | FV-6082 | 243 | Control Valve |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | FV-6082 | [30 empty] | F | 6082 |  | FIC-6082
S-02115 | FV-6086 | 243 | Control Valve |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | FV-6086 | [30 empty] | F | 6086 |  | FIC-6086
S-02115 | FV-7091 | 243 | Control Valve |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | FV-7091 | [30 empty] | F | 7091 |  | FIC-7091
S-02115 | FV-7141 | 243 | Control Valve |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FV-7141 | [30 empty] | F | 7141 |  | FIC-7141
S-02115 | HV-1003 | 243 | Control Valve |  | P01 | [10 empty] | °C | HV-1003 | [30 empty] | H | 1003 |  | HS-1003
S-02115 | HV-2003 | 243 | Control Valve |  | P02 | [10 empty] | °C | HV-2003 | [30 empty] | H | 2003 |  | HS-2003
S-02115 | HV-2031 | 243 | Control Valve |  | P03 | [10 empty] | °C | HV-2031 | [30 empty] | H | 2031 |  | HIC-2031
S-02115 | HV-2076 | 243 | Control Valve |  | P09 | [10 empty] | °C | HV-2076 | [30 empty] | H | 2076 |  | HIC-2076
S-02115 | HV-2097 | 243 | Control Valve |  | P10 | [10 empty] | °C | HV-2097 | [30 empty] | H | 2097 |  | HIC-2097
S-02115 | HV-2098 | 243 | Control Valve |  | P10 | [10 empty] | °C | HV-2078 | [30 empty] | H | 2098 |  | HS-2098
S-02115 | HV1-2225/1 | 243 | Control Valve |  | P13 | [10 empty] | °C |  |  | and supplied by H 2001 vendor | [28 empty] | H | 2225 | 1 | HV-2225/1
S-02115 | HV1-2225/2 | 243 | Control Valve |  | P13 | [10 empty] | °C |  |  | and supplied by H 2001 vendor | [28 empty] | H | 2225 | 2 | HV-2225/2
S-02115 | HV/1-2225 | 243 | Control Valve |  | P13 | [10 empty] | °C | HV-2225/1 | and supplied by H 2001 vendor | [29 empty] | H | 2225 |  | HIC-2225
S-02115 | HV/2-2225 | 243 | Control Valve |  | P13 | [10 empty] | °C | HV-2225/2 | and supplied by H 2001 vendor | [29 empty] | H | 2225 |  | HIC-2225
S-02115 | HV-2371 | 243 | Control Valve |  | P18 | [10 empty] | °C | HV-2371 | [30 empty] | H | 2371 |  | HIC-2371
S-02115 | HV-3011 | 243 | Control Valve |  | P22 | [10 empty] | °C | HV-3011 | [30 empty] | H | 3011 |  | HIC-3011
S-02115 | HV-5338 | 243 | Control Valve |  | P40 | [10 empty] | °C | HV-5338 | [30 empty] | H | 5338 |  | HIC-5338
S-02115 | HV-6069 | 243 | Control Valve |  | P07 | [10 empty] | °C | HV-6069 | [30 empty] | H | 6069 |  | HIC-6069
S-02115 | LV-2016 | 243 | Control Valve |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | LV-2016 | [30 empty] | L | 2016 |  | LIC-2016
S-02115 | LV-2372 | 243 | Control Valve |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | LV-2372 | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LV-2403 | 243 | Control Valve |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | LV-2403 | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LV-2419 | 243 | Control Valve |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | LV-2419 | [30 empty] | L | 2419 |  | LIC-2419
S-02115 | LV-2441 | 243 | Control Valve |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | LV-2441 | [30 empty] | L | 2441 |  | LIC-2441
S-02115 | LV-2474 | 243 | Control Valve |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | LV-2474 | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LV/A-3161 | 243 | Control Valve |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | LV-3161/A | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LV/B-3161 | 243 | Control Valve |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | LV-3161/B | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LV-3192 | 243 | Control Valve |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | LV-3192 | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LV-5070 | 243 | Control Valve |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | LV-5070 | [30 empty] | L | 5070 |  | LIC-5070
S-02115 | LV-5501 | 243 | Control Valve |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | LV-5501 | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LV/A-6021 | 243 | Control Valve |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | LV-6021/A | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LV/B-6021 | 243 | Control Valve |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | LV-6021/B | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | LV-6082 | 243 | Control Valve |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | LV-6082 | [30 empty] | L | 6082 |  | LIC-6082
S-02115 | LV-7251 | 243 | Control Valve |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | LV-7251 | [30 empty] | L | 7251 |  | LIC-7251
S-02115 | PV-1006 | 243 | Control Valve |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | PV-1006 | [30 empty] | P | 1006 |  | PIC-1006
S-02115 | PV-1011 | 243 | Control Valve |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | PV-1011 | [30 empty] | P | 1011 |  | PIC-1011
S-02115 | PV-1045 | 243 | Control Valve |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | PV-1045 | [30 empty] | P | 1045 |  | PIC-1045
S-02115 | PV-2015 | 243 | Control Valve |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | PV-2015 | [30 empty] | P | 2015 |  | PIC-2015
S-02115 | PV-2073 | 243 | Control Valve |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | PV-2073 | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | PV-2224 | 243 | Control Valve |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | PV-2224 | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PV-2361 | 243 | Control Valve |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | PV-2361 | [30 empty] | P | 2361 |  | PIC-2361
S-02115 | PV-2363 | 243 | Control Valve |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | PV-2363 | [30 empty] | P | 2363 |  | PIC-2363
S-02115 | PV-2406 | 243 | Control Valve |  | P19 |  | 34"-RFG-20-120-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | PV-2406 | [30 empty] | P | 2406 |  | PIC-2406
S-02115 | PV-2481 | 243 | Control Valve |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | PV-2481 | [30 empty] | P | 2481 |  | PIC-2481
S-02115 | PV-2536 | 243 | Control Valve |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | PV-2536 | [30 empty] | P | 2536 |  | PIC-2536
S-02115 | PDV-2575 | 243 | Control Valve |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | PDV-2575 | [30 empty] | P | 2575 |  | PDIC-2575
S-02115 | PV-2603 | 243 | Control Valve |  | U17 |  | 3"-HG-20-109-D24-N |  |  | 29 | 25 | bar g |  | 40 | 100 | °C | PV-2603 | [30 empty] | P | 2603 |  | PIC-2603
S-02115 | PV-2608 | 243 | Control Valve |  | U17 |  | 3"-HG-20-108-F24-N |  |  | 55 | 50.4 | bar g |  | 48 | 100 | °C | PV-2608 | [30 empty] | P | 2608 |  | PIC-2608
S-02115 | PV-3042 | 243 | Control Valve |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | PV-3042 | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PV-3166 | 243 | Control Valve |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | PV-3166 | [30 empty] | P | 3166 |  | PIC-3166
S-02115 | PV-3194 | 243 | Control Valve |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | PV-3194 | [30 empty] | P | 3194 |  | PIC-3194
S-02115 | PV-5069 | 243 | Control Valve |  | P31 |  | 14"-LPS-50-103-D24-H |  |  | 9.5 | 2.4 | bar g |  | 187 | 340 | °C | PV-5069 | [30 empty] | P | 5069 |  | PIC-5069
S-02115 | PV/A-5091 | 243 | Control Valve |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | PV-5091/A | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | PV/B-5091 | 243 | Control Valve |  | P32 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | PV-5091/B | [30 empty] | P | 5091 |  | PIC-5091
S-02115 | PV-5109 | 243 | Control Valve |  | P32 | [10 empty] | °C | PV-5109 | [30 empty] | P | 5109 |  | PIC-5109
S-02115 | PV/A-5207 | 243 | Control Valve |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | PV-5207/A | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PV/B-5207 | 243 | Control Valve |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | PV-5207/B | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PV-6025 | 243 | Control Valve |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | PV-6025 | [30 empty] | P | 6025 |  | PIC-6025
S-02115 | PV/A-7002 | 243 | Control Valve |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | PV-7002/A | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PV/B-7002 | 243 | Control Valve |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | PV-7002/B | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PV/C-7002 | 243 | Control Valve |  | U03 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | PV-7002/C | [30 empty] | P | 7002 |  | PIC-7002
S-02115 | PV-7004 | 243 | Control Valve |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | PV-7004 | [30 empty] | P | 7004 |  | PIC-7004
S-02115 | PV/A-7025 | 243 | Control Valve |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | PV-7025/A | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | PV/B-7025 | 243 | Control Valve |  | U04 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | PV-7025/B | [30 empty] | P | 7025 |  | PIC-7025
S-02115 | PV-7028 | 243 | Control Valve |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | PV-7028 | [30 empty] | P | 7028 |  | PIC-7028
S-02115 | PV/A-7031 | 243 | Control Valve |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | PV-7031/A | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PV/B-7031 | 243 | Control Valve |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | PV-7031/B | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PV/C-7031 | 243 | Control Valve |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | PV-7031/C | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PV/D-7031 | 243 | Control Valve |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | PV-7031/D | [30 empty] | P | 7031 |  | PIC-7031
S-02115 | PV-7034 | 243 | Control Valve |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | PV-7034 | [30 empty] | P | 7034 |  | PIC-7034
S-02115 | PV/A-7051 | 243 | Control Valve |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | PV-7051/A | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | PV/B-7051 | 243 | Control Valve |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | PV-7051/B | [30 empty] | P | 7051 |  | PIC-7051
S-02115 | PV-7056 | 243 | Control Valve |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | PV-7056 | [30 empty] | P | 7056 |  | PIC-7056
S-02115 | PV-7094 | 243 | Control Valve |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | PV-7094 | [30 empty] | P | 7094 |  | PIC-7094
S-02115 | PV-7101 | 243 | Control Valve |  | U09 | [10 empty] | °C | PV-7101 | [30 empty] | P | 7101 |  | PIC-7101
S-02115 | TV-2220 | 243 | Control Valve |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | TV-2220 | [30 empty] | T | 2220 |  | TIC-2220
S-02115 | TV/1-2335 | 243 | Control Valve |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | TV-2335/1 | and supplied by E 2020 vendor | [29 empty] | T | 2335 |  | TIC-2335
S-02115 | TV/2-2335 | 243 | Control Valve |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | TV-2335/2 | and supplied by E 2020 vendor | [29 empty] | T | 2335 |  | TIC-2335
S-02115 | TV/1-2336 | 243 | Control Valve |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | TV-2336/1 | and supplied by E 2020 vendor | [29 empty] | T | 2336 |  | TIC-2336
S-02115 | TV/2-2336 | 243 | Control Valve |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | TV-2336/2 | and supplied by E 2020 vendor | [29 empty] | T | 2336 |  | TIC-2336
S-02115 | TV-2457 | 243 | Control Valve |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | TV-2457 | [30 empty] | T | 2457 |  | TIC-2457
S-02115 | TV-3113 | 243 | Control Valve |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | TV-3113 | [30 empty] | T | 3113 |  | TIC-3113
S-02115 | TV-3116 | 243 | Control Valve |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | TV-3116 | [30 empty] | T | 3116 |  | TIC-3116
S-02115 | TV-3118 | 243 | Control Valve |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | TV-3118 | [30 empty] | T | 3118 |  | TIC-3118
S-02115 | TV-5064 | 243 | Control Valve |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | TV-5064 | [30 empty] | T | 5064 |  | TIC-5064
S-02115 | TV-5277 | 243 | Control Valve |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | TV-5277 | [30 empty] | T | 5277 |  | TIC-5277
S-02115 | TV-7002 | 243 | Control Valve |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | TV-7002 | [30 empty] | T | 7002 |  | TIC-7002
S-02115 | TV-7003 | 243 | Control Valve |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | TV-7003 | [30 empty] | T | 7003 |  | TIC-7003
S-02115 | TV-7004 | 243 | Control Valve |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | TV-7004 | [30 empty] | T | 7004 |  | TIC-7004
S-02115 | TV/A-7025 | 243 | Control Valve |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | TV-7025/A | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | TV/B-7025 | 243 | Control Valve |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | TV-7025/B | [30 empty] | T | 7025 |  | TIC-7025
S-02115 | TV-7026 | 243 | Control Valve |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | TV-7026 | [30 empty] | T | 7026 |  | TIC-7026
S-02115 | TV-7027 | 243 | Control Valve |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | TV-7027 | [30 empty] | T | 7027 |  | TIC-7027
S-02115 | TV-7032 | 243 | Control Valve |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | TV-7032 | [30 empty] | T | 7032 |  | TIC-7032
S-02115 | TV-7033 | 243 | Control Valve |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | TV-7033 | [30 empty] | T | 7033 |  | TIC-7033
S-02115 | TV-7052 | 243 | Control Valve |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | TV-7052 | [30 empty] | T | 7052 |  | TIC-7052
S-02115 | TV-7053 | 243 | Control Valve |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | TV-7053 | [30 empty] | T | 7053 |  | TIC-7053
S-02115 | TV/A-7071 | 243 | Control Valve |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | TV-7071/A | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TV/B-7071 | 243 | Control Valve |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | TV-7071/B | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | USV-1001 | 243 | Control Valve |  | P01 | [10 empty] | °C | USV-1001 | [30 empty] | U | 1001 |  | USY-1001
S-02115 | USV-2010 | 243 | Control Valve |  | P02 | [10 empty] | °C | USV-2010 | [30 empty] | U | 2010 |  | USY-2010
S-02115 | USV-2021 | 243 | Control Valve |  | P02 | [10 empty] | °C | USV-2021 | [30 empty] | U | 2021 |  | USY-2021
S-02115 | USV-2038 | 243 | Control Valve |  | P03 | [10 empty] | °C | USV-2038 | [30 empty] | U | 2038 |  | USY-2038
S-02115 | USV-2043 | 243 | Control Valve |  | P03 | [10 empty] | °C | USV-2043 | [30 empty] | U | 2043 |  | USY-2043
S-02115 | USV-2045 | 243 | Control Valve |  | P03 | [10 empty] | °C | USV-2045 | [30 empty] | U | 2045 |  | USY-2045
S-02115 | USV-2048 | 243 | Control Valve |  | P03 | [10 empty] | °C | USV-2048 | [30 empty] | U | 2048 |  | USY-2048
S-02115 | USV-2049 | 243 | Control Valve |  | P03 | [10 empty] | °C | USV-2049 | [30 empty] | U | 2049 |  | USY-2049
S-02115 | USV-2092 | 243 | Control Valve |  | P10 | [10 empty] | °C | USV-2092 | [30 empty] | U | 2092 |  | USY-2092
S-02115 | USV-2093 | 243 | Control Valve |  | P10 | [10 empty] | °C | USV-2093 | [30 empty] | U | 2093 |  | USY-2093
S-02115 | USV-2094 | 243 | Control Valve |  | P10 | [10 empty] | °C | USV-2094 | [30 empty] | U | 2094 |  | USY-2094
S-02115 | USV1-2117 | 243 | Control Valve |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | and supplied by FT 2002 vendor | [29 empty] | U | 2117 |  | USV-2117
S-02115 | USV-2117 | 243 | Control Valve |  | P11 | [10 empty] | °C | USV-2217 | [30 empty] | U | 2117 |  | USY-2117
S-02115 | UV-2125 | 243 | Control Valve |  | P11 | [10 empty] | °C | UV-2125 | [30 empty] | U | 2125 |  | UY-2125
S-02115 | USV1-2166 | 243 | Control Valve |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | and supplied by FT 2001 vendor | [29 empty] | U | 2166 |  | USV-2166
S-02115 | USV-2166 | 243 | Control Valve |  | P12 | [10 empty] | °C | USV-2166 | [30 empty] | U | 2166 |  | USY-2166
S-02115 | UV-2233 | 243 | Control Valve |  | P13 | [10 empty] | °C | UV-2233 | [30 empty] | U | 2233 |  | UY-2233
S-02115 | USV-2381 | 243 | Control Valve |  | P18 | [10 empty] | °C | USV-2381 | [30 empty] | U | 2381 |  | USY-2381
S-02115 | USV-2482 | 243 | Control Valve |  | P21 | [10 empty] | °C | USV-2482 | [30 empty] | U | 2482 |  | USY-2482
S-02115 | USV-2541 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2541 | [30 empty] | U | 2541 |  | USY-2541
S-02115 | USV-2542 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2542 | [30 empty] | U | 2542 |  | USY-2542
S-02115 | USV-2543 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2543 | [30 empty] | U | 2543 |  | USY-2543
S-02115 | USV-2544 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2544 | [30 empty] | U | 2544 |  | USY-2544
S-02115 | USV-2545 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2545 | [30 empty] | U | 2545 |  | USY-2545
S-02115 | USV-2547 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2547 | [30 empty] | U | 2547 |  | USY-2547
S-02115 | USV-2548 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2548 | [30 empty] | U | 2548 |  | USY-2548
S-02115 | USV-2549 | 243 | Control Valve |  | U01 | [10 empty] | °C | USV-2549 | [30 empty] | U | 2549 |  | USY-2549
S-02115 | USV-3018 | 243 | Control Valve |  | P22 | [10 empty] | °C | USV-3018 | [30 empty] | U | 3018 |  | USY-3018
S-02115 | USV-3052 | 243 | Control Valve |  | P23 | [10 empty] | °C | USV-3052 | [30 empty] | U | 3052 |  | USY-3052
S-02115 | USV-3172 | 243 | Control Valve |  | P27 | [10 empty] | °C | USV-3172 | [30 empty] | U | 3172 |  | USY-3172
S-02115 | UV-5021 | 243 | Control Valve |  | P29 | [10 empty] | °C | UV-5021 | [30 empty] | U | 5021 |  | UY-5021
S-02115 | USV-5302 | 243 | Control Valve |  | P39 | [10 empty] | °C | USV-5302 | [30 empty] | U | 5302 |  | USY-5302
S-02115 | USV-5391 | 243 | Control Valve |  | P43 | [10 empty] | °C | USV-5391 | [30 empty] | U | 5391 |  | USY-5391
S-02115 | USV-5392 | 243 | Control Valve |  | P43 | [10 empty] | °C | USV-5392 | [30 empty] | U | 5392 |  | USY-5392
S-02115 | USV-5393 | 243 | Control Valve |  | P43 | [10 empty] | °C | USV-5393 | [30 empty] | U | 5393 |  | USY-5393
S-02115 | USV-5420 | 243 | Control Valve |  | P44 | [10 empty] | °C | USV-5420 | [30 empty] | U | 5420 |  | USY-5420
S-02115 | USV-5421 | 243 | Control Valve |  | P44 | [10 empty] | °C | USV-5421 | [30 empty] | U | 5421 |  | USY-5421
S-02115 | USV-5422 | 243 | Control Valve |  | P44 | [10 empty] | °C | USV-5422 | [30 empty] | U | 5422 |  | USY-5422
S-02115 | USV-6035 | 243 | Control Valve |  | P06 | [10 empty] | °C | UV-6035 | [30 empty] | U | 6035 |  | UY-6035
S-02115 | USV-6081 | 243 | Control Valve |  | P08 | [10 empty] | °C | USV-6081 | [30 empty] | U | 6081 |  | USY-6081
S-02115 | USV-6082 | 243 | Control Valve |  | P08 | [10 empty] | °C | USV-6082 | [30 empty] | U | 6082 |  | USY-6082
S-02115 | USV1-7130 | 243 | Control Valve |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | and supplied by FP 7001 vendor | [29 empty] | U | 7130 |  | USV-7130
S-02115 | USV-7130 | 243 | Control Valve |  | U10 | [10 empty] | °C | USV-7130 | [30 empty] | U | 7130 |  | USY-7130
S-02115 | USV1-7135 | 243 | Control Valve |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | and supplied by FP 7001 vendor | [29 empty] | U | 7135 |  | USV-7135
S-02115 | USV-7135 | 243 | Control Valve |  | U10 | [10 empty] | °C | USV-7135 | [30 empty] | U | 7135 |  | USY-7135
S-02115 | FV1-2007 | 243.1 | Valve Body/Bonnet |  | P02 |  | 10"-PO-20-106-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | Globe | 8 " | Class 600 | Flange, RF | Monel | 10" / 12" | [25 empty] | F | 2007 |  | FV-2007
S-02115 | FV1-2009 | 243.1 | Valve Body/Bonnet |  | P02 |  | 4"-PO-20-105-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | Globe | 4 " | Class 600 | Flange, RF | Monel | 4" / 4" | [25 empty] | F | 2009 |  | FV-2009
S-02115 | FV1-2040 | 243.1 | Valve Body/Bonnet |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Globe | 3 " | Class 600 | Flange, RF | A 351 CF8C | 4" / 4" | [25 empty] | F | 2040 |  | FV-2040
S-02115 | FV1-2061 | 243.1 | Valve Body/Bonnet |  | P10 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Globe | 24 " | Class 600 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | F | 2061 |  | FV-2061
S-02115 | FV1-2072 | 243.1 | Valve Body/Bonnet |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Globe | 8 " | Class 600 | Flange, RF | A 216 WCB | 12" / 12" | [25 empty] | F | 2072 |  | FV-2072
S-02115 | FV1-2079 | 243.1 | Valve Body/Bonnet |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Globe | 1 1/2 " | Class 600 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | F | 2079 |  | FV-2079
S-02115 | FV1-2091 | 243.1 | Valve Body/Bonnet |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Globe | 10 " | Class 600 | Flange, RF | A 216 WCB | 12" / 12" | [25 empty] | F | 2091 |  | FV-2091
S-02115 | FV1-2150 | 243.1 | Valve Body/Bonnet |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Globe | 2 " | Class 600 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | F | 2150 |  | FV-2150
S-02115 | FV1-2233/1 | 243.1 | Valve Body/Bonnet |  | P13 |  | 3"-PRC-20-130-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | Globe | 1.5 " | Class 900 | Flange, RTJ | A 351 CF8 | 3" / 3" | [25 empty] | F | 2233 | 1 | FV-2233/1
S-02115 | FV1-2233/2 | 243.1 | Valve Body/Bonnet |  | P13 |  | 3"-BFW-70-103-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | F | 2233 | 2 | FV-2233/2
S-02115 | FV1-2417 | 243.1 | Valve Body/Bonnet |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 10 " | Class 1500 | Flange, RTJ | A 216 WCB | 12" / 12" | [25 empty] | F | 2417 |  | FV-2417
S-02115 | FV1-2531/1 | 243.1 | Valve Body/Bonnet |  | U01 |  | 10"-NG-20-104-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Globe | 6 " | Class 150 | Flange, RF | A 216 WCB | 10" / 10" | [25 empty] | F | 2531 | 1 | FV-2531/1
S-02115 | FV1-2531/2 | 243.1 | Valve Body/Bonnet |  | U01 |  | 24"-NG-20-112-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Globe | 10 " | Class 150 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | F | 2531 | 2 | FV-2531/2
S-02115 | FV1-2536 | 243.1 | Valve Body/Bonnet |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Globe | 16 " | Class 150 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | F | 2536 |  | FV-2536
S-02115 | FV1-3041 | 243.1 | Valve Body/Bonnet |  | P23 |  | 8"-BFW-70-101-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Globe | 6 " | Class 600 | Flange, RF | A 216 WCB | 8" / 8" | [25 empty] | F | 3041 |  | FV-3041
S-02115 | FV1-3169 | 243.1 | Valve Body/Bonnet |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Globe | 4 " | Class 900 | Flange, RTJ | A 216 WCB | 6" / 24" | [25 empty] | F | 3169 |  | FV-3169
S-02115 | FV1-3171 | 243.1 | Valve Body/Bonnet |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Globe | 6 " | Class 900 | Flange, RTJ | A 216 WCB | 6" / 6" | [25 empty] | F | 3171 |  | FV-3171
S-02115 | FV1-5020 | 243.1 | Valve Body/Bonnet |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | Globe | 1 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | F | 5020 |  | FV-5020
S-02115 | FV1-5041 | 243.1 | Valve Body/Bonnet |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | Globe | 8 " | Class 150 | Flange, RF | A 351 CF8 | 10" / 10" | [25 empty] | F | 5041 |  | FV-5041
S-02115 | FV1-5093 | 243.1 | Valve Body/Bonnet |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | Globe | 6 " | Class 150 | Flange, RF | A 216 WCB | 8" / 8" | [25 empty] | F | 5093 |  | FV-5093
S-02115 | FV1-5107 | 243.1 | Valve Body/Bonnet |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | Globe | 1 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | F | 5107 |  | FV-5107
S-02115 | FV1-5161 | 243.1 | Valve Body/Bonnet |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | Globe | 8 " | Class 150 | Flange, RF | A 216 WCB | 10" / 10" | [25 empty] | F | 5161 |  | FV-5161
S-02115 | FV1-5203 | 243.1 | Valve Body/Bonnet |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | Globe | 8 " | Class 150 | Flange, RF | A 216 WCB | 12" / 12" | [25 empty] | F | 5203 |  | FV-5203
S-02115 | FV1-5239 | 243.1 | Valve Body/Bonnet |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | Globe | 6 " | Class 300 | Flange, RF | A 216 WCB | 8" / 8" | [25 empty] | F | 5239 |  | FV-5239
S-02115 | FV1-5301 | 243.1 | Valve Body/Bonnet |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | Globe | 12 " | Class 150 | Flange, RF | A 217 WC9 | 16" / 20" | [25 empty] | F | 5301 |  | FV-5301
S-02115 | FV1-5321 | 243.1 | Valve Body/Bonnet |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | Globe | 10 " | Class 300 | Flange, RF | A 216 WCB | 12" / 12" | [25 empty] | F | 5321 |  | FV-5321
S-02115 | FV1-5336 | 243.1 | Valve Body/Bonnet |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Globe | 4 " | Class 300 | Flange, RF | A 216 WCB | 6" / 6" | [25 empty] | F | 5336 |  | FV-5336
S-02115 | FV1-5337 | 243.1 | Valve Body/Bonnet |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Globe | 6 " | Class 300 | Flange, RF | A 216 WCB | 6" / 6" | [25 empty] | F | 5337 |  | FV-5337
S-02115 | FV1-5367 | 243.1 | Valve Body/Bonnet |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | Globe | 2 " | Class 600 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | F | 5367 |  | FV-5367
S-02115 | FV1-5383 | 243.1 | Valve Body/Bonnet |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | Globe | 1 " | Class 150 | Flange, RF | A 351 CF8 | 2" / 2" | [25 empty] | F | 5383 |  | FV-5383
S-02115 | FV1-5441 | 243.1 | Valve Body/Bonnet |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | Globe | 1 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | F | 5441 |  | FV-5441
S-02115 | FV1-5501 | 243.1 | Valve Body/Bonnet |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | Globe | 3 " | Class 150 | Flange, RF | A 216 WCB | 6" / 6" | [25 empty] | F | 5501 |  | FV-5501
S-02115 | FV1-6031 | 243.1 | Valve Body/Bonnet |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 3 " | Class 600 | Flange, RF | A 216 WCB | 4" / 4" | [25 empty] | F | 6031 |  | FV-6031
S-02115 | FV1-6070 | 243.1 | Valve Body/Bonnet |  | P07 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Globe | 14 " | Class 600 | Flange, RF | A 216 WCB | 16" / 16" | [25 empty] | F | 6070 |  | FV-6070
S-02115 | FV1-6081 | 243.1 | Valve Body/Bonnet |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | Globe | 1 " | Class 900 | Flange, RTJ | A 351 CF8 | 2" / 2" | [25 empty] | F | 6081 |  | FV-6081
S-02115 | FV1-6082 | 243.1 | Valve Body/Bonnet |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | Globe | 1 " | Class 150 | Flange, RF | A 351 CF8 | 2" / 2" | [25 empty] | F | 6082 |  | FV-6082
S-02115 | FV1-6086 | 243.1 | Valve Body/Bonnet |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | Globe | By vendor " | Class 900 | Flange, RTJ | A 351 CF8 | 4" / 16" | [25 empty] | F | 6086 |  | FV-6086
S-02115 | FV1-7091 | 243.1 | Valve Body/Bonnet |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | Globe | 8 " | Class 150 | Flange, RF | A 351 CF8 | 8" / 8" | [25 empty] | F | 7091 |  | FV-7091
S-02115 | FV1-7141 | 243.1 | Valve Body/Bonnet |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 6 " | Class 1500 | Flange, RTJ | A 216 WCB | 8" / 8" | [25 empty] | F | 7141 |  | FV-7141
S-02115 | HV1-1003 | 243.1 | Valve Body/Bonnet |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Gate | 14 " | Class 600 | Flange, RF | A 216 WCB | 14" / 14" | [25 empty] | H | 1003 |  | HV-1003
S-02115 | HV1-2003 | 243.1 | Valve Body/Bonnet |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Gate | 10 " | Class 600 | Flange, RF | Monel | 10" / 10" | [25 empty] | H | 2003 |  | HV-2003
S-02115 | HV1-2031 | 243.1 | Valve Body/Bonnet |  | P03 |  | 2"-HPS-20-110-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 351 CF8C | 2" / 4" | [25 empty] | H | 2031 |  | HV-2031
S-02115 | HV1-2076 | 243.1 | Valve Body/Bonnet |  | P09 |  | 8"-HPS-20-114-F24-H |  |  | 52 | 44 | bar g |  | 343 | 410 | °C | Globe | 8 " | Class 600 | Flange, RF | A 216 WCB | 8" / 8" | [25 empty] | H | 2076 |  | HV-2076
S-02115 | HV1-2097 | 243.1 | Valve Body/Bonnet |  | P10 |  | 3"-HPS-20-112-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Globe | 2 " | Class 600 | Flange, RF | A 216 WCB | 3" / 4" | [25 empty] | H | 2097 |  | HV-2097
S-02115 | HV1-2098 | 243.1 | Valve Body/Bonnet |  | P10 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Gate | 12 " | Class 600 | Flange, RF | A 216 WCB | 12" / 12" | [25 empty] | H | 2098 |  | HV-2098
S-02115 | HV1-2334 | 243.1 | Valve Body/Bonnet |  | P16B |  | 2"-BD-20-101-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Globe, special | 1 " | Class 900 | Flange, RTJ or BW | A 217 WC9 | 2" / 6" | [25 empty] | H | 2334 |  | HV-2334
S-02115 | HV1-2335 | 243.1 | Valve Body/Bonnet |  | P16B |  | 2"-BD-20-139-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Globe, special | 1 " | Class 900 | Flange, RTJ or BW | A 217 WC9 | 2" / 6" | [25 empty] | H | 2335 |  | HV-2335
S-02115 | HV1-2371 | 243.1 | Valve Body/Bonnet |  | P18 |  | 6"-BFW-20-109-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | Globe, special | 4 " | Class 900 | Flange, RTJ | A 217 WC9 | 6" / 6" | [25 empty] | H | 2371 |  | HV-2371
S-02115 | HV1-2385 | 243.1 | Valve Body/Bonnet |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Globe, special | 1 " | Class 900 | Flange, RTJ or BW | A 217 WC9 | 2" / 12" | [25 empty] | H | 2385 |  | HV-2385
S-02115 | HV1-2545 | 243.1 | Valve Body/Bonnet |  | U01 |  | 2"-N-20-116-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Globe | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | H | 2545 |  | HV-2545
S-02115 | HV1-3010 | 243.1 | Valve Body/Bonnet |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 10 | bar g |  | 48 | 100 | °C | Globe | 2 " | Class 300 | Flange, RF | A 351 CF8 | 3" / 3" | [25 empty] | H | 3010 |  | HV-3010
S-02115 | HV1-3011 | 243.1 | Valve Body/Bonnet |  | P22 |  | 2"-SG-30-131-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Globe | By vendor " | Class 300 | Flange, RF | A 351 CF8 | 2" / 2" | [25 empty] | H | 3011 |  | HV-3011
S-02115 | HV1-3013 | 243.1 | Valve Body/Bonnet |  | P22 |  | 3"-HG-30-101-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | Globe | 1 " | Class 300 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | H | 3013 |  | HV-3013
S-02115 | HV1-3016 | 243.1 | Valve Body/Bonnet |  | P22 |  | 3"-PA-30-101-B24-N |  |  | 10.5 | 7.5 | bar g |  | 35 | 75 | °C | Globe | 3 " | Class 150 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | H | 3016 |  | HV-3016
S-02115 | HV1-3054 | 243.1 | Valve Body/Bonnet |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Globe, special | 1 " | Class 600 | Flange, RF | A 217 WC9 | 2" / 4" | [25 empty] | H | 3054 |  | HV-3054
S-02115 | HV1-3087 | 243.1 | Valve Body/Bonnet |  | P24 |  | 2"-CBD-30-107-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Globe, special | 1 1/2 " | Class 600 | Flange, RF | A 217 WC9 | 2" / 6" | [25 empty] | H | 3087 |  | HV-3087
S-02115 | HV1-3090 | 243.1 | Valve Body/Bonnet |  | P24 |  | 2"-CBD-30-105-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Globe, special | 1 1/2 " | Class 600 | Flange, RF | A 217 WC9 | 2" / 6" | [25 empty] | H | 3090 |  | HV-3090
S-02115 | HV1-3093 | 243.1 | Valve Body/Bonnet |  | P24 |  | 2"-CBD-30-103-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Globe, special | 1 1/2 " | Class 600 | Flange, RF | A 217 WC9 | 2" / 6" | [25 empty] | H | 3093 |  | HV-3093
S-02115 | HV1-3166 | 243.1 | Valve Body/Bonnet |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Globe | By vendor " | Class 900 | Flange, RTJ | A 351 CF8 | 4" / 12" | [25 empty] | H | 3166 |  | HV-3166
S-02115 | HV1-5338 | 243.1 | Valve Body/Bonnet |  | P40 |  | 3"-PMV-50-116-B24-P |  |  | 6 | 2.6 | bar g |  | 101 | 165 | °C | Globe | 3 " | Class 150 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | H | 5338 |  | HV-5338
S-02115 | HV1-6069 | 243.1 | Valve Body/Bonnet |  | P07 |  | 16"-PRG-60-107-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | Butterfly | 16 " | Class 600 | Flange, RF | A 216 WCB | 16" / 16" | [25 empty] | H | 6069 |  | HV-6069
S-02115 | LV1-2016 | 243.1 | Valve Body/Bonnet |  | P02 |  | 6"-HPC-20-102-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | Globe | 3 " | Class 600 | Flange, RF | A 217 WC9 | 6" / 8" | [25 empty] | L | 2016 |  | LV-2016
S-02115 | LV1-2372 | 243.1 | Valve Body/Bonnet |  | P19 |  | 6"-BFW-20-106-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 4 " | Class 1500 | Flange, RTJ | A 216 WCB | 6" / 6" | [25 empty] | L | 2372 |  | LV-2372
S-02115 | LV1-2403 | 243.1 | Valve Body/Bonnet |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | Globe | 2 " | Class 900 | Flange, RTJ | A 351 CF8 | 3" / 3" | [25 empty] | L | 2403 |  | LV-2403
S-02115 | LV1-2419 | 243.1 | Valve Body/Bonnet |  | P19 |  | 4"-PRC-20-123-F40-H |  |  | 30 | 26 | bar g |  | 159 | 200 | °C | Globe | 4 " | Class 600 | Flange, RF | A 351 CF8 | 4" / 4" | [25 empty] | L | 2419 |  | LV-2419
S-02115 | LV1-2441 | 243.1 | Valve Body/Bonnet |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | Globe | 4 " | Class 900 | Flange, RTJ | A 351 CF8 | 6" / 6" | [25 empty] | L | 2441 |  | LV-2441
S-02115 | LV1-2474 | 243.1 | Valve Body/Bonnet |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | Globe | 3 " | Class 900 | Flange, RTJ | A 351 CF8 | 4" / 4" | [25 empty] | L | 2474 |  | LV-2474
S-02115 | LV1-3161/A | 243.1 | Valve Body/Bonnet |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Globe | 8 " | Class 900 | Flange, RTJ | A 351 CF8 | 10" / 12" | [25 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV1-3161/B | 243.1 | Valve Body/Bonnet |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Globe | 8 " | Class 900 | Flange, RTJ | A 351 CF8 | 10" / 12" | [25 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV1-3192 | 243.1 | Valve Body/Bonnet |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | Globe | 8 " | Class 150 | Flange, RF | A 351 CF8 | 10" / 14" | [25 empty] | L | 3192 |  | LV-3192
S-02115 | LV1-5070 | 243.1 | Valve Body/Bonnet |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | Globe | 3 " | Class 300 | Flange, RF | A 217 WC9 | 4" / 4" | [25 empty] | L | 5070 |  | LV-5070
S-02115 | LV1-5501 | 243.1 | Valve Body/Bonnet |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | Globe | 2 " | Class 600 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | L | 5501 |  | LV-5501
S-02115 | LV1-6021/A | 243.1 | Valve Body/Bonnet |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | Globe | 6 " | Class 600 | Flange, RF | A 216 WCB | 10" / 10" | [25 empty] | L | 6021 | A | LV-6021/A
S-02115 | LV1-6021/B | 243.1 | Valve Body/Bonnet |  | P05 |  | 18"-MPC-60-104-F24-H |  |  | 47 | 32.5 | bar g |  | 240 | 260 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 18" / 34" | [25 empty] | L | 6021 | B | LV-6021/B
S-02115 | LV1-6082 | 243.1 | Valve Body/Bonnet |  | P08 |  | 4"-BD-60-111-B40-N |  |  | 9 | 1.5 | bar g |  | 65 | 125 | °C | Globe | 3 " | Class 150 | Flange, RF | A 351 CF8 | 4" / 4" | [25 empty] | L | 6082 |  | LV-6082
S-02115 | LV1-7251 | 243.1 | Valve Body/Bonnet |  | U16 |  | 3"-BD-70-111-B24-N |  |  | 10.5 | 8 | bar g |  | 173 | 200 | °C | Globe | 2 " | Class 150 | Flange, RF | A 217 WC9 | 3" / 4" | [25 empty] | L | 7251 |  | LV-7251
S-02115 | PV1-1006 | 243.1 | Valve Body/Bonnet |  | P01 |  | 14"-NG-10-102-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Globe | 10 " | Class 600 | Flange, RF | A 216 WCB | 14" / 14" | [25 empty] | P | 1006 |  | PV-1006
S-02115 | PV1-1011 | 243.1 | Valve Body/Bonnet |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Globe | 6 " | Class 600 | Flange, RF | A 216 WCB | 8" / 24" | [25 empty] | P | 1011 |  | PV-1011
S-02115 | PV1-1045 | 243.1 | Valve Body/Bonnet |  | P04 |  | 8"-PRG-10-108-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 8"/16" | [25 empty] | P | 1045 |  | PV-1045
S-02115 | PV1-2015 | 243.1 | Valve Body/Bonnet |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Globe | 4 " | Class 600 | Flange, RF | A 216 WCB | 6" / 6" | [25 empty] | P | 2015 |  | PV-2015
S-02115 | PV1-2073 | 243.1 | Valve Body/Bonnet |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 12" / 24" | [25 empty] | P | 2073 |  | PV-2073
S-02115 | PV1-2361 | 243.1 | Valve Body/Bonnet |  | P17 |  | 8"-HHPS-20-2054-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Globe | By vendor " | Class 1500 | Flange, RTJ | A 217 WC6 | 8"/20" | [25 empty] | P | 2361 |  | PV-2361
S-02115 | PV1-2363 | 243.1 | Valve Body/Bonnet |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Globe | 24 " | Class 1500 | Flange, RTJ | A 217 WC6 | 24" / 24" | [25 empty] | P | 2363 |  | PV-2363
S-02115 | PV1-2406 | 243.1 | Valve Body/Bonnet |  | P19 |  | 18"-RFG-20-118-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Globe | By vendor " | Class 300 | Flange, RF | A 351 CF8 | 18" / 24" | [25 empty] | P | 2406 |  | PV-2406
S-02115 | PV1-2481 | 243.1 | Valve Body/Bonnet |  | P21 |  | 18"-SG-20-105-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Globe | By vendor " | Class 300 | Flange, RF | A 351 CF8 | 18" / 28" | [25 empty] | P | 2481 |  | PV-2481
S-02115 | PV1-2536 | 243.1 | Valve Body/Bonnet |  | U01 |  | 14"-PG-20-129-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Globe | By vendor " | Class 150 | Flange, RF | A 216 WCB | 14" / 14" | [25 empty] | P | 2536 |  | PV-2536
S-02115 | PV1-2551 | 243.1 | Valve Body/Bonnet |  | U01 |  | 2"NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Downstream pressure regulator | 1 1/2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 2551 |  | PCV-2551
S-02115 | PV1-2575 | 243.1 | Valve Body/Bonnet |  | U02 |  | 8"-N-20-105-B24-P |  |  | 10.5 | 6 | bar g |  | 70 | 110 | °C | Globe | 8 " | Class 150 | Flange, RF | A 216 WCB | 8" / 8" | [25 empty] | P | 2575 |  | PDV-2575
S-02115 | PV1-2603 | 243.1 | Valve Body/Bonnet |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | Globe | 1.5 " | Class 300 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | P | 2603 |  | PV-2603
S-02115 | PV1-2608 | 243.1 | Valve Body/Bonnet |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Globe | 1.5 " | Class 900 | Flange, RTJ | A 216 WCB | 3" / 3" | [25 empty] | P | 2608 |  | PV-2608
S-02115 | PV1-3008 | 243.1 | Valve Body/Bonnet |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Downstream pressure regulator | 1.5 " | Class 300 | Flange, RF | A 351 CF8 | 3" / 3" | [25 empty] | P | 3008 |  | PCV-3008
S-02115 | PV1-3042 | 243.1 | Valve Body/Bonnet |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Globe | 24 " | Class 600 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | P | 3042 |  | PV-3042
S-02115 | PV1-3166 | 243.1 | Valve Body/Bonnet |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Globe | By vendor " | Class 900 | Flange, RTJ | A 351 CF8 | 4" / 12" | [25 empty] | P | 3166 |  | PV-3166
S-02115 | PV1-3194 | 243.1 | Valve Body/Bonnet |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Globe | 6 " | Class 150 | Flange, RF | A 351 CF8 | 8" / 8" | [25 empty] | P | 3194 |  | PV-3194
S-02115 | PV1-5009 | 243.1 | Valve Body/Bonnet |  | P29 |  | 2"-N-50-101-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Downstream pressure regulator | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5009 |  | PCV-5009
S-02115 | PV1-5069 | 243.1 | Valve Body/Bonnet |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Globe | 10 " | Class 300 | Flange, RF | A 216 WCB | 14" / 14" | [25 empty] | P | 5069 |  | PV-5069
S-02115 | PV1-5091/A | 243.1 | Valve Body/Bonnet |  | P32 |  | 2"-N-50-104-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Globe | 1 1/2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5091 | A | PV-5091/A
S-02115 | PV1-5091/B | 243.1 | Valve Body/Bonnet |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | Globe | 4 " | Class 150 | Flange, RF | A 216 WCB | 6" / 6" | [25 empty] | P | 5091 | B | PV-5091/B
S-02115 | PV1-5109 | 243.1 | Valve Body/Bonnet |  | P32 |  | 4"-PG-50-103-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | Globe | 4 " | Class 150 | Flange, RF | A 216 WCB | 4" / 4" | [25 empty] | P | 5109 |  | PV-5109
S-02115 | PV1-5207/A | 243.1 | Valve Body/Bonnet |  | P36 |  | 2"-N-50-107-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Globe | 1 1/2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5207 | A | PV-5207/A
S-02115 | PV1-5207/B | 243.1 | Valve Body/Bonnet |  | P36 |  | 2"-VA-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Globe | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5207 | B | PV-5207/B
S-02115 | PV1-5395 | 243.1 | Valve Body/Bonnet |  | P43 |  | 2"-N-50-113-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Downstream pressure regulator | 1 1/2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5395 |  | PCV-5395
S-02115 | PV1-5412 | 243.1 | Valve Body/Bonnet |  | P44 |  | 2"-N-50-108-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Downstream pressure regulator | 1 1/2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5412 |  | PCV-5412
S-02115 | PV1-5445 | 243.1 | Valve Body/Bonnet |  | P45 |  | 2"-N-50-111-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Downstream pressure regulator | 1 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | P | 5445 |  | PCV-5445
S-02115 | PV1-6025 | 243.1 | Valve Body/Bonnet |  | P06 |  | 24"-MPS-70-101-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Globe | 20 " | Class 600 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | P | 6025 |  | PV-6025
S-02115 | PV1-7002/A | 243.1 | Valve Body/Bonnet |  | U03 |  | 10"-HHPS-70-115-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Steam conditioning valve PRDS | By vendor | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 10" / 12" | [25 empty] | P | 7002 | A | PV-7002/A
S-02115 | PV1-7002/B | 243.1 | Valve Body/Bonnet |  | U03 |  | 24"-HHPS-70-114-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Steam conditioning valve PRDS | By vendor | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 24" / 28" | [25 empty] | P | 7002 | B | PV-7002/B
S-02115 | PV1-7002/C | 243.1 | Valve Body/Bonnet |  | U03 |  | 24"-HHPS-70-113-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Steam conditioning valve PRDS | By vendor | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 24" / 28" | [25 empty] | P | 7002 | C | PV-7002/C
S-02115 | PV1-7004 | 243.1 | Valve Body/Bonnet |  | U03 |  | 16"-HPS-70-108-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 16"/28" | [25 empty] | P | 7004 |  | PV-7004
S-02115 | PV1-7025/A | 243.1 | Valve Body/Bonnet |  | U04 |  | 18"-HHPS-70-121-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Steam conditioning valve PRDS | By vendor | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 18" / 24" | [25 empty] | P | 7025 | A | PV-7025/A
S-02115 | PV1-7025/B | 243.1 | Valve Body/Bonnet |  | U04 |  | 18"-HHPS-70-120-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Steam conditioning valve PRDS | By vendor | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 18" / 24" | [25 empty] | P | 7025 | B | PV-7025/B
S-02115 | PV1-7028 | 243.1 | Valve Body/Bonnet |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | Globe | 20 " | Class 600 | Flange, RF | A 217 WC6 | 24" / 24" | [25 empty] | P | 7028 |  | PV-7028
S-02115 | PV1-7031/A | 243.1 | Valve Body/Bonnet |  | U05 |  | 24"-HPS-70-130-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Steam conditioning valve PRDS | By vendor | Class 600 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | P | 7031 | A | PV-7031/A
S-02115 | PV1-7031/B | 243.1 | Valve Body/Bonnet |  | U05 |  | 24"-HPS-70-131-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Steam conditioning valve PRDS | By vendor | Class 600 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | P | 7031 | B | PV-7031/B
S-02115 | PV1-7031/C | 243.1 | Valve Body/Bonnet |  | U05 |  | 10"-MPS-70-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 10" / 16" | [25 empty] | P | 7031 | C | PV-7031/C
S-02115 | PV1-7031/D | 243.1 | Valve Body/Bonnet |  | U05 |  | 10"-MPS-70-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 10" / 16" | [25 empty] | P | 7031 | D | PV-7031/D
S-02115 | PV1-7034 | 243.1 | Valve Body/Bonnet |  | U05 |  | 14"-MPS-70-121-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Globe | By vendor " | Class 600 | Flange, RF | A 216 WCB | 14" / 24" | [25 empty] | P | 7034 |  | PV-7034
S-02115 | PV1-7051/A | 243.1 | Valve Body/Bonnet |  | U06 |  | 16"-HPS-70-120-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Steam conditioning valve PRDS | By vendor | Class 600 | Flange, RF | A 216 WCB | 16" / 24" | [25 empty] | P | 7051 | A | PV-7051/A
S-02115 | PV1-7051/B | 243.1 | Valve Body/Bonnet |  | U06 |  | 16"-HPS-70-121-F34-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Steam conditioning valve PRDS | By vendor | Class 600 | Flange, RF | A 216 WCB | 16" / 24" | [25 empty] | P | 7051 | B | PV-7051/B
S-02115 | PV1-7056 | 243.1 | Valve Body/Bonnet |  | U06 |  | 24"-LPS-70-109-D24-P |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Globe | By vendor " | Class 300 | Flange, RF | A 216 WCB | 24" / 32" | [25 empty] | P | 7056 |  | PV-7056
S-02115 | PV1-7094 | 243.1 | Valve Body/Bonnet |  | U09 |  | 18"-LPS-70-127-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Globe | 12 " | Class 300 | Flange, RF | A 216 WCB | 18" / 18" | [25 empty] | P | 7094 |  | PV-7094
S-02115 | PV1-7101 | 243.1 | Valve Body/Bonnet |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | Globe | By vendor " | Class 150 | Flange, RF | A 216 WCB | 24" / 24" | [25 empty] | P | 7101 |  | PV-7101
S-02115 | TV1-2220 | 243.1 | Valve Body/Bonnet |  | P12 |  | 8"-NG-10-106-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Butterfly | 6 " | Class 600 | Wafer, RF | A 216 WCB | 8" / 8" | [25 empty] | T | 2220 |  | TV-2220
S-02115 | TV1-2457 | 243.1 | Valve Body/Bonnet |  | P20 |  | 16"-RFG-20-127-D40-P |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | Butterfly | 16 " | Class 300 | Wafer, RF | A 351 CF8 | 16" / 16" | [25 empty] | T | 2457 |  | TV-2457
S-02115 | TV1-3113 | 243.1 | Valve Body/Bonnet |  | P25 |  | 10"-SG-30-926-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Butterfly | 10 " | Class 1500 | Wafer, RTJ | A 351 CF8 | 10" / 10" | [25 empty] | T | 3113 |  | TV-3113
S-02115 | TV1-3116 | 243.1 | Valve Body/Bonnet |  | P25 |  | 10"-SG-30-931-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Butterfly | 10 " | Class 1500 | Wafer, RTJ | A 351 CF8 | 10" / 10" | [25 empty] | T | 3116 |  | TV-3116
S-02115 | TV1-3118 | 243.1 | Valve Body/Bonnet |  | P25 |  | 10"-SG-30-937-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Butterfly | 10 " | Class 1500 | Wafer, RTJ | A 351 CF8 | 10" / 10" | [25 empty] | T | 3118 |  | TV-3118
S-02115 | TV1-5064 | 243.1 | Valve Body/Bonnet |  | P30 |  | 16"-RFG-50-103-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Butterfly | 16 " | Class 300 | Wafer, RF | A 351 CF8 | 16" / 16" | [25 empty] | T | 5064 |  | TV-5064
S-02115 | TV1-5277 | 243.1 | Valve Body/Bonnet |  | P38 |  | 18"-RFG-50-125-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Butterfly | 18 " | Class 300 | Wafer, RF | A 351 CF8 | 18" / 18" | [25 empty] | T | 5277 |  | TV-5277
S-02115 | TV1-7002 | 243.1 | Valve Body/Bonnet |  | U03 |  | 2"-BFW-70-104-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 1 " | Class 1500 | Flange, RTJ or BW | A 216 WCB | 2" / 2" | [25 empty] | T | 7002 |  | TV-7002
S-02115 | TV1-7003 | 243.1 | Valve Body/Bonnet |  | U03 |  | 3"-BFW-70-143-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 3" / 3" | [25 empty] | T | 7003 |  | TV-7003
S-02115 | TV1-7004 | 243.1 | Valve Body/Bonnet |  | U03 |  | 3"-BFW-70-141-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 1500 | Flange, RTJ or BW | A 217 WC6 | 3" / 3" | [25 empty] | T | 7004 |  | TV-7004
S-02115 | TV1-7025/A | 243.1 | Valve Body/Bonnet |  | U04 |  | 2"-BFW-70-152-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 216 WCB | 2"/2" | [25 empty] | T | 7025 | A | TV-7025/A
S-02115 | TV1-7025/B | 243.1 | Valve Body/Bonnet |  | U04 |  | 2"-BFW-70-154-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 216 WCB | 2"/2" | [25 empty] | T | 7025 | B | TV-7025/B
S-02115 | TV1-7026 | 243.1 | Valve Body/Bonnet |  | U04 |  | 2"-BFW-70-112-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 1 " | Class 1500 | Flange, RTJ or BW | A 216 WCB | 2" / 2" | [25 empty] | T | 7026 |  | TV-7026
S-02115 | TV1-7027 | 243.1 | Valve Body/Bonnet |  | U04 |  | 2"-BFW-70-156-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Globe | 1 " | Class 1500 | Flange, RTJ or BW | A 216 WCB | 2" / 2" | [25 empty] | T | 7027 |  | TV-7027
S-02115 | TV1-7032 | 243.1 | Valve Body/Bonnet |  | U05 |  | 2"-BFW-70-115-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 217 WC6 | 2" / 2" | [25 empty] | T | 7032 |  | TV-7032
S-02115 | TV1-7033 | 243.1 | Valve Body/Bonnet |  | U05 |  | 2"-BFW-70-108-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 217 WC6 | 2" / 2" | [25 empty] | T | 7033 |  | TV-7033
S-02115 | TV1-7052 | 243.1 | Valve Body/Bonnet |  | U06 |  | 2"-BFW-70-121-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | T | 7052 |  | TV-7052
S-02115 | TV1-7053 | 243.1 | Valve Body/Bonnet |  | U06 |  | 2"-BFW-70-119-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Globe | 1.5 " | Class 600 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | T | 7053 |  | TV-7053
S-02115 | TV1-7071/A | 243.1 | Valve Body/Bonnet |  | U07 |  | 2"-BFW-70-124-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Desuperheater spraynozzle | By vendor | Class 600 | Flange, RF | A 216 WCB | Water-2"/Steam- by vendor | [25 empty] | T | 7071 | A | TV-7071/A
S-02115 | TV1-7071/B | 243.1 | Valve Body/Bonnet |  | U07 |  | 2"-BFW-70-145-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Desuperheater spraynozzle | By vendor | Class 600 | Flange, RF | A 216 WCB | Water-2"/Steam- by vendor | [25 empty] | T | 7071 | B | TV-7071/B
S-02115 | USV1-1001 | 243.1 | Valve Body/Bonnet |  | P01 |  | 2"-OW-10-103-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Ball | 2 " | Class 600 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 1001 |  | USV-1001
S-02115 | USV1-2010 | 243.1 | Valve Body/Bonnet |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | Butterfly | 12 " | Class 600 | Wafer, RF | Monel | 12" / 12" | [25 empty] | U | 2010 |  | USV-2010
S-02115 | USV1-2021 | 243.1 | Valve Body/Bonnet |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Butterfly | 6 " | Class 600 | Wafer, RF | A 216 WCB | 6" / 6" | [25 empty] | U | 2021 |  | USV-2021
S-02115 | USV1-2038 | 243.1 | Valve Body/Bonnet |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Globe | 4 " | Class 600 | Flange, RF | A 351 CF8C | 4" / 4" | [25 empty] | U | 2038 |  | USV-2038
S-02115 | USV1-2043 | 243.1 | Valve Body/Bonnet |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Globe | 2 " | Class 600 | Flange, RF | Monel | 3" / 4" | [25 empty] | U | 2043 |  | USV-2043
S-02115 | USV1-2045 | 243.1 | Valve Body/Bonnet |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Butterfly | 16 " | Class 600 | Wafer, RF | Monel | 16" / 16" | [25 empty] | U | 2045 |  | USV-2045
S-02115 | USV1-2048 | 243.1 | Valve Body/Bonnet |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Butterfly | 16 " | Class 600 | Wafer, RF | Monel | 16" / 16" | [25 empty] | U | 2048 |  | USV-2048
S-02115 | USV1-2049 | 243.1 | Valve Body/Bonnet |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Globe | 1 1/2 " | Class 600 | Flange, RF | Monel | 1 1/2" / 2" | [25 empty] | U | 2049 |  | USV-2049
S-02115 | USV1-2092 | 243.1 | Valve Body/Bonnet |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | Butterfly | 24 " | Class 600 | Wafer, RF | A 216 WCB | 24" / 24" | [25 empty] | U | 2092 |  | USV-2092
S-02115 | USV1-2093 | 243.1 | Valve Body/Bonnet |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | Butterfly | 24 " | Class 600 | Wafer, RF | A 216 WCB | 24" / 24" | [25 empty] | U | 2093 |  | USV-2093
S-02115 | USV1-2094 | 243.1 | Valve Body/Bonnet |  | P10 |  | 2"-PRG-20-109-F24-H |  |  | 55 | 41.1 | bar g |  | 262 | 290 | °C | Globe | 1 " | Class 600 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 2094 |  | USV-2094
S-02115 | UV1-2125 | 243.1 | Valve Body/Bonnet |  | P11 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | Butterfly | 24 " | Class 150 | Wafer, RF | A 351 CF8 | 24" / 24" | [25 empty] | U | 2125 |  | UV-2125
S-02115 | UV1-2233 | 243.1 | Valve Body/Bonnet |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | Ball | 3 " | Class 900 | Flange, RTJ | A 351 CF8 | 3" / 3" | [25 empty] | U | 2233 |  | UV-2233
S-02115 | USV1-2381 | 243.1 | Valve Body/Bonnet |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Ball | 2 " | Class 900 | Flange, RTJ or BW | A 216 WCB | 2" / 2" | [25 empty] | U | 2381 |  | USV-2381
S-02115 | USV1-2482 | 243.1 | Valve Body/Bonnet |  | P21 |  | 12"-SG-20-106-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Butterfly | 12 " | Class 300 | Flange, RF | A 351 CF8 | 12" / 12" | [25 empty] | U | 2482 |  | USV-2482
S-02115 | USV1-2541 | 243.1 | Valve Body/Bonnet |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Butterfly | 28 " | Class 150 | Wafer, RF | A 216 WCB | 28" / 28" | [25 empty] | U | 2541 |  | USV-2541
S-02115 | USV1-2542 | 243.1 | Valve Body/Bonnet |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Butterfly | 28 " | Class 150 | Wafer, RF | A 216 WCB | 28" / 28" | [25 empty] | U | 2542 |  | USV-2542
S-02115 | USV1-2543 | 243.1 | Valve Body/Bonnet |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Ball | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 2543 |  | USV-2543
S-02115 | USV1-2544 | 243.1 | Valve Body/Bonnet |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | Butterfly | 24 " | Class 150 | Wafer, RF | A 216 WCB | 24" / 24" | [25 empty] | U | 2544 |  | USV-2544
S-02115 | USV1-2545 | 243.1 | Valve Body/Bonnet |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | Ball | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 2545 |  | USV-2545
S-02115 | USV1-2547 | 243.1 | Valve Body/Bonnet |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Ball | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 2547 |  | USV-2547
S-02115 | USV1-2548 | 243.1 | Valve Body/Bonnet |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Ball | 2 " | Class 150 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 2548 |  | USV-2548
S-02115 | USV1-2549 | 243.1 | Valve Body/Bonnet |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Ball | 1 1/2 " | Class 150 | Flange, RF | A 216 WCB | 1 1/2" / 2" | [25 empty] | U | 2549 |  | USV-2549
S-02115 | USV1-3018 | 243.1 | Valve Body/Bonnet |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C | Ball | 3 " | Class 300 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | U | 3018 |  | USV-3018
S-02115 | USV1-3052 | 243.1 | Valve Body/Bonnet |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Ball | 2 " | Class 600 | Flange, RF | A 216 WCB | 2" / 2" | [25 empty] | U | 3052 |  | USV-3052
S-02115 | USV1-3172 | 243.1 | Valve Body/Bonnet |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Butterfly | 10 " | Class 900 | Wafer, RTJ | A 351 CF8 | 10" / 10" | [25 empty] | U | 3172 |  | USV-3172
S-02115 | UV1-5021 | 243.1 | Valve Body/Bonnet |  | P29 |  | 24"-VA-50-140-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | Butterfly | 24 " | Class 150 | Wafer, RF | A 351 CF8 | 24" / 24" | [25 empty] | U | 5021 |  | UV-5021
S-02115 | USV1-5302 | 243.1 | Valve Body/Bonnet |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Butterfly | 32 " | Class 300 | Wafer, RF | A 216 WCB | 32" / 32" | [25 empty] | U | 5302 |  | USV-5302
S-02115 | USV1-5391 | 243.1 | Valve Body/Bonnet |  | P43 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Butterfly | 10 " | Class 300 | Wafer, RF | A 216 WCB | 10" / 10" | [25 empty] | U | 5391 |  | USV-5391
S-02115 | USV1-5392 | 243.1 | Valve Body/Bonnet |  | P43 |  | 10"-PMP-50-144-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Butterfly | 10 " | Class 300 | Wafer, RF | A 216 WCB | 10" / 10" | [25 empty] | U | 5392 |  | USV-5392
S-02115 | USV1-5393 | 243.1 | Valve Body/Bonnet |  | P43 |  | 3"-PMP-50-158-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | Ball | 3 " | Class 150 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | U | 5393 |  | USV-5393
S-02115 | USV1-5420 | 243.1 | Valve Body/Bonnet |  | P44 |  | 10"-PMP-50-152-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | Butterfly | 10 " | Class 150 | Wafer, RF | A 216 WCB | 10" / 10" | [25 empty] | U | 5420 |  | USV-5420
S-02115 | USV1-5421 | 243.1 | Valve Body/Bonnet |  | P44 |  | 3"-PMP-50-156-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | Ball | 3 " | Class 150 | Flange, RF | A 216 WCB | 3" / 3" | [25 empty] | U | 5421 |  | USV-5421
S-02115 | USV1-5422 | 243.1 | Valve Body/Bonnet |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | Butterfly | 10 " | Class 150 | Wafer, RF | A 216 WCB | 10" / 10" | [25 empty] | U | 5422 |  | USV-5422
S-02115 | UV1-6035 | 243.1 | Valve Body/Bonnet |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Butterfly | 8 " | Class 900 | Wafer, RTJ | A 351 CF8 | 8" / 8" | [25 empty] | U | 6035 |  | UV-6035
S-02115 | USV1-6081 | 243.1 | Valve Body/Bonnet |  | P08 |  | 2"-BD-60-109-G40-P |  |  | 57 | 1 | bar g |  | 73 | 260 | °C | Ball | 2 " | Class 900 | Flange, RTJ | A 351 CF8 | 2" / 2" | [25 empty] | U | 6081 |  | USV-6081
S-02115 | USV1-6082 | 243.1 | Valve Body/Bonnet |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | Ball | 4 " | Class 900 | Flange, RTJ | A 351 CF8 | 4" / 4" | [25 empty] | U | 6082 |  | USV-6082
S-02115 | FZ-2233 | 243.11 | Spray Nozzle |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | Variable section spray nozzle | : | 24"/A 216 WCB | 42.1 / 46 bar g | 267 / 300 °C |  |  | See FV-2233-1 and -2 | [23 empty] | F | 2233 |  | FZ-2233
S-02115 | FZ-6058 | 243.11 | Spray Nozzle |  | P07 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Variable section spray nozzle | : | 16"/ Carbon steel / F24 | 47.3 / 55 bar g | 365 / 410 °C |  |  |  | 2"/ Carbon steel / F24 | 53 / 60 bar g | 50 / 70 °C | [20 empty] | F | 6058 |  | FZ-6058
S-02115 | TZ-7025 | 243.11 | Spray Nozzle |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | Variable section spray nozzle | : | 24"/A 217 WC6 | 42 / 52 bar g | 345 / 470 °C |  |  | See TV-7025-A and -B | [23 empty] | T | 7025 |  | TZ-7025
S-02115 | FV2-2007 | 243.2 | Trim |  | P02 |  | 10"-PO-20-106-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | 452 | Single seated | Equal % | Monel | IV | [26 empty] | F | 2007 |  | FV-2007
S-02115 | FV2-2009 | 243.2 | Trim |  | P02 |  | 4"-PO-20-105-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | 136 | Single seated | Equal % | Monel | IV | [26 empty] | F | 2009 |  | FV-2009
S-02115 | FV2-2040 | 243.2 | Trim |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 43 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 2040 |  | FV-2040
S-02115 | FV2-2061 | 243.2 | Trim |  | P10 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 5850 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 2061 |  | FV-2061
S-02115 | FV2-2072 | 243.2 | Trim |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 636 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 2072 |  | FV-2072
S-02115 | FV2-2079 | 243.2 | Trim |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 15 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 2079 |  | FV-2079
S-02115 | FV2-2091 | 243.2 | Trim |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 1109 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 2091 |  | FV-2091
S-02115 | FV2-2150 | 243.2 | Trim |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 29 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 2150 |  | FV-2150
S-02115 | FV2-2233/1 | 243.2 | Trim |  | P13 |  | 3"-PRC-20-130-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 6.1, no oversizing | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | F | 2233 | 1 | FV-2233/1
S-02115 | FV2-2233/2 | 243.2 | Trim |  | P13 |  | 3"-BFW-70-103-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 7.0, no oversizing | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | F | 2233 | 2 | FV-2233/2
S-02115 | FV2-2417 | 243.2 | Trim |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 452 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 2417 |  | FV-2417
S-02115 | FV2-2531/1 | 243.2 | Trim |  | U01 |  | 10"-NG-20-104-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 145 | Single seated | Linear | AISI 316 | IV | [26 empty] | F | 2531 | 1 | FV-2531/1
S-02115 | FV2-2531/2 | 243.2 | Trim |  | U01 |  | 24"-NG-20-112-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 432 | Single seated | Linear | AISI 316 | IV | [26 empty] | F | 2531 | 2 | FV-2531/2
S-02115 | FV2-2536 | 243.2 | Trim |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 1406 | Single seated | Linear | AISI 316 | IV | [26 empty] | F | 2536 |  | FV-2536
S-02115 | FV2-3041 | 243.2 | Trim |  | P23 |  | 8"-BFW-70-101-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 356 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 3041 |  | FV-3041
S-02115 | FV2-3169 | 243.2 | Trim |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 49.3 | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | F | 3169 |  | FV-3169
S-02115 | FV2-3171 | 243.2 | Trim |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 360 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 3171 |  | FV-3171
S-02115 | FV2-5020 | 243.2 | Trim |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 7.2 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5020 |  | FV-5020
S-02115 | FV2-5041 | 243.2 | Trim |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 416 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5041 |  | FV-5041
S-02115 | FV2-5093 | 243.2 | Trim |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 274 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5093 |  | FV-5093
S-02115 | FV2-5107 | 243.2 | Trim |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 1.6 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5107 |  | FV-5107
S-02115 | FV2-5161 | 243.2 | Trim |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 673 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5161 |  | FV-5161
S-02115 | FV2-5203 | 243.2 | Trim |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 509 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5203 |  | FV-5203
S-02115 | FV2-5239 | 243.2 | Trim |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 203 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5239 |  | FV-5239
S-02115 | FV2-5301 | 243.2 | Trim |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 415 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | F | 5301 |  | FV-5301
S-02115 | FV2-5321 | 243.2 | Trim |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 906 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5321 |  | FV-5321
S-02115 | FV2-5336 | 243.2 | Trim |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 109 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5336 |  | FV-5336
S-02115 | FV2-5337 | 243.2 | Trim |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 396 (full size trim) | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5337 |  | FV-5337
S-02115 | FV2-5367 | 243.2 | Trim |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 25.2 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5367 |  | FV-5367
S-02115 | FV2-5383 | 243.2 | Trim |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | 11 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5383 |  | FV-5383
S-02115 | FV2-5441 | 243.2 | Trim |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 7.0, no oversizing | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5441 |  | FV-5441
S-02115 | FV2-5501 | 243.2 | Trim |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | 44 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 5501 |  | FV-5501
S-02115 | FV2-6031 | 243.2 | Trim |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 38 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 6031 |  | FV-6031
S-02115 | FV2-6070 | 243.2 | Trim |  | P07 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 1020 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 6070 |  | FV-6070
S-02115 | FV2-6081 | 243.2 | Trim |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 1.5 | Anti cavitation trim | Linear | AISI 316, hard faced | IV | [26 empty] | F | 6081 |  | FV-6081
S-02115 | FV2-6082 | 243.2 | Trim |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | 10 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | F | 6082 |  | FV-6082
S-02115 | FV2-6086 | 243.2 | Trim |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 39 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | F | 6086 |  | FV-6086
S-02115 | FV2-7091 | 243.2 | Trim |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 566 | Single seated | Equal % | AISI 316 | IV | [26 empty] | F | 7091 |  | FV-7091
S-02115 | FV2-7141 | 243.2 | Trim |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 52 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | F | 7141 |  | FV-7141
S-02115 | HV2-1003 | 243.2 | Trim |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Line size | WDF | On/Off | Min. same as body | V | [26 empty] | H | 1003 |  | HV-1003
S-02115 | HV2-2003 | 243.2 | Trim |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Line size | WDF | On/Off | Monel | V | [26 empty] | H | 2003 |  | HV-2003
S-02115 | HV2-2031 | 243.2 | Trim |  | P03 |  | 2"-HPS-20-110-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 12 | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | H | 2031 |  | HV-2031
S-02115 | HV2-2076 | 243.2 | Trim |  | P09 |  | 8"-HPS-20-114-F24-H |  |  | 52 | 44 | bar g |  | 343 | 410 | °C | 447 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | H | 2076 |  | HV-2076
S-02115 | HV2-2097 | 243.2 | Trim |  | P10 |  | 3"-HPS-20-112-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | 9.6 | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | H | 2097 |  | HV-2097
S-02115 | HV2-2098 | 243.2 | Trim |  | P10 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Line size | WDF | On/Off | Min. same as body | IV | [26 empty] | H | 2098 |  | HV-2098
S-02115 | HV2-2334 | 243.2 | Trim |  | P16B |  | 2"-BD-20-101-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 17.5 | Single seated | Quick opening | AISI 316, hard faced | IV | [26 empty] | H | 2334 |  | HV-2334
S-02115 | HV2-2335 | 243.2 | Trim |  | P16B |  | 2"-BD-20-139-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 17.5 | Single seated | Quick opening | AISI 316, hard faced | IV | [26 empty] | H | 2335 |  | HV-2335
S-02115 | HV2-2371 | 243.2 | Trim |  | P18 |  | 6"-BFW-20-109-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | 20.4 | Multi stage | Linear | AISI 316, hard faced | IV | [26 empty] | H | 2371 |  | HV-2371
S-02115 | HV2-2385 | 243.2 | Trim |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 3.2 | Multi stage | Linear | AISI 316, hard faced | IV | [26 empty] | H | 2385 |  | HV-2385
S-02115 | HV2-2545 | 243.2 | Trim |  | U01 |  | 2"-N-20-116-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 15 | Single seated | Linear | AISI 316 | IV | [26 empty] | H | 2545 |  | HV-2545
S-02115 | HV2-3010 | 243.2 | Trim |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 10 | bar g |  | 48 | 100 | °C | 15 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | H | 3010 |  | HV-3010
S-02115 | HV2-3011 | 243.2 | Trim |  | P22 |  | 2"-SG-30-131-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 21 | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | H | 3011 |  | HV-3011
S-02115 | HV2-3013 | 243.2 | Trim |  | P22 |  | 3"-HG-30-101-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 1.7 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | H | 3013 |  | HV-3013
S-02115 | HV2-3016 | 243.2 | Trim |  | P22 |  | 3"-PA-30-101-B24-N |  |  | 10.5 | 7.5 | bar g |  | 35 | 75 | °C | 108 | Single seated | Linear | AISI 316 | IV | [26 empty] | H | 3016 |  | HV-3016
S-02115 | HV2-3054 | 243.2 | Trim |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 3 | Multi stage | Linear | AISI 316, hard faced | IV | [26 empty] | H | 3054 |  | HV-3054
S-02115 | HV2-3087 | 243.2 | Trim |  | P24 |  | 2"-CBD-30-107-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | 36.5 | Single seated | Quick opening | AISI 316, hard faced | IV | [26 empty] | H | 3087 |  | HV-3087
S-02115 | HV2-3090 | 243.2 | Trim |  | P24 |  | 2"-CBD-30-105-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | 36.5 | Single seated | Quick opening | AISI 316, hard faced | IV | [26 empty] | H | 3090 |  | HV-3090
S-02115 | HV2-3093 | 243.2 | Trim |  | P24 |  | 2"-CBD-30-103-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | 36.5 | Single seated | Quick opening | AISI 316, hard faced | IV | [26 empty] | H | 3093 |  | HV-3093
S-02115 | HV2-3166 | 243.2 | Trim |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 61 | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | H | 3166 |  | HV-3166
S-02115 | HV2-5338 | 243.2 | Trim |  | P40 |  | 3"-PMV-50-116-B24-P |  |  | 6 | 2.6 | bar g |  | 101 | 165 | °C | Line size | Single seated | Linear | AISI 316 | V | [26 empty] | H | 5338 |  | HV-5338
S-02115 | HV2-6069 | 243.2 | Trim |  | P07 |  | 16"-PRG-60-107-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | Line size | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | H | 6069 |  | HV-6069
S-02115 | LV2-2016 | 243.2 | Trim |  | P02 |  | 6"-HPC-20-102-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | 7 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | L | 2016 |  | LV-2016
S-02115 | LV2-2372 | 243.2 | Trim |  | P19 |  | 6"-BFW-20-106-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 69 | Anti cavitation trim | Equal % | AISI 316, hard faced | IV | [26 empty] | L | 2372 |  | LV-2372
S-02115 | LV2-2403 | 243.2 | Trim |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | 12.2 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | L | 2403 |  | LV-2403
S-02115 | LV2-2419 | 243.2 | Trim |  | P19 |  | 4"-PRC-20-123-F40-H |  |  | 30 | 26 | bar g |  | 159 | 200 | °C | 136 | Single seated | Linear | AISI 316 | IV | [26 empty] | L | 2419 |  | LV-2419
S-02115 | LV2-2441 | 243.2 | Trim |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | 49.7 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | L | 2441 |  | LV-2441
S-02115 | LV2-2474 | 243.2 | Trim |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 39.1 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | L | 2474 |  | LV-2474
S-02115 | LV2-3161/A | 243.2 | Trim |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | 64 | Anti cavitation trim | Linear | AISI 316, hard faced | IV | [26 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV2-3161/B | 243.2 | Trim |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | 64 | Anti cavitation trim | Linear | AISI 316, hard faced | IV | [26 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV2-3192 | 243.2 | Trim |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 311 | Single seated | Linear | AISI 316 | IV | [26 empty] | L | 3192 |  | LV-3192
S-02115 | LV2-5070 | 243.2 | Trim |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | 53 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | L | 5070 |  | LV-5070
S-02115 | LV2-5501 | 243.2 | Trim |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | 21 | Single seated | Equal % | AISI 316 | IV | [26 empty] | L | 5501 |  | LV-5501
S-02115 | LV2-6021/A | 243.2 | Trim |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | 307 | Single seated | Linear | AISI 316 | IV | [26 empty] | L | 6021 | A | LV-6021/A
S-02115 | LV2-6021/B | 243.2 | Trim |  | P05 |  | 18"-MPC-60-104-F24-H |  |  | 47 | 32.5 | bar g |  | 240 | 260 | °C | 216 | By vendor | Linear | AISI 316, hard faced | IV | [26 empty] | L | 6021 | B | LV-6021/B
S-02115 | LV2-6082 | 243.2 | Trim |  | P08 |  | 4"-BD-60-111-B40-N |  |  | 9 | 1.5 | bar g |  | 65 | 125 | °C | 72 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | L | 6082 |  | LV-6082
S-02115 | LV2-7251 | 243.2 | Trim |  | U16 |  | 3"-BD-70-111-B24-N |  |  | 10.5 | 8 | bar g |  | 173 | 200 | °C | 16.5 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | L | 7251 |  | LV-7251
S-02115 | PV2-1006 | 243.2 | Trim |  | P01 |  | 14"-NG-10-102-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 773 | Single seated | Equal % | AISI 316 | IV | [26 empty] | P | 1006 |  | PV-1006
S-02115 | PV2-1011 | 243.2 | Trim |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 43.8 | Low noise trim | Linear | AISI 316 | IV | [26 empty] | P | 1011 |  | PV-1011
S-02115 | PV2-1045 | 243.2 | Trim |  | P04 |  | 8"-PRG-10-108-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 180, no additional oversizing | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 1045 |  | PV-1045
S-02115 | PV2-2015 | 243.2 | Trim |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 154 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | P | 2015 |  | PV-2015
S-02115 | PV2-2073 | 243.2 | Trim |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 455, no additional oversizing | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 2073 |  | PV-2073
S-02115 | PV2-2361 | 243.2 | Trim |  | P17 |  | 8"-HHPS-20-2054-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 144, no additional oversizing | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | P | 2361 |  | PV-2361
S-02115 | PV2-2363 | 243.2 | Trim |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Full size | Single seated | Equal % | AISI 316, hard faced | III | [26 empty] | P | 2363 |  | PV-2363
S-02115 | PV2-2406 | 243.2 | Trim |  | P19 |  | 18"-RFG-20-118-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 1058, no additional oversizing | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 2406 |  | PV-2406
S-02115 | PV2-2481 | 243.2 | Trim |  | P21 |  | 18"-SG-20-105-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 1235, no oversizing | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 2481 |  | PV-2481
S-02115 | PV2-2536 | 243.2 | Trim |  | U01 |  | 14"-PG-20-129-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 780 | Low noise trim | Linear | AISI 316 | V | [26 empty] | P | 2536 |  | PV-2536
S-02115 | PV2-2551 | 243.2 | Trim |  | U01 |  | 2"NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 14 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | P | 2551 |  | PCV-2551
S-02115 | PV2-2575 | 243.2 | Trim |  | U02 |  | 8"-N-20-105-B24-P |  |  | 10.5 | 6 | bar g |  | 70 | 110 | °C | 690 | Single seated | Linear | AISI 316 | IV | [26 empty] | P | 2575 |  | PDV-2575
S-02115 | PV2-2603 | 243.2 | Trim |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 21 | Single seated | Equal % | AISI 316 | IV | [26 empty] | P | 2603 |  | PV-2603
S-02115 | PV2-2608 | 243.2 | Trim |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 5.1 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | P | 2608 |  | PV-2608
S-02115 | PV2-3008 | 243.2 | Trim |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 6 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | P | 3008 |  | PCV-3008
S-02115 | PV2-3042 | 243.2 | Trim |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Full size | Single seated | Equal % | AISI 316, hard faced | III | [26 empty] | P | 3042 |  | PV-3042
S-02115 | PV2-3166 | 243.2 | Trim |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 67, no additional oversizing | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 3166 |  | PV-3166
S-02115 | PV2-3194 | 243.2 | Trim |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 217 | Single seated | Equal % | AISI 316 | IV | [26 empty] | P | 3194 |  | PV-3194
S-02115 | PV2-5009 | 243.2 | Trim |  | P29 |  | 2"-N-50-101-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 39.2 | Low noise trim | Linear | AISI 316 | IV | [26 empty] | P | 5009 |  | PCV-5009
S-02115 | PV2-5069 | 243.2 | Trim |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 545 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | P | 5069 |  | PV-5069
S-02115 | PV2-5091/A | 243.2 | Trim |  | P32 |  | 2"-N-50-104-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 14.4 | Single seated | Linear | AISI 316 | IV | [26 empty] | P | 5091 | A | PV-5091/A
S-02115 | PV2-5091/B | 243.2 | Trim |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 149 | Single seated | Linear | AISI 316 | IV | [26 empty] | P | 5091 | B | PV-5091/B
S-02115 | PV2-5109 | 243.2 | Trim |  | P32 |  | 4"-PG-50-103-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 134 | Single seated | Linear | AISI 316 | V | [26 empty] | P | 5109 |  | PV-5109
S-02115 | PV2-5207/A | 243.2 | Trim |  | P36 |  | 2"-N-50-107-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 14.4 | Single seated | Linear | AISI 316 | IV | [26 empty] | P | 5207 | A | PV-5207/A
S-02115 | PV2-5207/B | 243.2 | Trim |  | P36 |  | 2"-VA-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 42 | Single seated | Linear | AISI 316 | IV | [26 empty] | P | 5207 | B | PV-5207/B
S-02115 | PV2-5395 | 243.2 | Trim |  | P43 |  | 2"-N-50-113-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 17.4 | Low noise trim | Linear | AISI 316 | IV | [26 empty] | P | 5395 |  | PCV-5395
S-02115 | PV2-5412 | 243.2 | Trim |  | P44 |  | 2"-N-50-108-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 17.4 | Low noise trim | Linear | AISI 316 | IV | [26 empty] | P | 5412 |  | PCV-5412
S-02115 | PV2-5445 | 243.2 | Trim |  | P45 |  | 2"-N-50-111-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0.24 | Single seated | Linear | AISI 316 | IV | [26 empty] | P | 5445 |  | PCV-5445
S-02115 | PV2-6025 | 243.2 | Trim |  | P06 |  | 24"-MPS-70-101-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 4290 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | P | 6025 |  | PV-6025
S-02115 | PV2-7002/A | 243.2 | Trim |  | U03 |  | 10"-HHPS-70-115-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 55 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7002 | A | PV-7002/A
S-02115 | PV2-7002/B | 243.2 | Trim |  | U03 |  | 24"-HHPS-70-114-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 532 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7002 | B | PV-7002/B
S-02115 | PV2-7002/C | 243.2 | Trim |  | U03 |  | 24"-HHPS-70-113-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 532 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7002 | C | PV-7002/C
S-02115 | PV2-7004 | 243.2 | Trim |  | U03 |  | 16"-HPS-70-108-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 1120 | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 7004 |  | PV-7004
S-02115 | PV2-7025/A | 243.2 | Trim |  | U04 |  | 18"-HHPS-70-121-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 158 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7025 | A | PV-7025/A
S-02115 | PV2-7025/B | 243.2 | Trim |  | U04 |  | 18"-HHPS-70-120-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 158 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7025 | B | PV-7025/B
S-02115 | PV2-7028 | 243.2 | Trim |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 3530 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | P | 7028 |  | PV-7028
S-02115 | PV2-7031/A | 243.2 | Trim |  | U05 |  | 24"-HPS-70-130-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 907 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7031 | A | PV-7031/A
S-02115 | PV2-7031/B | 243.2 | Trim |  | U05 |  | 24"-HPS-70-131-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 907 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7031 | B | PV-7031/B
S-02115 | PV2-7031/C | 243.2 | Trim |  | U05 |  | 10"-MPS-70-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 167 | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | P | 7031 | C | PV-7031/C
S-02115 | PV2-7031/D | 243.2 | Trim |  | U05 |  | 10"-MPS-70-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 167 | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | P | 7031 | D | PV-7031/D
S-02115 | PV2-7034 | 243.2 | Trim |  | U05 |  | 14"-MPS-70-121-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 860, no additional oversizing | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 7034 |  | PV-7034
S-02115 | PV2-7051/A | 243.2 | Trim |  | U06 |  | 16"-HPS-70-120-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 360 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7051 | A | PV-7051/A
S-02115 | PV2-7051/B | 243.2 | Trim |  | U06 |  | 16"-HPS-70-121-F34-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | 360 | Water injection | Linear | AISI 316, hard faced | III | [26 empty] | P | 7051 | B | PV-7051/B
S-02115 | PV2-7056 | 243.2 | Trim |  | U06 |  | 24"-LPS-70-109-D24-P |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 2650 | Low noise trim | Linear | AISI 316, hard faced | V | [26 empty] | P | 7056 |  | PV-7056
S-02115 | PV2-7094 | 243.2 | Trim |  | U09 |  | 18"-LPS-70-127-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 660 | Low noise trim | Linear | AISI 316, hard faced | IV | [26 empty] | P | 7094 |  | PV-7094
S-02115 | PV2-7101 | 243.2 | Trim |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C |  | Low noise trim | Linear | AISI 316 | IV | [26 empty] | P | 7101 |  | PV-7101
S-02115 | TV2-2220 | 243.2 | Trim |  | P12 |  | 8"-NG-10-106-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Full size (min. 670) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 2220 |  | TV-2220
S-02115 | TV2-2457 | 243.2 | Trim |  | P20 |  | 16"-RFG-20-127-D40-P |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | Full size (min. 3676) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 2457 |  | TV-2457
S-02115 | TV2-3113 | 243.2 | Trim |  | P25 |  | 10"-SG-30-926-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Full size (min. 2472) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 3113 |  | TV-3113
S-02115 | TV2-3116 | 243.2 | Trim |  | P25 |  | 10"-SG-30-931-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Full size (min. 2472) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 3116 |  | TV-3116
S-02115 | TV2-3118 | 243.2 | Trim |  | P25 |  | 10"-SG-30-937-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Full size (min. 2472) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 3118 |  | TV-3118
S-02115 | TV2-5064 | 243.2 | Trim |  | P30 |  | 16"-RFG-50-103-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Full size (min. 4313) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 5064 |  | TV-5064
S-02115 | TV2-5277 | 243.2 | Trim |  | P38 |  | 18"-RFG-50-125-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Full size (min. 4500) | Low dynamic torque | Equal % | Min. same as body | IV | [26 empty] | T | 5277 |  | TV-5277
S-02115 | TV2-7002 | 243.2 | Trim |  | U03 |  | 2"-BFW-70-104-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0.46 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7002 |  | TV-7002
S-02115 | TV2-7003 | 243.2 | Trim |  | U03 |  | 3"-BFW-70-143-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 4.4 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7003 |  | TV-7003
S-02115 | TV2-7004 | 243.2 | Trim |  | U03 |  | 3"-BFW-70-141-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 4.43 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7004 |  | TV-7004
S-02115 | TV2-7025/A | 243.2 | Trim |  | U04 |  | 2"-BFW-70-152-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 7.4 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | T | 7025 | A | TV-7025/A
S-02115 | TV2-7025/B | 243.2 | Trim |  | U04 |  | 2"-BFW-70-154-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 7.4 | Single seated | Equal % | AISI 316, hard faced | IV | [26 empty] | T | 7025 | B | TV-7025/B
S-02115 | TV2-7026 | 243.2 | Trim |  | U04 |  | 2"-BFW-70-112-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0.23 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7026 |  | TV-7026
S-02115 | TV2-7027 | 243.2 | Trim |  | U04 |  | 2"-BFW-70-156-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0.23 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7027 |  | TV-7027
S-02115 | TV2-7032 | 243.2 | Trim |  | U05 |  | 2"-BFW-70-115-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 8.5 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7032 |  | TV-7032
S-02115 | TV2-7033 | 243.2 | Trim |  | U05 |  | 2"-BFW-70-108-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 8.5 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7033 |  | TV-7033
S-02115 | TV2-7052 | 243.2 | Trim |  | U06 |  | 2"-BFW-70-121-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 2.9 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7052 |  | TV-7052
S-02115 | TV2-7053 | 243.2 | Trim |  | U06 |  | 2"-BFW-70-119-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 2.9 | Single seated | Linear | AISI 316, hard faced | IV | [26 empty] | T | 7053 |  | TV-7053
S-02115 | TV2-7071/A | 243.2 | Trim |  | U07 |  | 2"-BFW-70-124-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 0.64 | Desuperheater | Equal % | AISI 316, hard faced | IV | [26 empty] | T | 7071 | A | TV-7071/A
S-02115 | TV2-7071/B | 243.2 | Trim |  | U07 |  | 2"-BFW-70-145-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 0.64 | Desuperheater | Equal % | AISI 316, hard faced | IV | [26 empty] | T | 7071 | B | TV-7071/B
S-02115 | USV2-1001 | 243.2 | Trim |  | P01 |  | 2"-OW-10-103-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Line size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 1001 |  | USV-1001
S-02115 | USV2-2010 | 243.2 | Trim |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | Line size | Triple offset | On/Off | Monel | VI | [26 empty] | U | 2010 |  | USV-2010
S-02115 | USV2-2021 | 243.2 | Trim |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 2021 |  | USV-2021
S-02115 | USV2-2038 | 243.2 | Trim |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Full size | Single seated | On/Off | AISI 316 | V | [26 empty] | U | 2038 |  | USV-2038
S-02115 | USV2-2043 | 243.2 | Trim |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Full size | Single seated | On/Off | Monel | VI | [26 empty] | U | 2043 |  | USV-2043
S-02115 | USV2-2045 | 243.2 | Trim |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Line size | Triple offset | On/Off | Monel | VI | [26 empty] | U | 2045 |  | USV-2045
S-02115 | USV2-2048 | 243.2 | Trim |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Line size | Triple offset | On/Off | Monel | VI | [26 empty] | U | 2048 |  | USV-2048
S-02115 | USV2-2049 | 243.2 | Trim |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Line size | Single seated | On/Off | Monel | VI | [26 empty] | U | 2049 |  | USV-2049
S-02115 | USV2-2092 | 243.2 | Trim |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 2092 |  | USV-2092
S-02115 | USV2-2093 | 243.2 | Trim |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 2093 |  | USV-2093
S-02115 | USV2-2094 | 243.2 | Trim |  | P10 |  | 2"-PRG-20-109-F24-H |  |  | 55 | 41.1 | bar g |  | 262 | 290 | °C | Full size | Single seated | On/Off | AISI 316 | V | [26 empty] | U | 2094 |  | USV-2094
S-02115 | UV2-2125 | 243.2 | Trim |  | P11 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | Line size | Offset disc | On/Off | Min. same as body | V | [26 empty] | U | 2125 |  | UV-2125
S-02115 | UV2-2233 | 243.2 | Trim |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | Line size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 2233 |  | UV-2233
S-02115 | USV2-2381 | 243.2 | Trim |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Line size | Full bore | On/Off | AISI 316 | IV | [26 empty] | U | 2381 |  | USV-2381
S-02115 | USV2-2482 | 243.2 | Trim |  | P21 |  | 12"-SG-20-106-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Full size | Triple offset | On/Off | AISI 316 | V | [26 empty] | U | 2482 |  | USV-2482
S-02115 | USV2-2541 | 243.2 | Trim |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Line size | Triple offset | On/Off | AISI 316 | V | [26 empty] | U | 2541 |  | USV-2541
S-02115 | USV2-2542 | 243.2 | Trim |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Line size | Triple offset | On/Off | AISI 316 | V | [26 empty] | U | 2542 |  | USV-2542
S-02115 | USV2-2543 | 243.2 | Trim |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Line size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 2543 |  | USV-2543
S-02115 | USV2-2544 | 243.2 | Trim |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | Line size | Triple offset | On/Off | AISI 316 | V | [26 empty] | U | 2544 |  | USV-2544
S-02115 | USV2-2545 | 243.2 | Trim |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | Line size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 2545 |  | USV-2545
S-02115 | USV2-2547 | 243.2 | Trim |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Full size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 2547 |  | USV-2547
S-02115 | USV2-2548 | 243.2 | Trim |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Full size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 2548 |  | USV-2548
S-02115 | USV2-2549 | 243.2 | Trim |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Full size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 2549 |  | USV-2549
S-02115 | USV2-3018 | 243.2 | Trim |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C | Line size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 3018 |  | USV-3018
S-02115 | USV2-3052 | 243.2 | Trim |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Line size | Full bore | On/Off | AISI 316 | IV | [26 empty] | U | 3052 |  | USV-3052
S-02115 | USV2-3172 | 243.2 | Trim |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 3172 |  | USV-3172
S-02115 | UV2-5021 | 243.2 | Trim |  | P29 |  | 24"-VA-50-140-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 5021 |  | UV-5021
S-02115 | USV2-5302 | 243.2 | Trim |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Full size | Triple offset | On/Off | AISI 316, hard faced | IV | [26 empty] | U | 5302 |  | USV-5302
S-02115 | USV2-5391 | 243.2 | Trim |  | P43 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 5391 |  | USV-5391
S-02115 | USV2-5392 | 243.2 | Trim |  | P43 |  | 10"-PMP-50-144-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 5392 |  | USV-5392
S-02115 | USV2-5393 | 243.2 | Trim |  | P43 |  | 3"-PMP-50-158-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | Line size | Full bore | On/Off | AISI 316 | IV | [26 empty] | U | 5393 |  | USV-5393
S-02115 | USV2-5420 | 243.2 | Trim |  | P44 |  | 10"-PMP-50-152-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 5420 |  | USV-5420
S-02115 | USV2-5421 | 243.2 | Trim |  | P44 |  | 3"-PMP-50-156-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | Line size | Full bore | On/Off | AISI 316 | IV | [26 empty] | U | 5421 |  | USV-5421
S-02115 | USV2-5422 | 243.2 | Trim |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 5422 |  | USV-5422
S-02115 | UV2-6035 | 243.2 | Trim |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Line size | Triple offset | On/Off | Min. same as body | V | [26 empty] | U | 6035 |  | UV-6035
S-02115 | USV2-6081 | 243.2 | Trim |  | P08 |  | 2"-BD-60-109-G40-P |  |  | 57 | 1 | bar g |  | 73 | 260 | °C | Full size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 6081 |  | USV-6081
S-02115 | USV2-6082 | 243.2 | Trim |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | Full size | Full bore | On/Off | AISI 316 | V | [26 empty] | U | 6082 |  | USV-6082
S-02115 | FV3-2007 | 243.3 | Actuator |  | P02 |  | 10"-PO-20-106-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | Diaphragm with spring return | Modulating | FC | 47 bar | No | [26 empty] | F | 2007 |  | FV-2007
S-02115 | FV3-2009 | 243.3 | Actuator |  | P02 |  | 4"-PO-20-105-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | Diaphragm with spring return | Modulating | FC | 47 bar | No | [26 empty] | F | 2009 |  | FV-2009
S-02115 | FV3-2040 | 243.3 | Actuator |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FO | 52 bar | Yes | [26 empty] | F | 2040 |  | FV-2040
S-02115 | FV3-2061 | 243.3 | Actuator |  | P10 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Diaphragm with spring return | Modulating | FC | 55 bar | No | [26 empty] | F | 2061 |  | FV-2061
S-02115 | FV3-2072 | 243.3 | Actuator |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FO | 52 bar | No | [26 empty] | F | 2072 |  | FV-2072
S-02115 | FV3-2079 | 243.3 | Actuator |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Diaphragm with spring return | Modulating | FO | 60 bar | Yes | [26 empty] | F | 2079 |  | FV-2079
S-02115 | FV3-2091 | 243.3 | Actuator |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Diaphragm with spring return | Modulating | FC | 55 bar | No | [26 empty] | F | 2091 |  | FV-2091
S-02115 | FV3-2150 | 243.3 | Actuator |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Diaphragm with spring return | Modulating | FC | 60 bar | No | [26 empty] | F | 2150 |  | FV-2150
S-02115 | FV3-2233/1 | 243.3 | Actuator |  | P13 |  | 3"-PRC-20-130-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | F | 2233 | 1 | FV-2233/1
S-02115 | FV3-2233/2 | 243.3 | Actuator |  | P13 |  | 3"-BFW-70-103-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | F | 2233 | 2 | FV-2233/2
S-02115 | FV3-2417 | 243.3 | Actuator |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLC | 170 bar | No | [26 empty] | F | 2417 |  | FV-2417
S-02115 | FV3-2531/1 | 243.3 | Actuator |  | U01 |  | 10"-NG-20-104-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Diaphragm with spring return | Modulating | FC | 7 bar | No | [26 empty] | F | 2531 | 1 | FV-2531/1
S-02115 | FV3-2531/2 | 243.3 | Actuator |  | U01 |  | 24"-NG-20-112-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Diaphragm with spring return | Modulating | FC | 7 bar | No | [26 empty] | F | 2531 | 2 | FV-2531/2
S-02115 | FV3-2536 | 243.3 | Actuator |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Diaphragm with spring return | Modulating | FC | 7 bar | No | [26 empty] | F | 2536 |  | FV-2536
S-02115 | FV3-3041 | 243.3 | Actuator |  | P23 |  | 8"-BFW-70-101-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Diaphragm with spring return | Modulating | FLC | 80 bar | No | [26 empty] | F | 3041 |  | FV-3041
S-02115 | FV3-3169 | 243.3 | Actuator |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 99 bar | No | [26 empty] | F | 3169 |  | FV-3169
S-02115 | FV3-3171 | 243.3 | Actuator |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 99 bar | No | [26 empty] | F | 3171 |  | FV-3171
S-02115 | FV3-5020 | 243.3 | Actuator |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 7.5 bar | No | [26 empty] | F | 5020 |  | FV-5020
S-02115 | FV3-5041 | 243.3 | Actuator |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | Diaphragm with spring return | Modulating | FC | 13 bar | No | [26 empty] | F | 5041 |  | FV-5041
S-02115 | FV3-5093 | 243.3 | Actuator |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | Diaphragm with spring return | Modulating | FC | 13 bar | No | [26 empty] | F | 5093 |  | FV-5093
S-02115 | FV3-5107 | 243.3 | Actuator |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | Diaphragm with spring return | Modulating | FC | 13 bar | No | [26 empty] | F | 5107 |  | FV-5107
S-02115 | FV3-5161 | 243.3 | Actuator |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | Diaphragm with spring return | Modulating | FC | 10 bar | No | [26 empty] | F | 5161 |  | FV-5161
S-02115 | FV3-5203 | 243.3 | Actuator |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | Diaphragm with spring return | Modulating | FC | 13 bar | No | [26 empty] | F | 5203 |  | FV-5203
S-02115 | FV3-5239 | 243.3 | Actuator |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | Diaphragm with spring return | Modulating | FC | 16 bar | No | [26 empty] | F | 5239 |  | FV-5239
S-02115 | FV3-5301 | 243.3 | Actuator |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | Diaphragm with spring return | Modulating | FC | 10.5 bar | No | [26 empty] | F | 5301 |  | FV-5301
S-02115 | FV3-5321 | 243.3 | Actuator |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | Diaphragm with spring return | Modulating | FC | 19 bar | No | [26 empty] | F | 5321 |  | FV-5321
S-02115 | FV3-5336 | 243.3 | Actuator |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | Diaphragm with spring return | Modulating | FC | 19 bar | No | [26 empty] | F | 5336 |  | FV-5336
S-02115 | FV3-5337 | 243.3 | Actuator |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | Diaphragm with spring return | Modulating | FC | 19 bar | No | [26 empty] | F | 5337 |  | FV-5337
S-02115 | FV3-5367 | 243.3 | Actuator |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | Diaphragm with spring return | Modulating | FC | 82 bar | No | [26 empty] | F | 5367 |  | FV-5367
S-02115 | FV3-5383 | 243.3 | Actuator |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | Diaphragm with spring return | Modulating | FC | 7 bar | Yes | [26 empty] | F | 5383 |  | FV-5383
S-02115 | FV3-5441 | 243.3 | Actuator |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | Diaphragm with spring return | Modulating | FC | 7.5 bar | No | [26 empty] | F | 5441 |  | FV-5441
S-02115 | FV3-5501 | 243.3 | Actuator |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | Diaphragm with spring return | Modulating | FC | 7.5 bar | No | [26 empty] | F | 5501 |  | FV-5501
S-02115 | FV3-6031 | 243.3 | Actuator |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | F | 6031 |  | FV-6031
S-02115 | FV3-6070 | 243.3 | Actuator |  | P07 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Diaphragm with spring return | Modulating | FC | 55 bar | No | [26 empty] | F | 6070 |  | FV-6070
S-02115 | FV3-6081 | 243.3 | Actuator |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | Diaphragm with spring return | Modulating | FC | 57 bar | No | [26 empty] | F | 6081 |  | FV-6081
S-02115 | FV3-6082 | 243.3 | Actuator |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | Diaphragm with spring return | Modulating | FC | 9 bar | No | [26 empty] | F | 6082 |  | FV-6082
S-02115 | FV3-6086 | 243.3 | Actuator |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | Diaphragm with spring return | Modulating | FC | 57 bar | No | [26 empty] | F | 6086 |  | FV-6086
S-02115 | FV3-7091 | 243.3 | Actuator |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | Diaphragm with spring return | Modulating | FLC | 14 bar | No | [26 empty] | F | 7091 |  | FV-7091
S-02115 | FV3-7141 | 243.3 | Actuator |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FC | 170 bar | No | [26 empty] | F | 7141 |  | FV-7141
S-02115 | HV3-1003 | 243.3 | Actuator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Electric motor | On/Off | FL | 60 bar | No | [26 empty] | H | 1003 |  | HV-1003
S-02115 | HV3-2003 | 243.3 | Actuator |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | Electric motor | On/Off | FL | 47 bar | No | [26 empty] | H | 2003 |  | HV-2003
S-02115 | HV3-2031 | 243.3 | Actuator |  | P03 |  | 2"-HPS-20-110-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FC | 52 bar | No | [26 empty] | H | 2031 |  | HV-2031
S-02115 | HV3-2076 | 243.3 | Actuator |  | P09 |  | 8"-HPS-20-114-F24-H |  |  | 52 | 44 | bar g |  | 343 | 410 | °C | Diaphragm with spring return | Modulating | FC | 52 bar | Yes | [26 empty] | H | 2076 |  | HV-2076
S-02115 | HV3-2097 | 243.3 | Actuator |  | P10 |  | 3"-HPS-20-112-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Diaphragm with spring return | Modulating | FC | 52 | No | [26 empty] | H | 2097 |  | HV-2097
S-02115 | HV3-2098 | 243.3 | Actuator |  | P10 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Electric motor | On/Off | FL | 52 bar | Yes | [26 empty] | H | 2098 |  | HV-2098
S-02115 | HV3-2334 | 243.3 | Actuator |  | P16B |  | 2"-BD-20-101-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Lever operated, spring return |  |  |  | Yes | [26 empty] | H | 2334 |  | HV-2334
S-02115 | HV3-2335 | 243.3 | Actuator |  | P16B |  | 2"-BD-20-139-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Lever operated, spring return |  |  |  | Yes | [26 empty] | H | 2335 |  | HV-2335
S-02115 | HV3-2371 | 243.3 | Actuator |  | P18 |  | 6"-BFW-20-109-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | Diaphragm with spring return | Modulating | FC | 113 | No | [26 empty] | H | 2371 |  | HV-2371
S-02115 | HV3-2385 | 243.3 | Actuator |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Hand operated calibrated scale |  |  |  | Yes | [26 empty] | H | 2385 |  | HV-2385
S-02115 | HV3-2545 | 243.3 | Actuator |  | U01 |  | 2"-N-20-116-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Hand operated |  |  |  | Yes | [26 empty] | H | 2545 |  | HV-2545
S-02115 | HV3-3010 | 243.3 | Actuator |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 10 | bar g |  | 48 | 100 | °C | Hand operated | Modulating | [29 empty] | H | 3010 |  | HV-3010
S-02115 | HV3-3011 | 243.3 | Actuator |  | P22 |  | 2"-SG-30-131-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 29 bar | Yes | [26 empty] | H | 3011 |  | HV-3011
S-02115 | HV3-3013 | 243.3 | Actuator |  | P22 |  | 3"-HG-30-101-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | Hand operated | Modulating | [29 empty] | H | 3013 |  | HV-3013
S-02115 | HV3-3016 | 243.3 | Actuator |  | P22 |  | 3"-PA-30-101-B24-N |  |  | 10.5 | 7.5 | bar g |  | 35 | 75 | °C | Hand operated | Modulating | [29 empty] | H | 3016 |  | HV-3016
S-02115 | HV3-3054 | 243.3 | Actuator |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Hand operated calibrated scale |  |  |  | Yes | [26 empty] | H | 3054 |  | HV-3054
S-02115 | HV3-3087 | 243.3 | Actuator |  | P24 |  | 2"-CBD-30-107-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Lever operated, spring return | On/Off |  |  | Yes | [26 empty] | H | 3087 |  | HV-3087
S-02115 | HV3-3090 | 243.3 | Actuator |  | P24 |  | 2"-CBD-30-105-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Lever operated, spring return | On/Off |  |  | Yes | [26 empty] | H | 3090 |  | HV-3090
S-02115 | HV3-3093 | 243.3 | Actuator |  | P24 |  | 2"-CBD-30-103-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Lever operated, spring return | On/Off |  |  | Yes | [26 empty] | H | 3093 |  | HV-3093
S-02115 | HV3-3166 | 243.3 | Actuator |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Hand operated | Modulating |  |  | Yes | [26 empty] | H | 3166 |  | HV-3166
S-02115 | HV3-5338 | 243.3 | Actuator |  | P40 |  | 3"-PMV-50-116-B24-P |  |  | 6 | 2.6 | bar g |  | 101 | 165 | °C | Diaphragm with spring return | Modulating | FC | 6 bar | [27 empty] | H | 5338 |  | HV-5338
S-02115 | HV3-6069 | 243.3 | Actuator |  | P07 |  | 16"-PRG-60-107-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | Piston with spring return | Modulating | FC | 5 bar | No | [26 empty] | H | 6069 |  | HV-6069
S-02115 | LV3-2016 | 243.3 | Actuator |  | P02 |  | 6"-HPC-20-102-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | Diaphragm with spring return | Modulating | FC | 53 bar | No | [26 empty] | L | 2016 |  | LV-2016
S-02115 | LV3-2372 | 243.3 | Actuator |  | P19 |  | 6"-BFW-20-106-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLC | 170 bar | No | [26 empty] | L | 2372 |  | LV-2372
S-02115 | LV3-2403 | 243.3 | Actuator |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | Diaphragm with spring return | Modulating | FC | 71 bar | No | [26 empty] | L | 2403 |  | LV-2403
S-02115 | LV3-2419 | 243.3 | Actuator |  | P19 |  | 4"-PRC-20-123-F40-H |  |  | 30 | 26 | bar g |  | 159 | 200 | °C | Diaphragm with spring return | Modulating | FC | 30 bar | No | [26 empty] | L | 2419 |  | LV-2419
S-02115 | LV3-2441 | 243.3 | Actuator |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | Diaphragm with spring return | Modulating | FC | 71 bar | No | [26 empty] | L | 2441 |  | LV-2441
S-02115 | LV3-2474 | 243.3 | Actuator |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | L | 2474 |  | LV-2474
S-02115 | LV3-3161/A | 243.3 | Actuator |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 100 bar | No | [26 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV3-3161/B | 243.3 | Actuator |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 100 bar | No | [26 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV3-3192 | 243.3 | Actuator |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 8 bar | No | [26 empty] | L | 3192 |  | LV-3192
S-02115 | LV3-5070 | 243.3 | Actuator |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | Diaphragm with spring return | Modulating | FC | 18 bar | No | [26 empty] | L | 5070 |  | LV-5070
S-02115 | LV3-5501 | 243.3 | Actuator |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | Diaphragm with spring return | Modulating | FC | 82 bar | No | [26 empty] | L | 5501 |  | LV-5501
S-02115 | LV3-6021/A | 243.3 | Actuator |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | Diaphragm with spring return | Modulating | FC | 73 bar | Yes | [26 empty] | L | 6021 | A | LV-6021/A
S-02115 | LV3-6021/B | 243.3 | Actuator |  | P05 |  | 18"-MPC-60-104-F24-H |  |  | 47 | 32.5 | bar g |  | 240 | 260 | °C | Diaphragm with spring return | Modulating | FC | 47 bar | Yes | [26 empty] | L | 6021 | B | LV-6021/B
S-02115 | LV3-6082 | 243.3 | Actuator |  | P08 |  | 4"-BD-60-111-B40-N |  |  | 9 | 1.5 | bar g |  | 65 | 125 | °C | Diaphragm with spring return | Modulating | FC | bar | No | [26 empty] | L | 6082 |  | LV-6082
S-02115 | LV3-7251 | 243.3 | Actuator |  | U16 |  | 3"-BD-70-111-B24-N |  |  | 10.5 | 8 | bar g |  | 173 | 200 | °C | Diaphragm with spring return | Modulating | FC | 10.5 bar | No | [26 empty] | L | 7251 |  | LV-7251
S-02115 | PV3-1006 | 243.3 | Actuator |  | P01 |  | 14"-NG-10-102-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Diaphragm with spring return | Modulating | FLC | 60 bar | No | [26 empty] | P | 1006 |  | PV-1006
S-02115 | PV3-1011 | 243.3 | Actuator |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Diaphragm with spring return | Modulating | FC | 55 bar | No | [26 empty] | P | 1011 |  | PV-1011
S-02115 | PV3-1045 | 243.3 | Actuator |  | P04 |  | 8"-PRG-10-108-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Diaphragm with spring return | Modulating | FC | 55 bar | [27 empty] | P | 1045 |  | PV-1045
S-02115 | PV3-2015 | 243.3 | Actuator |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Diaphragm with spring return | Modulating | FC | 52 bar | No | [26 empty] | P | 2015 |  | PV-2015
S-02115 | PV3-2073 | 243.3 | Actuator |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Diaphragm with spring return | Modulating | FC | 55 bar | No | [26 empty] | P | 2073 |  | PV-2073
S-02115 | PV3-2361 | 243.3 | Actuator |  | P17 |  | 8"-HHPS-20-2054-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Diaphragm with spring return | Modulating | FLC | 112 bar | Yes | [26 empty] | P | 2361 |  | PV-2361
S-02115 | PV3-2363 | 243.3 | Actuator |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Diaphragm with spring return | Modulating | FLO | 112 bar | No | [26 empty] | P | 2363 |  | PV-2363
S-02115 | PV3-2406 | 243.3 | Actuator |  | P19 |  | 18"-RFG-20-118-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Diaphragm with spring return | Modulating | FC | 29 bar | Yes | [26 empty] | P | 2406 |  | PV-2406
S-02115 | PV3-2481 | 243.3 | Actuator |  | P21 |  | 18"-SG-20-105-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 29 bar | Yes | [26 empty] | P | 2481 |  | PV-2481
S-02115 | PV3-2536 | 243.3 | Actuator |  | U01 |  | 14"-PG-20-129-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Diaphragm with spring return | Modulating | FC | 7 bar | No | [26 empty] | P | 2536 |  | PV-2536
S-02115 | PV3-2551 | 243.3 | Actuator |  | U01 |  | 2"NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Self actuating | Modulating |  | 7 bar | [27 empty] | P | 2551 |  | PCV-2551
S-02115 | PV3-2575 | 243.3 | Actuator |  | U02 |  | 8"-N-20-105-B24-P |  |  | 10.5 | 6 | bar g |  | 70 | 110 | °C | Diaphragm with spring return | Modulating | FC | 10.5 bar | Yes | [26 empty] | P | 2575 |  | PDV-2575
S-02115 | PV3-2603 | 243.3 | Actuator |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | Diaphragm with spring return | Modulating | FC | 28 bar | No | [26 empty] | P | 2603 |  | PV-2603
S-02115 | PV3-2608 | 243.3 | Actuator |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 99 bar | Yes | [26 empty] | P | 2608 |  | PV-2608
S-02115 | PV3-3008 | 243.3 | Actuator |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Self actuating- reducer | Modulating |  | 29 bar | [27 empty] | P | 3008 |  | PCV-3008
S-02115 | PV3-3042 | 243.3 | Actuator |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Diaphragm with spring return | Modulating | FLC | 45 bar | Yes | [26 empty] | P | 3042 |  | PV-3042
S-02115 | PV3-3166 | 243.3 | Actuator |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FO | 99 bar | No | [26 empty] | P | 3166 |  | PV-3166
S-02115 | PV3-3194 | 243.3 | Actuator |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Diaphragm with spring return | Modulating | FC | 7 bar | No | [26 empty] | P | 3194 |  | PV-3194
S-02115 | PV3-5009 | 243.3 | Actuator |  | P29 |  | 2"-N-50-101-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Self actuating- reducer | Modulating |  | 10.5 bar | [27 empty] | P | 5009 |  | PCV-5009
S-02115 | PV3-5069 | 243.3 | Actuator |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Diaphragm with spring return | Modulating | FC | 9.5 bar | No | [26 empty] | P | 5069 |  | PV-5069
S-02115 | PV3-5091/A | 243.3 | Actuator |  | P32 |  | 2"-N-50-104-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Diaphragm with spring return | Modulating | FC | 10.5 bar | No | [26 empty] | P | 5091 | A | PV-5091/A
S-02115 | PV3-5091/B | 243.3 | Actuator |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | Diaphragm with spring return | Modulating | FC | 3.5 bar | No | [26 empty] | P | 5091 | B | PV-5091/B
S-02115 | PV3-5109 | 243.3 | Actuator |  | P32 |  | 4"-PG-50-103-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | Diaphragm with spring return | Modulating | FC | 3.5 bar | No | [26 empty] | P | 5109 |  | PV-5109
S-02115 | PV3-5207/A | 243.3 | Actuator |  | P36 |  | 2"-N-50-107-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Diaphragm with spring return | Modulating | FO | 10.5 bar | Yes | [26 empty] | P | 5207 | A | PV-5207/A
S-02115 | PV3-5207/B | 243.3 | Actuator |  | P36 |  | 2"-VA-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Diaphragm with spring return | Modulating | FC | 3.5 bar | Yes | [26 empty] | P | 5207 | B | PV-5207/B
S-02115 | PV3-5395 | 243.3 | Actuator |  | P43 |  | 2"-N-50-113-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Self actuating- reducer | Modulating |  | 10.5 bar | [27 empty] | P | 5395 |  | PCV-5395
S-02115 | PV3-5412 | 243.3 | Actuator |  | P44 |  | 2"-N-50-108-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Self actuating- reducer | Modulating |  | 10.5 bar | [27 empty] | P | 5412 |  | PCV-5412
S-02115 | PV3-5445 | 243.3 | Actuator |  | P45 |  | 2"-N-50-111-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Self actuating- reductor | Modulating |  | 10.5 bar | [27 empty] | P | 5445 |  | PCV-5445
S-02115 | PV3-6025 | 243.3 | Actuator |  | P06 |  | 24"-MPS-70-101-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Diaphragm with spring return | Modulating | FC | 45 bar | No | [26 empty] | P | 6025 |  | PV-6025
S-02115 | PV3-7002/A | 243.3 | Actuator |  | U03 |  | 10"-HHPS-70-115-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Diaphragm with spring return | Modulating | FLO | 112 bar | No | [26 empty] | P | 7002 | A | PV-7002/A
S-02115 | PV3-7002/B | 243.3 | Actuator |  | U03 |  | 24"-HHPS-70-114-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Diaphragm with spring return | Modulating | FLO | 112 bar | No | 1 sec | [25 empty] | P | 7002 | B | PV-7002/B
S-02115 | PV3-7002/C | 243.3 | Actuator |  | U03 |  | 24"-HHPS-70-113-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Diaphragm with spring return | Modulating | FLO | 112 bar | No | 1 sec | [25 empty] | P | 7002 | C | PV-7002/C
S-02115 | PV3-7004 | 243.3 | Actuator |  | U03 |  | 16"-HPS-70-108-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FC | 52 bar | No | [26 empty] | P | 7004 |  | PV-7004
S-02115 | PV3-7025/A | 243.3 | Actuator |  | U04 |  | 18"-HHPS-70-121-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Diaphragm with spring return | Modulating | FLO | 112 bar | No | [26 empty] | P | 7025 | A | PV-7025/A
S-02115 | PV3-7025/B | 243.3 | Actuator |  | U04 |  | 18"-HHPS-70-120-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | Diaphragm with spring return | Modulating | FLO | 112 bar | No | [26 empty] | P | 7025 | B | PV-7025/B
S-02115 | PV3-7028 | 243.3 | Actuator |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | Diaphragm with spring return | Modulating | FC | 52 bar | No | [26 empty] | P | 7028 |  | PV-7028
S-02115 | PV3-7031/A | 243.3 | Actuator |  | U05 |  | 24"-HPS-70-130-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FLO | 52 bar | No | [26 empty] | P | 7031 | A | PV-7031/A
S-02115 | PV3-7031/B | 243.3 | Actuator |  | U05 |  | 24"-HPS-70-131-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FLO | 52 bar | No | [26 empty] | P | 7031 | B | PV-7031/B
S-02115 | PV3-7031/C | 243.3 | Actuator |  | U05 |  | 10"-MPS-70-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Diaphragm with spring return | Modulating | FC | 45 bar | No | [26 empty] | P | 7031 | C | PV-7031/C
S-02115 | PV3-7031/D | 243.3 | Actuator |  | U05 |  | 10"-MPS-70-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Diaphragm with spring return | Modulating | FC | 45 bar | No | [26 empty] | P | 7031 | D | PV-7031/D
S-02115 | PV3-7034 | 243.3 | Actuator |  | U05 |  | 14"-MPS-70-121-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Diaphragm with spring return | Modulating | FC | 45 bar | No | [26 empty] | P | 7034 |  | PV-7034
S-02115 | PV3-7051/A | 243.3 | Actuator |  | U06 |  | 16"-HPS-70-120-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | Modulating | FLO | 52 bar | No | [26 empty] | P | 7051 | A | PV-7051/A
S-02115 | PV3-7051/B | 243.3 | Actuator |  | U06 |  | 16"-HPS-70-121-F34-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Diaphragm with spring return | Modulating | FLO | 52 bar | No | [26 empty] | P | 7051 | B | PV-7051/B
S-02115 | PV3-7056 | 243.3 | Actuator |  | U06 |  | 24"-LPS-70-109-D24-P |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Diaphragm with spring return | Modulating | FC | 9.5 bar | No | [26 empty] | P | 7056 |  | PV-7056
S-02115 | PV3-7094 | 243.3 | Actuator |  | U09 |  | 18"-LPS-70-127-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Diaphragm with spring return | Modulating | FC | 9.5 bar | No | [26 empty] | P | 7094 |  | PV-7094
S-02115 | PV3-7101 | 243.3 | Actuator |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | Diaphragm with spring return | Modulating | FC | 3.5 bar | No | [26 empty] | P | 7101 |  | PV-7101
S-02115 | TV3-2220 | 243.3 | Actuator |  | P12 |  | 8"-NG-10-106-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Piston with spring return | Modulating | FLO | 5 bar | Yes | [26 empty] | T | 2220 |  | TV-2220
S-02115 | TV3-2457 | 243.3 | Actuator |  | P20 |  | 16"-RFG-20-127-D40-P |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | Piston with spring return | Modulating | FC | 5 bar | Yes | [26 empty] | T | 2457 |  | TV-2457
S-02115 | TV3-3113 | 243.3 | Actuator |  | P25 |  | 10"-SG-30-926-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Piston with spring return | Modulating | FLO | 5 bar | Yes | [26 empty] | T | 3113 |  | TV-3113
S-02115 | TV3-3116 | 243.3 | Actuator |  | P25 |  | 10"-SG-30-931-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Piston with spring return | Modulating | FLO | 5 bar | Yes | [26 empty] | T | 3116 |  | TV-3116
S-02115 | TV3-3118 | 243.3 | Actuator |  | P25 |  | 10"-SG-30-937-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | Piston with spring return | Modulating | FLO | 5 bar | Yes | [26 empty] | T | 3118 |  | TV-3118
S-02115 | TV3-5064 | 243.3 | Actuator |  | P30 |  | 16"-RFG-50-103-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Piston with spring return | Modulating | FC | 5 bar | Yes | [26 empty] | T | 5064 |  | TV-5064
S-02115 | TV3-5277 | 243.3 | Actuator |  | P38 |  | 18"-RFG-50-125-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Piston with spring return | Modulating | FC | 5 bar | Yes | [26 empty] | T | 5277 |  | TV-5277
S-02115 | TV3-7002 | 243.3 | Actuator |  | U03 |  | 2"-BFW-70-104-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 170 bar | No | [26 empty] | T | 7002 |  | TV-7002
S-02115 | TV3-7003 | 243.3 | Actuator |  | U03 |  | 3"-BFW-70-143-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 170 bar | No | [26 empty] | T | 7003 |  | TV-7003
S-02115 | TV3-7004 | 243.3 | Actuator |  | U03 |  | 3"-BFW-70-141-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 170 bar | No | [26 empty] | T | 7004 |  | TV-7004
S-02115 | TV3-7025/A | 243.3 | Actuator |  | U04 |  | 2"-BFW-70-152-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | T | 7025 | A | TV-7025/A
S-02115 | TV3-7025/B | 243.3 | Actuator |  | U04 |  | 2"-BFW-70-154-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | T | 7025 | B | TV-7025/B
S-02115 | TV3-7026 | 243.3 | Actuator |  | U04 |  | 2"-BFW-70-112-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 170 bar | No | [26 empty] | T | 7026 |  | TV-7026
S-02115 | TV3-7027 | 243.3 | Actuator |  | U04 |  | 2"-BFW-70-156-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 170 bar | No | [26 empty] | T | 7027 |  | TV-7027
S-02115 | TV3-7032 | 243.3 | Actuator |  | U05 |  | 2"-BFW-70-115-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 80 bar | No | [26 empty] | T | 7032 |  | TV-7032
S-02115 | TV3-7033 | 243.3 | Actuator |  | U05 |  | 2"-BFW-70-108-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 80 bar | No | [26 empty] | T | 7033 |  | TV-7033
S-02115 | TV3-7052 | 243.3 | Actuator |  | U06 |  | 2"-BFW-70-121-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 80 bar | No | [26 empty] | T | 7052 |  | TV-7052
S-02115 | TV3-7053 | 243.3 | Actuator |  | U06 |  | 2"-BFW-70-119-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FLO | 80 bar | No | [26 empty] | T | 7053 |  | TV-7053
S-02115 | TV3-7071/A | 243.3 | Actuator |  | U07 |  | 2"-BFW-70-124-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | T | 7071 | A | TV-7071/A
S-02115 | TV3-7071/B | 243.3 | Actuator |  | U07 |  | 2"-BFW-70-145-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Diaphragm with spring return | Modulating | FC | 80 bar | No | [26 empty] | T | 7071 | B | TV-7071/B
S-02115 | USV3-1001 | 243.3 | Actuator |  | P01 |  | 2"-OW-10-103-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Piston with spring return | On/Off | FC | 60 bar | No | [26 empty] | U | 1001 |  | USV-1001
S-02115 | USV3-2010 | 243.3 | Actuator |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | Piston with spring return | On/Off | FC | 47 bar | No | 2 sec | [25 empty] | U | 2010 |  | USV-2010
S-02115 | USV3-2021 | 243.3 | Actuator |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | Piston with spring return | On/Off | FC | 52 bar | No | [26 empty] | U | 2021 |  | USV-2021
S-02115 | USV3-2038 | 243.3 | Actuator |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Diaphragm with spring return | On/Off | FC | 52 bar | No | [26 empty] | U | 2038 |  | USV-2038
S-02115 | USV3-2043 | 243.3 | Actuator |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Diaphragm with spring return | On/Off | FO | 47 bar | No | 2 sec | [25 empty] | U | 2043 |  | USV-2043
S-02115 | USV3-2045 | 243.3 | Actuator |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Piston with spring return | On/Off | FC | 47 bar | No | 2 sec | [25 empty] | U | 2045 |  | USV-2045
S-02115 | USV3-2048 | 243.3 | Actuator |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Piston with spring return | On/Off | FC | 47 bar | No | 2 sec | [25 empty] | U | 2048 |  | USV-2048
S-02115 | USV3-2049 | 243.3 | Actuator |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | Diaphragm with spring return | On/Off | FO | 47 bar | No | 2 sec | [25 empty] | U | 2049 |  | USV-2049
S-02115 | USV3-2092 | 243.3 | Actuator |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | Piston with spring return | On/Off | FC | 55 bar | No | 10 sec | [25 empty] | U | 2092 |  | USV-2092
S-02115 | USV3-2093 | 243.3 | Actuator |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | Piston with spring return | On/Off | FC | 55 bar | No | 10 sec | [25 empty] | U | 2093 |  | USV-2093
S-02115 | USV3-2094 | 243.3 | Actuator |  | P10 |  | 2"-PRG-20-109-F24-H |  |  | 55 | 41.1 | bar g |  | 262 | 290 | °C | Diaphragm with spring return | On/Off | FO | 55 bar | No | 10 sec | [25 empty] | U | 2094 |  | USV-2094
S-02115 | UV3-2125 | 243.3 | Actuator |  | P11 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | Piston with spring return | On/Off | FC | 3.5 bar | No | [26 empty] | U | 2125 |  | UV-2125
S-02115 | UV3-2233 | 243.3 | Actuator |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | Piston with spring return | On/Off | FC | 80 bar | No | sec | [25 empty] | U | 2233 |  | UV-2233
S-02115 | USV3-2381 | 243.3 | Actuator |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Piston with spring return | On/Off | FC | 112 bar | No | [26 empty] | U | 2381 |  | USV-2381
S-02115 | USV3-2482 | 243.3 | Actuator |  | P21 |  | 12"-SG-20-106-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Piston with spring return | On/Off | FO | 29 bar | No | 10 | [25 empty] | U | 2482 |  | USV-2482
S-02115 | USV3-2541 | 243.3 | Actuator |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Diaphragm with spring return | On/Off | FC | 7 bar | No | 10 sec | [25 empty] | U | 2541 |  | USV-2541
S-02115 | USV3-2542 | 243.3 | Actuator |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Diaphragm with spring return | On/Off | FC | 7 bar | No | 10 sec | [25 empty] | U | 2542 |  | USV-2542
S-02115 | USV3-2543 | 243.3 | Actuator |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | Piston with spring return | On/Off | FO | 7 bar | No | 10 | [25 empty] | U | 2543 |  | USV-2543
S-02115 | USV3-2544 | 243.3 | Actuator |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | Diaphragm with spring return | On/Off | FC | 7 bar | No | 10 sec | [25 empty] | U | 2544 |  | USV-2544
S-02115 | USV3-2545 | 243.3 | Actuator |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | Piston with spring return | On/Off | FO | 7 bar | No | 10 | [25 empty] | U | 2545 |  | USV-2545
S-02115 | USV3-2547 | 243.3 | Actuator |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Piston with spring return | On/Off | FC | 7 bar | No | [26 empty] | U | 2547 |  | USV-2547
S-02115 | USV3-2548 | 243.3 | Actuator |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Piston with spring return | On/Off | FC | 7 bar | No | [26 empty] | U | 2548 |  | USV-2548
S-02115 | USV3-2549 | 243.3 | Actuator |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Piston with spring return | On/Off | FO | 7 bar | No | [26 empty] | U | 2549 |  | USV-2549
S-02115 | USV3-3018 | 243.3 | Actuator |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C | Piston with spring return | On/Off | FC | 99 bar | No | [26 empty] | U | 3018 |  | USV-3018
S-02115 | USV3-3052 | 243.3 | Actuator |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Piston with spring return | On/Off | FC | 47 bar | No | [26 empty] | U | 3052 |  | USV-3052
S-02115 | USV3-3172 | 243.3 | Actuator |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | Piston with spring return | On/Off | FC | 100 bar | No | [26 empty] | U | 3172 |  | USV-3172
S-02115 | UV3-5021 | 243.3 | Actuator |  | P29 |  | 24"-VA-50-140-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | Piston with spring return | On/Off | FO | 3.5 bar | No | [26 empty] | U | 5021 |  | UV-5021
S-02115 | USV3-5302 | 243.3 | Actuator |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Piston with spring return | On/Off | FC | 9.5 bar | No | [26 empty] | U | 5302 |  | USV-5302
S-02115 | USV3-5391 | 243.3 | Actuator |  | P43 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Piston with spring return | On/Off | FC | 19 bar | No | [26 empty] | U | 5391 |  | USV-5391
S-02115 | USV3-5392 | 243.3 | Actuator |  | P43 |  | 10"-PMP-50-144-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Piston with spring return | On/Off | FC | 19 bar | No | [26 empty] | U | 5392 |  | USV-5392
S-02115 | USV3-5393 | 243.3 | Actuator |  | P43 |  | 3"-PMP-50-158-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | Piston with spring return | On/Off | FC | 14 bar | No | [26 empty] | U | 5393 |  | USV-5393
S-02115 | USV3-5420 | 243.3 | Actuator |  | P44 |  | 10"-PMP-50-152-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | Piston with spring return | On/Off | FC | 4.5 bar | No | [26 empty] | U | 5420 |  | USV-5420
S-02115 | USV3-5421 | 243.3 | Actuator |  | P44 |  | 3"-PMP-50-156-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | Piston with spring return | On/Off | FC | 14 bar | No | [26 empty] | U | 5421 |  | USV-5421
S-02115 | USV3-5422 | 243.3 | Actuator |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | Piston with spring return | On/Off | FC | 4.5 bar | No | [26 empty] | U | 5422 |  | USV-5422
S-02115 | UV3-6035 | 243.3 | Actuator |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Piston with spring return | On/Off | FC | 71 bar | No | [26 empty] | U | 6035 |  | UV-6035
S-02115 | USV3-6081 | 243.3 | Actuator |  | P08 |  | 2"-BD-60-109-G40-P |  |  | 57 | 1 | bar g |  | 73 | 260 | °C | Diaphragm with spring return | On/Off | FC | 57 bar | No | [26 empty] | U | 6081 |  | USV-6081
S-02115 | USV3-6082 | 243.3 | Actuator |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | Piston with spring return | On/Off | FC | 57 bar | No | [26 empty] | U | 6082 |  | USV-6082
S-02115 | FV4-2007 | 243.4 | Positioner |  | P02 |  | 10"-PO-20-106-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | FF/P | [30 empty] | F | 2007 |  | FV-2007
S-02115 | FV4-2009 | 243.4 | Positioner |  | P02 |  | 4"-PO-20-105-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C | FF/P | [30 empty] | F | 2009 |  | FV-2009
S-02115 | FV4-2040 | 243.4 | Positioner |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | F | 2040 |  | FV-2040
S-02115 | FV4-2061 | 243.4 | Positioner |  | P10 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF/P | [30 empty] | F | 2061 |  | FV-2061
S-02115 | FV4-2072 | 243.4 | Positioner |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | F | 2072 |  | FV-2072
S-02115 | FV4-2079 | 243.4 | Positioner |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF/P | [30 empty] | F | 2079 |  | FV-2079
S-02115 | FV4-2091 | 243.4 | Positioner |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF/P | [30 empty] | F | 2091 |  | FV-2091
S-02115 | FV4-2150 | 243.4 | Positioner |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | FF/P | [30 empty] | F | 2150 |  | FV-2150
S-02115 | FV4-2233/1 | 243.4 | Positioner |  | P13 |  | 3"-PRC-20-130-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | FF/P | [30 empty] | F | 2233 | 1 | FV-2233/1
S-02115 | FV4-2233/2 | 243.4 | Positioner |  | P13 |  | 3"-BFW-70-103-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | F | 2233 | 2 | FV-2233/2
S-02115 | FV4-2417 | 243.4 | Positioner |  | P19 |  | 12"-BFW-70-107-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | F | 2417 |  | FV-2417
S-02115 | FV4-2531/1 | 243.4 | Positioner |  | U01 |  | 10"-NG-20-104-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF/P | [30 empty] | F | 2531 | 1 | FV-2531/1
S-02115 | FV4-2531/2 | 243.4 | Positioner |  | U01 |  | 24"-NG-20-112-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | FF/P | [30 empty] | F | 2531 | 2 | FV-2531/2
S-02115 | FV4-2536 | 243.4 | Positioner |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF/P | [30 empty] | F | 2536 |  | FV-2536
S-02115 | FV4-3041 | 243.4 | Positioner |  | P23 |  | 8"-BFW-70-101-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | FF/P | [30 empty] | F | 3041 |  | FV-3041
S-02115 | FV4-3169 | 243.4 | Positioner |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | F | 3169 |  | FV-3169
S-02115 | FV4-3171 | 243.4 | Positioner |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | F | 3171 |  | FV-3171
S-02115 | FV4-5020 | 243.4 | Positioner |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | F | 5020 |  | FV-5020
S-02115 | FV4-5041 | 243.4 | Positioner |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | FF/P | [30 empty] | F | 5041 |  | FV-5041
S-02115 | FV4-5093 | 243.4 | Positioner |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF/P | [30 empty] | F | 5093 |  | FV-5093
S-02115 | FV4-5107 | 243.4 | Positioner |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | FF/P | [30 empty] | F | 5107 |  | FV-5107
S-02115 | FV4-5161 | 243.4 | Positioner |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | FF/P | [30 empty] | F | 5161 |  | FV-5161
S-02115 | FV4-5203 | 243.4 | Positioner |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | FF/P | [30 empty] | F | 5203 |  | FV-5203
S-02115 | FV4-5239 | 243.4 | Positioner |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | FF/P | [30 empty] | F | 5239 |  | FV-5239
S-02115 | FV4-5301 | 243.4 | Positioner |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | FF/P | [30 empty] | F | 5301 |  | FV-5301
S-02115 | FV4-5321 | 243.4 | Positioner |  | P40 |  | 12"-PMP-50-132-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | FF/P | [30 empty] | F | 5321 |  | FV-5321
S-02115 | FV4-5336 | 243.4 | Positioner |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | FF/P | [30 empty] | F | 5336 |  | FV-5336
S-02115 | FV4-5337 | 243.4 | Positioner |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | FF/P | [30 empty] | F | 5337 |  | FV-5337
S-02115 | FV4-5367 | 243.4 | Positioner |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | FF/P | [30 empty] | F | 5367 |  | FV-5367
S-02115 | FV4-5383 | 243.4 | Positioner |  | P42 |  | 2"-DMW-50-101-B50-N |  |  | 7 | 5 | bar g |  | 35 | 65 | °C | FF/P | [30 empty] | F | 5383 |  | FV-5383
S-02115 | FV4-5441 | 243.4 | Positioner |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | FF/P | [30 empty] | F | 5441 |  | FV-5441
S-02115 | FV4-5501 | 243.4 | Positioner |  | U23A |  | 6"-PMW-50-194-B24-H |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | FF/P | [30 empty] | F | 5501 |  | FV-5501
S-02115 | FV4-6031 | 243.4 | Positioner |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | F | 6031 |  | FV-6031
S-02115 | FV4-6070 | 243.4 | Positioner |  | P07 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | FF/P | [30 empty] | F | 6070 |  | FV-6070
S-02115 | FV4-6081 | 243.4 | Positioner |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | FF/P | [30 empty] | F | 6081 |  | FV-6081
S-02115 | FV4-6082 | 243.4 | Positioner |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | FF/P | [30 empty] | F | 6082 |  | FV-6082
S-02115 | FV4-6086 | 243.4 | Positioner |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | FF/P | [30 empty] | F | 6086 |  | FV-6086
S-02115 | FV4-7091 | 243.4 | Positioner |  | U09 |  | 8"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | FF/P | [30 empty] | F | 7091 |  | FV-7091
S-02115 | FV4-7141 | 243.4 | Positioner |  | U11 |  | 8"-BFW-70-163-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | F | 7141 |  | FV-7141
S-02115 | HV4-2031 | 243.4 | Positioner |  | P03 |  | 2"-HPS-20-110-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | H | 2031 |  | HV-2031
S-02115 | HV4-2076 | 243.4 | Positioner |  | P09 |  | 8"-HPS-20-114-F24-H |  |  | 52 | 44 | bar g |  | 343 | 410 | °C | FF/P | [30 empty] | H | 2076 |  | HV-2076
S-02115 | HV5-2097 | 243.4 | Positioner |  | P10 |  | 3"-HPS-20-112-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | FF/P | [30 empty] | H | 2097 |  | HV-2097
S-02115 | HV4-2371 | 243.4 | Positioner |  | P18 |  | 6"-BFW-20-109-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | FF/P | [30 empty] | H | 2371 |  | HV-2371
S-02115 | HV4-3011 | 243.4 | Positioner |  | P22 |  | 2"-SG-30-131-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | H | 3011 |  | HV-3011
S-02115 | HV4-5338 | 243.4 | Positioner |  | P40 |  | 3"-PMV-50-116-B24-P |  |  | 6 | 2.6 | bar g |  | 101 | 165 | °C | FF/P | [30 empty] | H | 5338 |  | HV-5338
S-02115 | HV4-6069 | 243.4 | Positioner |  | P07 |  | 16"-PRG-60-107-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | FF/P | [30 empty] | H | 6069 |  | HV-6069
S-02115 | LV4-2016 | 243.4 | Positioner |  | P02 |  | 6"-HPC-20-102-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | FF/P | [30 empty] | L | 2016 |  | LV-2016
S-02115 | LV4-2372 | 243.4 | Positioner |  | P19 |  | 6"-BFW-20-106-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | L | 2372 |  | LV-2372
S-02115 | LV4-2403 | 243.4 | Positioner |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | FF/P | [30 empty] | L | 2403 |  | LV-2403
S-02115 | LV4-2419 | 243.4 | Positioner |  | P19 |  | 4"-PRC-20-123-F40-H |  |  | 30 | 26 | bar g |  | 159 | 200 | °C | FF/P | [30 empty] | L | 2419 |  | LV-2419
S-02115 | LV4-2441 | 243.4 | Positioner |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | FF/P | [30 empty] | L | 2441 |  | LV-2441
S-02115 | LV4-2474 | 243.4 | Positioner |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | FF/P | [30 empty] | L | 2474 |  | LV-2474
S-02115 | LV4-3161/A | 243.4 | Positioner |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV4-3161/B | 243.4 | Positioner |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV4-3192 | 243.4 | Positioner |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | L | 3192 |  | LV-3192
S-02115 | LV4-5070 | 243.4 | Positioner |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | FF/P | [30 empty] | L | 5070 |  | LV-5070
S-02115 | LV4-5501 | 243.4 | Positioner |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | FF/P | [30 empty] | L | 5501 |  | LV-5501
S-02115 | LV4-6021/A | 243.4 | Positioner |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | FF/P | [30 empty] | L | 6021 | A | LV-6021/A
S-02115 | LV4-6021/B | 243.4 | Positioner |  | P05 |  | 18"-MPC-60-104-F24-H |  |  | 47 | 32.5 | bar g |  | 240 | 260 | °C | FF/P | [30 empty] | L | 6021 | B | LV-6021/B
S-02115 | LV4-6082 | 243.4 | Positioner |  | P08 |  | 4"-BD-60-111-B40-N |  |  | 9 | 1.5 | bar g |  | 65 | 125 | °C | FF/P | [30 empty] | L | 6082 |  | LV-6082
S-02115 | LV4-7251 | 243.4 | Positioner |  | U16 |  | 3"-BD-70-111-B24-N |  |  | 10.5 | 8 | bar g |  | 173 | 200 | °C | FF/P | [30 empty] | L | 7251 |  | LV-7251
S-02115 | PV4-1006 | 243.4 | Positioner |  | P01 |  | 14"-NG-10-102-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | FF/P | [30 empty] | P | 1006 |  | PV-1006
S-02115 | PV4-1011 | 243.4 | Positioner |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF/P | [30 empty] | P | 1011 |  | PV-1011
S-02115 | PV4-1045 | 243.4 | Positioner |  | P04 |  | 8"-PRG-10-108-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | FF/P | [30 empty] | P | 1045 |  | PV-1045
S-02115 | PV4-2015 | 243.4 | Positioner |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | FF/P | [30 empty] | P | 2015 |  | PV-2015
S-02115 | PV4-2073 | 243.4 | Positioner |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | FF/P | [30 empty] | P | 2073 |  | PV-2073
S-02115 | PV4-2361 | 243.4 | Positioner |  | P17 |  | 8"-HHPS-20-2054-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF/P | [30 empty] | P | 2361 |  | PV-2361
S-02115 | PV4-2363 | 243.4 | Positioner |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | FF/P | [30 empty] | P | 2363 |  | PV-2363
S-02115 | PV4-2406 | 243.4 | Positioner |  | P19 |  | 18"-RFG-20-118-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF/P | [30 empty] | P | 2406 |  | PV-2406
S-02115 | PV4-2481 | 243.4 | Positioner |  | P21 |  | 18"-SG-20-105-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | P | 2481 |  | PV-2481
S-02115 | PV4-2536 | 243.4 | Positioner |  | U01 |  | 14"-PG-20-129-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | FF/P | [30 empty] | P | 2536 |  | PV-2536
S-02115 | PV4-2575 | 243.4 | Positioner |  | U02 |  | 8"-N-20-105-B24-P |  |  | 10.5 | 6 | bar g |  | 70 | 110 | °C | FF/P | [30 empty] | P | 2575 |  | PDV-2575
S-02115 | PV4-2603 | 243.4 | Positioner |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | FF/P | [30 empty] | P | 2603 |  | PV-2603
S-02115 | PV4-2608 | 243.4 | Positioner |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | P | 2608 |  | PV-2608
S-02115 | PV4-3042 | 243.4 | Positioner |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | FF/P | [30 empty] | P | 3042 |  | PV-3042
S-02115 | PV4-3166 | 243.4 | Positioner |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | P | 3166 |  | PV-3166
S-02115 | PV4-3194 | 243.4 | Positioner |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | FF/P | [30 empty] | P | 3194 |  | PV-3194
S-02115 | PV4-5069 | 243.4 | Positioner |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FF/P | [30 empty] | P | 5069 |  | PV-5069
S-02115 | PV4-5091/A | 243.4 | Positioner |  | P32 |  | 2"-N-50-104-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | FF/P | [30 empty] | P | 5091 | A | PV-5091/A
S-02115 | PV4-5091/B | 243.4 | Positioner |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | FF/P | [30 empty] | P | 5091 | B | PV-5091/B
S-02115 | PV4-5109 | 243.4 | Positioner |  | P32 |  | 4"-PG-50-103-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | FF/P | [30 empty] | P | 5109 |  | PV-5109
S-02115 | PV4-5207/A | 243.4 | Positioner |  | P36 |  | 2"-N-50-107-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | FF/P | [30 empty] | P | 5207 | A | PV-5207/A
S-02115 | PV4-5207/B | 243.4 | Positioner |  | P36 |  | 2"-VA-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | FF/P | [30 empty] | P | 5207 | B | PV-5207/B
S-02115 | PV4-6025 | 243.4 | Positioner |  | P06 |  | 24"-MPS-70-101-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF/P | [30 empty] | P | 6025 |  | PV-6025
S-02115 | PV4-7002/A | 243.4 | Positioner |  | U03 |  | 10"-HHPS-70-115-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF/P | [30 empty] | P | 7002 | A | PV-7002/A
S-02115 | PV4-7002/B | 243.4 | Positioner |  | U03 |  | 24"-HHPS-70-114-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF/P | [30 empty] | P | 7002 | B | PV-7002/B
S-02115 | PV4-7002/C | 243.4 | Positioner |  | U03 |  | 24"-HHPS-70-113-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF/P | [30 empty] | P | 7002 | C | PV-7002/C
S-02115 | PV4-7004 | 243.4 | Positioner |  | U03 |  | 16"-HPS-70-108-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | P | 7004 |  | PV-7004
S-02115 | PV4-7025/A | 243.4 | Positioner |  | U04 |  | 18"-HHPS-70-121-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF/P | [30 empty] | P | 7025 | A | PV-7025/A
S-02115 | PV4-7025/B | 243.4 | Positioner |  | U04 |  | 18"-HHPS-70-120-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF/P | [30 empty] | P | 7025 | B | PV-7025/B
S-02115 | PV4-7028 | 243.4 | Positioner |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | FF/P | [30 empty] | P | 7028 |  | PV-7028
S-02115 | PV4-7031/A | 243.4 | Positioner |  | U05 |  | 24"-HPS-70-130-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | P | 7031 | A | PV-7031/A
S-02115 | PV4-7031/B | 243.4 | Positioner |  | U05 |  | 24"-HPS-70-131-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | P | 7031 | B | PV-7031/B
S-02115 | PV4-7031/C | 243.4 | Positioner |  | U05 |  | 10"-MPS-70-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF/P | [30 empty] | P | 7031 | C | PV-7031/C
S-02115 | PV4-7031/D | 243.4 | Positioner |  | U05 |  | 10"-MPS-70-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF/P | [30 empty] | P | 7031 | D | PV-7031/D
S-02115 | PV4-7034 | 243.4 | Positioner |  | U05 |  | 14"-MPS-70-121-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | FF/P | [30 empty] | P | 7034 |  | PV-7034
S-02115 | PV4-7051/A | 243.4 | Positioner |  | U06 |  | 16"-HPS-70-120-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | FF/P | [30 empty] | P | 7051 | A | PV-7051/A
S-02115 | PV4-7051/B | 243.4 | Positioner |  | U06 |  | 16"-HPS-70-121-F34-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | FF/P | [30 empty] | P | 7051 | B | PV-7051/B
S-02115 | PV4-7056 | 243.4 | Positioner |  | U06 |  | 24"-LPS-70-109-D24-P |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FF/P | [30 empty] | P | 7056 |  | PV-7056
S-02115 | PV4-7094 | 243.4 | Positioner |  | U09 |  | 18"-LPS-70-127-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | FF/P | [30 empty] | P | 7094 |  | PV-7094
S-02115 | PV4-7101 | 243.4 | Positioner |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | FF/P | [30 empty] | P | 7101 |  | PV-7101
S-02115 | TV4-2220 | 243.4 | Positioner |  | P12 |  | 8"-NG-10-106-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | FF/P | [30 empty] | T | 2220 |  | TV-2220
S-02115 | TV4-2457 | 243.4 | Positioner |  | P20 |  | 16"-RFG-20-127-D40-P |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | FF/P | [30 empty] | T | 2457 |  | TV-2457
S-02115 | TV4-3113 | 243.4 | Positioner |  | P25 |  | 10"-SG-30-926-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | FF/P | [30 empty] | T | 3113 |  | TV-3113
S-02115 | TV4-3116 | 243.4 | Positioner |  | P25 |  | 10"-SG-30-931-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | FF/P | [30 empty] | T | 3116 |  | TV-3116
S-02115 | TV4-3118 | 243.4 | Positioner |  | P25 |  | 10"-SG-30-937-H40-H |  |  | 99 | 80 | bar g |  | 74 | 260 | °C | FF/P | [30 empty] | T | 3118 |  | TV-3118
S-02115 | TV4-5064 | 243.4 | Positioner |  | P30 |  | 16"-RFG-50-103-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | FF/P | [30 empty] | T | 5064 |  | TV-5064
S-02115 | TV4-5277 | 243.4 | Positioner |  | P38 |  | 18"-RFG-50-125-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | FF/P | [30 empty] | T | 5277 |  | TV-5277
S-02115 | TV4-7002 | 243.4 | Positioner |  | U03 |  | 2"-BFW-70-104-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7002 |  | TV-7002
S-02115 | TV4-7003 | 243.4 | Positioner |  | U03 |  | 3"-BFW-70-143-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7003 |  | TV-7003
S-02115 | TV4-7004 | 243.4 | Positioner |  | U03 |  | 3"-BFW-70-141-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7004 |  | TV-7004
S-02115 | TV4-7025/A | 243.4 | Positioner |  | U04 |  | 2"-BFW-70-152-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7025 | A | TV-7025/A
S-02115 | TV4-7025/B | 243.4 | Positioner |  | U04 |  | 2"-BFW-70-154-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7025 | B | TV-7025/B
S-02115 | TV4-7026 | 243.4 | Positioner |  | U04 |  | 2"-BFW-70-112-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7026 |  | TV-7026
S-02115 | TV4-7027 | 243.4 | Positioner |  | U04 |  | 2"-BFW-70-156-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7027 |  | TV-7027
S-02115 | TV4-7032 | 243.4 | Positioner |  | U05 |  | 2"-BFW-70-115-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7032 |  | TV-7032
S-02115 | TV4-7033 | 243.4 | Positioner |  | U05 |  | 2"-BFW-70-108-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7033 |  | TV-7033
S-02115 | TV4-7052 | 243.4 | Positioner |  | U06 |  | 2"-BFW-70-121-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7052 |  | TV-7052
S-02115 | TV4-7053 | 243.4 | Positioner |  | U06 |  | 2"-BFW-70-119-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7053 |  | TV-7053
S-02115 | TV4-7071/A | 243.4 | Positioner |  | U07 |  | 2"-BFW-70-124-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | FF/P | [30 empty] | T | 7071 | A | TV-7071/A
S-02115 | TV4-7071/B | 243.4 | Positioner |  | U07 |  | 2"-BFW-70-145-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | FF/P | [30 empty] | T | 7071 | B | TV-7071/B
S-02115 | FV6-2061 | 243.6 | Solenoid Valve |  | P10 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 3-Way, 2oo2 D configuration | FUSY-2061 | [29 empty] | F | 2061 |  | FV-2061
S-02115 | FV6-2091 | 243.6 | Solenoid Valve |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 3-Way | FUSY-2091 | [29 empty] | F | 2091 |  | FV-2091
S-02115 | FV6-2150 | 243.6 | Solenoid Valve |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 3-Way | FUSY-2150 | [29 empty] | F | 2150 |  | FV-2150
S-02115 | FV6-2536 | 243.6 | Solenoid Valve |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 3-Way | FUY-2536 | [29 empty] | F | 2536 |  | FV-2536
S-02115 | FV6-3171 | 243.6 | Solenoid Valve |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 3-Way | FUSY-3171 | [29 empty] | F | 3171 |  | FV-3171
S-02115 | FV6-5020 | 243.6 | Solenoid Valve |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 3-Way | FUSY-5020 | [29 empty] | F | 5020 |  | FV-5020
S-02115 | FV6-5041 | 243.6 | Solenoid Valve |  | P30 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 3-Way | FUY-5041 | [29 empty] | F | 5041 |  | FV-5041
S-02115 | FV6-5107 | 243.6 | Solenoid Valve |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 3-Way | FUY-5107 | [29 empty] | F | 5107 |  | FV-5107
S-02115 | FV6-5161 | 243.6 | Solenoid Valve |  | P34 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 3-Way | FUY-5161 | [29 empty] | F | 5161 |  | FV-5161
S-02115 | FV6-5239 | 243.6 | Solenoid Valve |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 3-Way | FUY-5239 | [29 empty] | F | 5239 |  | FV-5239
S-02115 | FV6-5336 | 243.6 | Solenoid Valve |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 3-Way | FUY-5336 | [29 empty] | F | 5336 |  | FV-5336
S-02115 | FV6-5337 | 243.6 | Solenoid Valve |  | P40 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 3-Way | FUY-5337 | [29 empty] | F | 5337 |  | FV-5337
S-02115 | FV6-5441 | 243.6 | Solenoid Valve |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 3-Way | FUSY-5441 | [29 empty] | F | 5441 |  | FV-5441
S-02115 | FV6-6031 | 243.6 | Solenoid Valve |  | P06 |  | 4"-BFW-70-102-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 3-Way | FUY-6031 | [29 empty] | F | 6031 |  | FV-6031
S-02115 | FV6-6081 | 243.6 | Solenoid Valve |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 3-Way | FUSY-6081 | [29 empty] | F | 6081 |  | FV-6081
S-02115 | FV5-6082 | 243.6 | Solenoid Valve |  | P08 |  | 2"-BD-60-121-B40-P |  |  | 9 | 2.5 | bar g |  | 100 | 125 | °C | 3-Way | FUY-6082 | [29 empty] | F | 6082 |  | FV-6082
S-02115 | FV6-6086 | 243.6 | Solenoid Valve |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 3-Way | FUSY-6086 | [29 empty] | F | 6086 |  | FV-6086
S-02115 | LV6-2403 | 243.6 | Solenoid Valve |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | 3-Way | LUSY-2403 | [29 empty] | L | 2403 |  | LV-2403
S-02115 | LV6-2441 | 243.6 | Solenoid Valve |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | 3-Way | LUSY-2441 | [29 empty] | L | 2441 |  | LV-2441
S-02115 | LV6-2474 | 243.6 | Solenoid Valve |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 3-Way | LUSY-2474 | [29 empty] | L | 2474 |  | LV-2474
S-02115 | LV6-3161/A | 243.6 | Solenoid Valve |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | 3-Way | LUSY-3161/A | [29 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV6-3161/B | 243.6 | Solenoid Valve |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | 3-Way | LUSY-3161/B | [29 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV6-3192 | 243.6 | Solenoid Valve |  | P28 |  | 10"-PMC-30-108-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 3-Way | LUSY-3192 | [29 empty] | L | 3192 |  | LV-3192
S-02115 | LV6-5070 | 243.6 | Solenoid Valve |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | 3-Way | LUSY-5070 | [29 empty] | L | 5070 |  | LV-5070
S-02115 | LV6-5501 | 243.6 | Solenoid Valve |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | 3-Way | LUSY-5501 | [29 empty] | L | 5501 |  | LV-5501
S-02115 | LV6-6021/B | 243.6 | Solenoid Valve |  | P05 |  | 18"-MPC-60-104-F24-H |  |  | 47 | 32.5 | bar g |  | 240 | 260 | °C | 3-Way | LUSY-6021 | [29 empty] | L | 6021 | B | LV-6021/B
S-02115 | LV5-6082 | 243.6 | Solenoid Valve |  | P08 |  | 4"-BD-60-111-B40-N |  |  | 9 | 1.5 | bar g |  | 65 | 125 | °C | 3-Way | LUY-6082 | [29 empty] | L | 6082 |  | LV-6082
S-02115 | PV6-2073 | 243.6 | Solenoid Valve |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 3-Way | PUSY-2073 | [29 empty] | P | 2073 |  | PV-2073
S-02115 | PV6-5069 | 243.6 | Solenoid Valve |  | P31 |  | 14"-LPS-70-104-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 3-Way | PUSY-5069 | [29 empty] | P | 5069 |  | PV-5069
S-02115 | USV6-1001 | 243.6 | Solenoid Valve |  | P01 |  | 2"-OW-10-103-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 3-Way | USY-1001 | [29 empty] | U | 1001 |  | USV-1001
S-02115 | USV5-2010 | 243.6 | Solenoid Valve |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | 3-Way | USY-2010 A | [29 empty] | U | 2010 |  | USV-2010
S-02115 | USV6-2010 | 243.6 | Solenoid Valve |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | 3-Way | USY-2010 B | [29 empty] | U | 2010 |  | USV-2010
S-02115 | USV6-2021 | 243.6 | Solenoid Valve |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 3-Way, 2oo2 D configuration | USY-2021 | [29 empty] | U | 2021 |  | USV-2021
S-02115 | USV6-2038 | 243.6 | Solenoid Valve |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 3-Way, 2oo2 D configuration | USY-2038 | [29 empty] | U | 2038 |  | USV-2038
S-02115 | USV5-2043 | 243.6 | Solenoid Valve |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2043 A | [29 empty] | U | 2043 |  | USV-2043
S-02115 | USV6-2043 | 243.6 | Solenoid Valve |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2043 B | [29 empty] | U | 2043 |  | USV-2043
S-02115 | USV5-2045 | 243.6 | Solenoid Valve |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2045 A | [29 empty] | U | 2045 |  | USV-2045
S-02115 | USV6-2045 | 243.6 | Solenoid Valve |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2045 B | [29 empty] | U | 2045 |  | USV-2045
S-02115 | USV5-2048 | 243.6 | Solenoid Valve |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2048 A | [29 empty] | U | 2048 |  | USV-2048
S-02115 | USV6-2048 | 243.6 | Solenoid Valve |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2048 B | [29 empty] | U | 2048 |  | USV-2048
S-02115 | USV5-2049 | 243.6 | Solenoid Valve |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2049 A | [29 empty] | U | 2049 |  | USV-2049
S-02115 | USV6-2049 | 243.6 | Solenoid Valve |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 3-Way | USY-2049 B | [29 empty] | U | 2049 |  | USV-2049
S-02115 | USV6-2092 | 243.6 | Solenoid Valve |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | 3-Way, 2oo2 D configuration | USY-2092 | [29 empty] | U | 2092 |  | USV-2092
S-02115 | USV6-2093 | 243.6 | Solenoid Valve |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | 3-Way, 2oo2 D configuration | USY-2093 | [29 empty] | U | 2093 |  | USV-2093
S-02115 | USV6-2094 | 243.6 | Solenoid Valve |  | P10 |  | 2"-PRG-20-109-F24-H |  |  | 55 | 41.1 | bar g |  | 262 | 290 | °C | 3-Way, 2oo2 D configuration | USY-2094 | [29 empty] | U | 2094 |  | USV-2094
S-02115 | USV6-2117 | 243.6 | Solenoid Valve |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 3-Way | USY-2117 | [29 empty] | U | 2117 |  | USV-2117
S-02115 | UV6-2125 | 243.6 | Solenoid Valve |  | P11 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | 3-Way | UY-2125 | [29 empty] | U | 2125 |  | UV-2125
S-02115 | USV6-2166 | 243.6 | Solenoid Valve |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 3-Way | USY-2166 | [29 empty] | U | 2166 |  | USV-2166
S-02115 | UV6-2233 | 243.6 | Solenoid Valve |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 3-Way | UY-2233 | [29 empty] | U | 2233 |  | UV-2233
S-02115 | USV6-2381 | 243.6 | Solenoid Valve |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 3-Way | USY-2381 | [29 empty] | U | 2381 |  | USV-2381
S-02115 | USV6-2482 | 243.6 | Solenoid Valve |  | P21 |  | 12"-SG-20-106-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 3-Way, 2oo2 D configuration | USY-2482 | [29 empty] | U | 2482 |  | USV-2482
S-02115 | USV4-2541 | 243.6 | Solenoid Valve |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 3-Way, 2oo2 D configuration | USY-2541 | [29 empty] | U | 2541 |  | USV-2541
S-02115 | USV4-2542 | 243.6 | Solenoid Valve |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 3-Way, 2oo2 D configuration | USY-2542 | [29 empty] | U | 2542 |  | USV-2542
S-02115 | USV4-2543 | 243.6 | Solenoid Valve |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 3-Way, 2oo2 D configuration | USY-2543 | [29 empty] | U | 2543 |  | USV-2543
S-02115 | USV4-2544 | 243.6 | Solenoid Valve |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | 3-Way, 2oo2 D configuration | USY-2544 | [29 empty] | U | 2544 |  | USV-2544
S-02115 | USV4-2545 | 243.6 | Solenoid Valve |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | 3-Way, 2oo2 D configuration | USY-2545 | [29 empty] | U | 2545 |  | USV-2545
S-02115 | USV4-2547 | 243.6 | Solenoid Valve |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 3-Way | USY-2547 | [29 empty] | U | 2547 |  | USV-2547
S-02115 | USV4-2548 | 243.6 | Solenoid Valve |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 3-Way | USY-2548 | [29 empty] | U | 2548 |  | USV-2548
S-02115 | USV4-2549 | 243.6 | Solenoid Valve |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 3-Way | USY-2549 | [29 empty] | U | 2549 |  | USV-2549
S-02115 | USV6-3018 | 243.6 | Solenoid Valve |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C | 3-Way | USY-3018 | [29 empty] | U | 3018 |  | USV-3018
S-02115 | USV6-3052 | 243.6 | Solenoid Valve |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 3-Way | USY-3052 | [29 empty] | U | 3052 |  | USV-3052
S-02115 | USV6-3172 | 243.6 | Solenoid Valve |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | 3-Way, 2oo2 D configuration | USY-3172 | [29 empty] | U | 3172 |  | USV-3172
S-02115 | UV6-5021 | 243.6 | Solenoid Valve |  | P29 |  | 24"-VA-50-140-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | 3-Way | UY-5021 | [29 empty] | U | 5021 |  | UV-5021
S-02115 | USV6-5302 | 243.6 | Solenoid Valve |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | 3-Way | USY-5302 | [29 empty] | U | 5302 |  | USV-5302
S-02115 | USV6-5391 | 243.6 | Solenoid Valve |  | P43 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 3-Way | USY-5391 | [29 empty] | U | 5391 |  | USV-5391
S-02115 | USV6-5392 | 243.6 | Solenoid Valve |  | P43 |  | 10"-PMP-50-144-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 3-Way | USY-5392 | [29 empty] | U | 5392 |  | USV-5392
S-02115 | USV6-5393 | 243.6 | Solenoid Valve |  | P43 |  | 3"-PMP-50-158-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | 3-Way | USY-5393 | [29 empty] | U | 5393 |  | USV-5393
S-02115 | USV6-5420 | 243.6 | Solenoid Valve |  | P44 |  | 10"-PMP-50-152-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | 3-Way | USY-5420 | [29 empty] | U | 5420 |  | USV-5420
S-02115 | USV6-5421 | 243.6 | Solenoid Valve |  | P44 |  | 3"-PMP-50-156-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | 3-Way | USY-5421 | [29 empty] | U | 5421 |  | USV-5421
S-02115 | USV6-5422 | 243.6 | Solenoid Valve |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | 3-Way | USY-5422 | [29 empty] | U | 5422 |  | USV-5422
S-02115 | UV6-6035 | 243.6 | Solenoid Valve |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 3-Way | UY-6035 | [29 empty] | U | 6035 |  | UV-6035
S-02115 | USV6-6081 | 243.6 | Solenoid Valve |  | P08 |  | 2"-BD-60-109-G40-P |  |  | 57 | 1 | bar g |  | 73 | 260 | °C | 3-Way, 2oo2 D configuration | USY-6081 | [29 empty] | U | 6081 |  | USV-6081
S-02115 | USV6-6082 | 243.6 | Solenoid Valve |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 3-Way, 2oo2 D configuration | USY-6082 | [29 empty] | U | 6082 |  | USV-6082
S-02115 | USV6-7130 | 243.6 | Solenoid Valve |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 3-Way | USY-7130 | [29 empty] | U | 7130 |  | USV-7130
S-02115 | USV6-7135 | 243.6 | Solenoid Valve |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 3-Way | USY-7135 | [29 empty] | U | 7135 |  | USV-7135
S-02115 | FV7-2007 | 243.7 | Limit Switch |  | P02 |  | 10"-PO-20-106-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C |  | FZSL-2007 | [29 empty] | F | 2007 |  | FV-2007
S-02115 | FV7-2009 | 243.7 | Limit Switch |  | P02 |  | 4"-PO-20-105-F70-N |  |  | 47 | 39 | bar g |  | 35 | 85 | °C |  | FZSL-2009 | [29 empty] | F | 2009 |  | FV-2009
S-02115 | FV7-2061 | 243.7 | Limit Switch |  | P10 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C |  | FZSL-2061 | [29 empty] | F | 2061 |  | FV-2061
S-02115 | FV7-2072 | 243.7 | Limit Switch |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C |  | FZSL-2072 | [29 empty] | F | 2072 |  | FV-2072
S-02115 | FV7-2079 | 243.7 | Limit Switch |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C |  | FZSL-2079 | [29 empty] | F | 2079 |  | FV-2079
S-02115 | FV7-2091 | 243.7 | Limit Switch |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C |  | FZSL-2091 | [29 empty] | F | 2091 |  | FV-2091
S-02115 | FV7-2150 | 243.7 | Limit Switch |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C |  | FZSL-2150 | [29 empty] | F | 2150 |  | FV-2150
S-02115 | FV7-3171 | 243.7 | Limit Switch |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C |  | FZSL-3171 | [29 empty] | F | 3171 |  | FV-3171
S-02115 | HV6-1003 | 243.7 | Limit Switch |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | HZSH-1003 | [30 empty] | H | 1003 |  | HV-1003
S-02115 | HV7-1003 | 243.7 | Limit Switch |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C |  | HZSL-1003 | [29 empty] | H | 1003 |  | HV-1003
S-02115 | HV6-2003 | 243.7 | Limit Switch |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | HZSH-2003 | [30 empty] | H | 2003 |  | HV-2003
S-02115 | HV7-2003 | 243.7 | Limit Switch |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C |  | HZSL-2003 | [29 empty] | H | 2003 |  | HV-2003
S-02115 | HV6-2098 | 243.7 | Limit Switch |  | P10 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | HZSH-2098 | [30 empty] | H | 2098 |  | HV-2098
S-02115 | HV7-2098 | 243.7 | Limit Switch |  | P10 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C |  | HZSL-2098 | [29 empty] | H | 2098 |  | HV-2098
S-02115 | HV7-2225/1 | 243.7 | Limit Switch |  | P13 | [10 empty] | °C |  | HZSL-2225/1 | [29 empty] | H | 2225 | 1 | HV-2225/1
S-02115 | HV7-2225/2 | 243.7 | Limit Switch |  | P13 | [10 empty] | °C |  | HZSL-2225/2 | [29 empty] | H | 2225 | 2 | HV-2225/2
S-02115 | LV7-2403 | 243.7 | Limit Switch |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C |  | LZSL-2403 | [29 empty] | L | 2403 |  | LV-2403
S-02115 | LV7-3161/A | 243.7 | Limit Switch |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C |  | LZSL-3161/A | [29 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV7-3161/B | 243.7 | Limit Switch |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C |  | LZSL-3161/B | [29 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV7-5501 | 243.7 | Limit Switch |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C |  | LZSL-5501 | [29 empty] | L | 5501 |  | LV-5501
S-02115 | PV7-2073 | 243.7 | Limit Switch |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C |  | PZSL-2073 | [29 empty] | P | 2073 |  | PV-2073
S-02115 | USV7-1001 | 243.7 | Limit Switch |  | P01 |  | 2"-OW-10-103-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | UZSH-1001 | [30 empty] | U | 1001 |  | USV-1001
S-02115 | USV8-1001 | 243.7 | Limit Switch |  | P01 |  | 2"-OW-10-103-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C |  | UZSL-1001 | [29 empty] | U | 1001 |  | USV-1001
S-02115 | USV7-2010 | 243.7 | Limit Switch |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | UZSH-2010 | [30 empty] | U | 2010 |  | USV-2010
S-02115 | USV8-2010 | 243.7 | Limit Switch |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C |  | UZSL-2010 | [29 empty] | U | 2010 |  | USV-2010
S-02115 | USV7-2021 | 243.7 | Limit Switch |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | UZSH-2021 | [30 empty] | U | 2021 |  | USV-2021
S-02115 | USV8-2021 | 243.7 | Limit Switch |  | P02 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C |  | UZSL-2021 | [29 empty] | U | 2021 |  | USV-2021
S-02115 | USV7-2038 | 243.7 | Limit Switch |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | UZSH-2038 | [30 empty] | U | 2038 |  | USV-2038
S-02115 | USV8-2038 | 243.7 | Limit Switch |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C |  | UZSL-2038 | [29 empty] | U | 2038 |  | USV-2038
S-02115 | USV7-2043 | 243.7 | Limit Switch |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | UZSH-2043 | [30 empty] | U | 2043 |  | USV-2043
S-02115 | USV8-2043 | 243.7 | Limit Switch |  | P03 |  | 3"-PO-20-103-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C |  | UZSL-2043 | [29 empty] | U | 2043 |  | USV-2043
S-02115 | USV7-2045 | 243.7 | Limit Switch |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | UZSH-2045 | [30 empty] | U | 2045 |  | USV-2045
S-02115 | USV8-2045 | 243.7 | Limit Switch |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C |  | UZSL-2045 | [29 empty] | U | 2045 |  | USV-2045
S-02115 | USV7-2048 | 243.7 | Limit Switch |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | UZSH-2048 | [30 empty] | U | 2048 |  | USV-2048
S-02115 | USV8-2048 | 243.7 | Limit Switch |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C |  | UZSL-2048 | [29 empty] | U | 2048 |  | USV-2048
S-02115 | USV7-2049 | 243.7 | Limit Switch |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | UZSH-2049 | [30 empty] | U | 2049 |  | USV-2049
S-02115 | USV8-2049 | 243.7 | Limit Switch |  | P03 |  | 1 1/2"-PO-20-109-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C |  | UZSL-2049 | [29 empty] | U | 2049 |  | USV-2049
S-02115 | USV7-2092 | 243.7 | Limit Switch |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | UZSH-2092 | [30 empty] | U | 2092 |  | USV-2092
S-02115 | USV8-2092 | 243.7 | Limit Switch |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C |  | UZSL-2092 | [29 empty] | U | 2092 |  | USV-2092
S-02115 | USV7-2093 | 243.7 | Limit Switch |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C | UZSH-2093 | [30 empty] | U | 2093 |  | USV-2093
S-02115 | USV8-2093 | 243.7 | Limit Switch |  | P10 |  | 24"-PRG-20-108-F24-H |  |  | 55 | 42.1 | bar g |  | 262 | 290 | °C |  | UZSL-2093 | [29 empty] | U | 2093 |  | USV-2093
S-02115 | USV7-2094 | 243.7 | Limit Switch |  | P10 |  | 2"-PRG-20-109-F24-H |  |  | 55 | 41.1 | bar g |  | 262 | 290 | °C | UZSH-2094 | [30 empty] | U | 2094 |  | USV-2094
S-02115 | USV8-2094 | 243.7 | Limit Switch |  | P10 |  | 2"-PRG-20-109-F24-H |  |  | 55 | 41.1 | bar g |  | 262 | 290 | °C |  | UZSL-2094 | [29 empty] | U | 2094 |  | USV-2094
S-02115 | USV7-2117 | 243.7 | Limit Switch |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | UZSH-2117 | [30 empty] | U | 2117 |  | USV-2117
S-02115 | USV8-2117 | 243.7 | Limit Switch |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | UZSL-2117 | [29 empty] | U | 2117 |  | USV-2117
S-02115 | UV7-2125 | 243.7 | Limit Switch |  | P11 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | UZSH-2125 | [30 empty] | U | 2125 |  | UV-2125
S-02115 | UV8-2125 | 243.7 | Limit Switch |  | P11 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C |  | UZSL-2125 | [29 empty] | U | 2125 |  | UV-2125
S-02115 | USV7-2166 | 243.7 | Limit Switch |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | UZSH-2166 | [30 empty] | U | 2166 |  | USV-2166
S-02115 | USV8-2166 | 243.7 | Limit Switch |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | UZSL-2166 | [29 empty] | U | 2166 |  | USV-2166
S-02115 | UV7-2233 | 243.7 | Limit Switch |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | UZSH-2233 | [30 empty] | U | 2233 |  | UV-2233
S-02115 | UV8-2233 | 243.7 | Limit Switch |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C |  | UZSL-2233 | [29 empty] | U | 2233 |  | UV-2233
S-02115 | USV7-2381 | 243.7 | Limit Switch |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | UZSH-2381 | [30 empty] | U | 2381 |  | USV-2381
S-02115 | USV8-2381 | 243.7 | Limit Switch |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C |  | UZSL-2381 | [29 empty] | U | 2381 |  | USV-2381
S-02115 | USV7-2482 | 243.7 | Limit Switch |  | P21 |  | 12"-SG-20-106-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | UZSH-2482 | [30 empty] | U | 2482 |  | USV-2482
S-02115 | USV8-2482 | 243.7 | Limit Switch |  | P21 |  | 12"-SG-20-106-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C |  | UZSL-2482 | [29 empty] | U | 2482 |  | USV-2482
S-02115 | USV5-2541 | 243.7 | Limit Switch |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | UZSH-2541 | [30 empty] | U | 2541 |  | USV-2541
S-02115 | USV6-2541 | 243.7 | Limit Switch |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C |  | UZLL-2541 | [29 empty] | U | 2541 |  | USV-2541
S-02115 | USV5-2542 | 243.7 | Limit Switch |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | UZSH-2542 | [30 empty] | U | 2542 |  | USV-2542
S-02115 | USV6-2542 | 243.7 | Limit Switch |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C |  | UZLL-2542 | [29 empty] | U | 2542 |  | USV-2542
S-02115 | USV5-2543 | 243.7 | Limit Switch |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | UZSH-2543 | [30 empty] | U | 2543 |  | USV-2543
S-02115 | USV6-2543 | 243.7 | Limit Switch |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C |  | UZSL-2543 | [29 empty] | U | 2543 |  | USV-2543
S-02115 | USV5-2544 | 243.7 | Limit Switch |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | UZSH-2544 | [30 empty] | U | 2544 |  | USV-2544
S-02115 | USV6-2544 | 243.7 | Limit Switch |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C |  | UZLL-2544 | [29 empty] | U | 2544 |  | USV-2544
S-02115 | USV5-2545 | 243.7 | Limit Switch |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | UZSH-2545 | [30 empty] | U | 2545 |  | USV-2545
S-02115 | USV6-2545 | 243.7 | Limit Switch |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C |  | UZSL-2545 | [29 empty] | U | 2545 |  | USV-2545
S-02115 | USV5-2547 | 243.7 | Limit Switch |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | UZSH-2547 | [30 empty] | U | 2547 |  | USV-2547
S-02115 | USV6-2547 | 243.7 | Limit Switch |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C |  | UZSL-2547 | [29 empty] | U | 2547 |  | USV-2547
S-02115 | USV5-2548 | 243.7 | Limit Switch |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | UZSH-2548 | [30 empty] | U | 2548 |  | USV-2548
S-02115 | USV6-2548 | 243.7 | Limit Switch |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C |  | UZSL-2548 | [29 empty] | U | 2548 |  | USV-2548
S-02115 | USV5-2549 | 243.7 | Limit Switch |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | UZSH-2549 | [30 empty] | U | 2549 |  | USV-2549
S-02115 | USV6-2549 | 243.7 | Limit Switch |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C |  | UZSL-2549 | [29 empty] | U | 2549 |  | USV-2549
S-02115 | USV7-3018 | 243.7 | Limit Switch |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C | UZSH-3018 | [30 empty] | U | 3018 |  | USV-3018
S-02115 | USV8-3018 | 243.7 | Limit Switch |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C |  | UZSL-3018 | [29 empty] | U | 3018 |  | USV-3018
S-02115 | USV7-3052 | 243.7 | Limit Switch |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | UZSH-3052 | [30 empty] | U | 3052 |  | USV-3052
S-02115 | USV8-3052 | 243.7 | Limit Switch |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C |  | UZSL-3052 | [29 empty] | U | 3052 |  | USV-3052
S-02115 | USV7-3172 | 243.7 | Limit Switch |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | UZSH-3172 | [30 empty] | U | 3172 |  | USV-3172
S-02115 | USV8-3172 | 243.7 | Limit Switch |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C |  | UZSL-3172 | [29 empty] | U | 3172 |  | USV-3172
S-02115 | UV7-5021 | 243.7 | Limit Switch |  | P29 |  | 24"-VA-50-140-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C | UZSH-5021 | [30 empty] | U | 5021 |  | UV-5021
S-02115 | UV8-5021 | 243.7 | Limit Switch |  | P29 |  | 24"-VA-50-140-B40-N |  |  | 3.5 | 0 | bar g |  | 45 | 100 | °C |  | UZSL-5021 | [29 empty] | U | 5021 |  | UV-5021
S-02115 | USV7-5302 | 243.7 | Limit Switch |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | UZSH-5302 | [30 empty] | U | 5302 |  | USV-5302
S-02115 | USV8-5302 | 243.7 | Limit Switch |  | P39 |  | 32"-LPS-70-105-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C |  | UZSL-5302 | [29 empty] | U | 5302 |  | USV-5302
S-02115 | USV7-5391 | 243.7 | Limit Switch |  | P43 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | UZSH-5391 | [30 empty] | U | 5391 |  | USV-5391
S-02115 | USV8-5391 | 243.7 | Limit Switch |  | P43 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C |  | UZSL-5391 | [29 empty] | U | 5391 |  | USV-5391
S-02115 | USV7-5392 | 243.7 | Limit Switch |  | P43 |  | 10"-PMP-50-144-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | UZSH-5392 | [30 empty] | U | 5392 |  | USV-5392
S-02115 | USV8-5392 | 243.7 | Limit Switch |  | P43 |  | 10"-PMP-50-144-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C |  | UZSL-5392 | [29 empty] | U | 5392 |  | USV-5392
S-02115 | USV7-5393 | 243.7 | Limit Switch |  | P43 |  | 3"-PMP-50-158-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | UZSH-5393 | [30 empty] | U | 5393 |  | USV-5393
S-02115 | USV8-5393 | 243.7 | Limit Switch |  | P43 |  | 3"-PMP-50-158-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C |  | UZSL-5393 | [29 empty] | U | 5393 |  | USV-5393
S-02115 | USV7-5420 | 243.7 | Limit Switch |  | P44 |  | 10"-PMP-50-152-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | UZSH-5420 | [30 empty] | U | 5420 |  | USV-5420
S-02115 | USV8-5420 | 243.7 | Limit Switch |  | P44 |  | 10"-PMP-50-152-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C |  | UZSL-5420 | [29 empty] | U | 5420 |  | USV-5420
S-02115 | USV7-5421 | 243.7 | Limit Switch |  | P44 |  | 3"-PMP-50-156-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | UZSH-5421 | [30 empty] | U | 5421 |  | USV-5421
S-02115 | USV8-5421 | 243.7 | Limit Switch |  | P44 |  | 3"-PMP-50-156-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C |  | UZSL-5421 | [29 empty] | U | 5421 |  | USV-5421
S-02115 | USV7-5422 | 243.7 | Limit Switch |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C | UZSH-5422 | [30 empty] | U | 5422 |  | USV-5422
S-02115 | USV8-5422 | 243.7 | Limit Switch |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 4.5 | 1 | bar g |  | 48 | 75 | °C |  | UZSL-5422 | [29 empty] | U | 5422 |  | USV-5422
S-02115 | UV7-6035 | 243.7 | Limit Switch |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | UZSH-6035 | [30 empty] | U | 6035 |  | UV-6035
S-02115 | UV8-6035 | 243.7 | Limit Switch |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C |  | UZSL-6035 | [29 empty] | U | 6035 |  | UV-6035
S-02115 | USV7-6081 | 243.7 | Limit Switch |  | P08 |  | 2"-BD-60-109-G40-P |  |  | 57 | 1 | bar g |  | 73 | 260 | °C | UZSH-6081 | [30 empty] | U | 6081 |  | USV-6081
S-02115 | USV8-6081 | 243.7 | Limit Switch |  | P08 |  | 2"-BD-60-109-G40-P |  |  | 57 | 1 | bar g |  | 73 | 260 | °C |  | UZSL-6081 | [29 empty] | U | 6081 |  | USV-6081
S-02115 | USV7-6082 | 243.7 | Limit Switch |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | UZSH-6082 | [30 empty] | U | 6082 |  | USV-6082
S-02115 | USV8-6082 | 243.7 | Limit Switch |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C |  | UZSL-6082 | [29 empty] | U | 6082 |  | USV-6082
S-02115 | USV7-7130 | 243.7 | Limit Switch |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | UZSH-7130 | [30 empty] | U | 7130 |  | USV-7130
S-02115 | USV8-7130 | 243.7 | Limit Switch |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | UZSL-7130 | [29 empty] | U | 7130 |  | USV-7130
S-02115 | USV7-7135 | 243.7 | Limit Switch |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | UZSH-7135 | [30 empty] | U | 7135 |  | USV-7135
S-02115 | USV8-7135 | 243.7 | Limit Switch |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C |  | UZSL-7135 | [29 empty] | U | 7135 |  | USV-7135
S-02115 | PV8-2073 | 243.8 | Position transmitter |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA | PZI-2073 | [29 empty] | P | 2073 |  | PV-2073
S-02115 | PV5-7002/A | 243.8 | Position transmitter |  | U03 |  | 10"-HHPS-70-115-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | PZT-7002/A | [29 empty] | P | 7002 | A | PV-7002/A
S-02115 | PV5-7002/B | 243.8 | Position transmitter |  | U03 |  | 24"-HHPS-70-114-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | PZT-7002/B | [29 empty] | P | 7002 | B | PV-7002/B
S-02115 | PV5-7002/C | 243.8 | Position transmitter |  | U03 |  | 24"-HHPS-70-113-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | FF AI | PZT-7002/C | [29 empty] | P | 7002 | C | PV-7002/C
S-02115 | FV9-3169 | 243.99 | Remark: |  | P27 |  | 6"-SG-30-138-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | F | 3169 |  | FV-3169
S-02115 | HV9-2097 | 243.99 | Remark: |  | P10 |  | 3"-HPS-20-112-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | Valve to be sized together | with vent silencer. | [29 empty] | H | 2097 |  | HV-2097
S-02115 | HV9-2334 | 243.99 | Remark: |  | P16B |  | 2"-BD-20-101-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Intermittent blow-down valve | Gestra type PA 110 or | equivalent. | Alloy steel body due to flash | [27 empty] | H | 2334 |  | HV-2334
S-02115 | HV9-2335 | 243.99 | Remark: |  | P16B |  | 2"-BD-20-139-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Intermittent blow-down valve | Gestra type PA 110 or | equivalent. | Alloy steel body due to flash | [27 empty] | H | 2335 |  | HV-2335
S-02115 | HV5-2371 | 243.99 | Remark: |  | P18 |  | 6"-BFW-20-109-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | Alloy steel body due to flash | [30 empty] | H | 2371 |  | HV-2371
S-02115 | HV9-2385 | 243.99 | Remark: |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | Continuous blow-down valve | Gestra Reaktomat or equivalent | Alloy steel body due to flash | [28 empty] | H | 2385 |  | HV-2385
S-02115 | HV9-3011 | 243.99 | Remark: |  | P22 |  | 2"-SG-30-131-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | H | 3011 |  | HV-3011
S-02115 | HV9-3054 | 243.99 | Remark: |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | Continuous blow-down valve | Gestra Reaktomat or equivalent | Alloy steel body due to flash | [28 empty] | H | 3054 |  | HV-3054
S-02115 | HV9-3087 | 243.99 | Remark: |  | P24 |  | 2"-CBD-30-107-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Intermittent blow-down valve | Gestra type PA 47 or | equivalent. | Alloy steel body due to flash | [27 empty] | H | 3087 |  | HV-3087
S-02115 | HV9-3090 | 243.99 | Remark: |  | P24 |  | 2"-CBD-30-105-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Intermittent blow-down valve | Gestra type PA 47 or | equivalent. | Alloy steel body due to flash | [27 empty] | H | 3090 |  | HV-3090
S-02115 | HV9-3093 | 243.99 | Remark: |  | P24 |  | 2"-CBD-30-103-F24-P |  |  | 48 | 33.7 | bar g |  | 242 | 265 | °C | Intermittent blow-down valve | Gestra type PA 47 or | equivalent. | Alloy steel body due to flash | [27 empty] | H | 3093 |  | HV-3093
S-02115 | HV9-3166 | 243.99 | Remark: |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | H | 3166 |  | HV-3166
S-02115 | LV5-2016 | 243.99 | Remark: |  | P02 |  | 6"-HPC-20-102-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | Alloy steel body due to flash | [30 empty] | L | 2016 |  | LV-2016
S-02115 | LV9-3161/A | 243.99 | Remark: |  | P27 |  | 10"-PMC-30-101-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | For lower flow than normal the | downstream pressure approaches | 4 bar g due to less d/p across | downstream restriction orifice | FO-3191 | [26 empty] | L | 3161 | A | LV-3161/A
S-02115 | LV9-3161/B | 243.99 | Remark: |  | P27 |  | 10"-PMC-30-103-G40-N |  |  | 100 | 76.2 | bar g |  | 48 | 100 | °C | For lower flow than normal the | downstream pressure approaches | 4 bar g due to less d/p across | downstream restriction orifice | FO-3191 | [26 empty] | L | 3161 | B | LV-3161/B
S-02115 | LV7-5070 | 243.99 | Remark: |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | Alloy steel body due to flash | [30 empty] | L | 5070 |  | LV-5070
S-02115 | LV9-6021/B | 243.99 | Remark: |  | P05 |  | 18"-MPC-60-104-F24-H |  |  | 47 | 32.5 | bar g |  | 240 | 260 | °C | Valve size and trim type by | vendor. | [29 empty] | L | 6021 | B | LV-6021/B
S-02115 | LV5-7251 | 243.99 | Remark: |  | U16 |  | 3"-BD-70-111-B24-N |  |  | 10.5 | 8 | bar g |  | 173 | 200 | °C | Alloy steel body due to flash | [30 empty] | L | 7251 |  | LV-7251
S-02115 | PV9-1045 | 243.99 | Remark: |  | P04 |  | 8"-PRG-10-108-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | P | 1045 |  | PV-1045
S-02115 | PV9-2073 | 243.99 | Remark: |  | P09 |  | 12"-PRG-20-111-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | P | 2073 |  | PV-2073
S-02115 | PV9-2361 | 243.99 | Remark: |  | P17 |  | 8"-HHPS-20-2054-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | Valve to be sized and supplied | together with vent silencer. | [26 empty] | P | 2361 |  | PV-2361
S-02115 | PV9-2406 | 243.99 | Remark: |  | P19 |  | 18"-RFG-20-118-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | P | 2406 |  | PV-2406
S-02115 | PV9-2481 | 243.99 | Remark: |  | P21 |  | 18"-SG-20-105-D40-ET |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | P | 2481 |  | PV-2481
S-02115 | PV5-2536 | 243.99 | Remark: |  | U01 |  | 14"-PG-20-129-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | Vendor to specify additional | devices for noise reduction | if required | [28 empty] | P | 2536 |  | PV-2536
S-02115 | PV9-3166 | 243.99 | Remark: |  | P27 |  | 4"-SG-30-141-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Vendor to specify the size of | valve and additional devices | for noise reduction. | [28 empty] | P | 3166 |  | PV-3166
S-02115 | PV5-7004 | 243.99 | Remark: |  | U03 |  | 16"-HPS-70-108-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | Valve to be sized and supplied | together with silencer. | [29 empty] | P | 7004 |  | PV-7004
S-02115 | PV5-7031/C | 243.99 | Remark: |  | U05 |  | 10"-MPS-70-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Vendor to specify additional | devices for noise reduction | if required | [28 empty] | P | 7031 | C | PV-7031/C
S-02115 | PV5-7031/D | 243.99 | Remark: |  | U05 |  | 10"-MPS-70-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Vendor to specify additional | devices for noise reduction | if required | [28 empty] | P | 7031 | D | PV-7031/D
S-02115 | PV5-7034 | 243.99 | Remark: |  | U05 |  | 14"-MPS-70-121-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Valve to be sized and supplied | together with silencer. | [29 empty] | P | 7034 |  | PV-7034
S-02115 | PV5-7056 | 243.99 | Remark: |  | U06 |  | 24"-LPS-70-109-D24-P |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Valve to be sized and supplied | together with silencer. | [29 empty] | P | 7056 |  | PV-7056
S-02115 | PV5-7094 | 243.99 | Remark: |  | U09 |  | 18"-LPS-70-127-D24-H |  |  | 9.5 | 7 | bar g |  | 188 | 340 | °C | Vendor to specify additional | devices for noise reduction | if required | [28 empty] | P | 7094 |  | PV-7094
S-02115 | PV5-7101 | 243.99 | Remark: |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | Vendor to specify additional | devices for noise reduction | if required | [28 empty] | P | 7101 |  | PV-7101
S-02115 | TV5-7003 | 243.99 | Remark: |  | U03 |  | 3"-BFW-70-143-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Alloy steel body due to high | liquid velocity | [29 empty] | T | 7003 |  | TV-7003
S-02115 | TV5-7004 | 243.99 | Remark: |  | U03 |  | 3"-BFW-70-141-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | Alloy steel body due to high | liquid velocity | [29 empty] | T | 7004 |  | TV-7004
S-02115 | TV5-7032 | 243.99 | Remark: |  | U05 |  | 2"-BFW-70-115-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Alloy steel body due to high | liquid velocity | [29 empty] | T | 7032 |  | TV-7032
S-02115 | TV5-7033 | 243.99 | Remark: |  | U05 |  | 2"-BFW-70-108-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Alloy steel body due to high | liquid velocity | [29 empty] | T | 7033 |  | TV-7033
S-02115 | USV7-2541 | 243.99 | Remark: |  | U01 |  | 28"-FG-20-126-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | To be fire safe type | [30 empty] | U | 2541 |  | USV-2541
S-02115 | USV7-2542 | 243.99 | Remark: |  | U01 |  | 28"-FG-20-127-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | To be fire safe type | [30 empty] | U | 2542 |  | USV-2542
S-02115 | USV7-2543 | 243.99 | Remark: |  | U01 |  | 2"-FG-20-131-B24-N |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | To be fire safe type | [30 empty] | U | 2543 |  | USV-2543
S-02115 | USV7-2544 | 243.99 | Remark: |  | U01 |  | 24"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | To be fire safe type | [30 empty] | U | 2544 |  | USV-2544
S-02115 | USV7-2545 | 243.99 | Remark: |  | U01 |  | 2"-PG-20-125-B24-N |  |  | 7 | 2 | bar g |  | 47 | 100 | °C | To be fire safe type | [30 empty] | U | 2545 |  | USV-2545
S-02115 | USV7-2547 | 243.99 | Remark: |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | To be fire safe type | [30 empty] | U | 2547 |  | USV-2547
S-02115 | USV7-2548 | 243.99 | Remark: |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | To be fire safe type | [30 empty] | U | 2548 |  | USV-2548
S-02115 | USV7-2549 | 243.99 | Remark: |  | U01 |  | 1 1/2"-FG-20-106-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | To be fire safe type | [30 empty] | U | 2549 |  | USV-2549
S-02115 | SC-2119 | 248.01 | Speed Controller |  | P11 | [10 empty] | °C | By Vendor | [30 empty] | S | 2119 |  | SIC-2119
S-02115 | SC-2167 | 248.01 | Speed Controller |  | P12 | [10 empty] | °C | By Vendor | [30 empty] | S | 2167 |  | SIC-2167
S-02115 | SC-7131 | 248.01 | Speed Controller |  | U10 | [10 empty] | °C | By Vendor | [30 empty] | S | 7131 |  | SC-7131
S-02115 | SC-7136 | 248.01 | Speed Controller |  | U10 | [10 empty] | °C | By Vendor | [30 empty] | S | 7136 |  | SC-7136
S-02115 | SC-7193 | 248.01 | Speed Controller |  | U13 | [10 empty] | °C | By Vendor | [30 empty] | S | 7193 |  | SC-7193
S-02115 | SC-7196 | 248.01 | Speed Controller |  | U13 | [10 empty] | °C | By Vendor | [30 empty] | S | 7196 |  | SC-7196
S-02115 | FI-3010 | 256 | Rotameter, SS tube |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 10 | bar g |  | 48 | 100 | °C | 250-2500 Nm3/h |  | 867 Nm3/h |  | 2200 Nm3/h |  | Gas | 10 bar g | 48 °C | 4.57 kg/m3 | 0.016 cP | 1.01 | 1.39 | 11.14 | AISI 316 | By vendor, Class 300, RF | HV-3010 | [14 empty] | F | 3010 |  | FI-3010
S-02115 | FI-3013 | 256 | Rotameter, SS tube |  | P22 |  | 3"-HG-30-101-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 190-1900 Nm3/h |  | 633 Nm3/h |  | 1600 Nm3/h |  | Gas | 25 bar g | 40 °C | 1.99 kg/m3 | 0.009 cP | 1.01 | 1.4 | 2.02 kg/kmol | AISI 316 | By vendor, Class 300, RF | HV-3013 | [14 empty] | F | 3013 |  | FI-3013
S-02115 | FI-3016 | 256 | Rotameter, SS tube |  | P22 |  | 3"-PA-30-101-B24-N |  |  | 10.5 | 7.5 | bar g |  | 35 | 75 | °C | 900-9000 Nm3/h |  | 3000 Nm3/h |  | 8000 Nm3/h |  | Gas | 7.5 bar g | 35 °C | 9.63 kg/m3 | 0.019 cP | 1 | 1.41 | 28.89 kg/kmol | AISI 316 | By vendor, Class 150, RF | HV-3016 | [14 empty] | F | 3016 |  | FI-3016
S-02115 | FI-5021 | 256 | Rotameter, SS tube |  | P29 |  | 2"-N-50-101-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 330-3300 Nm3/h | [5 empty] | Gas | 6 bar g | 75 °C |  |  | 1 | 1.41 | 28.01 | AISI 316 | By vendor, Class 150, RF | [15 empty] | F | 5021 |  | FI-5021
S-02115 | FI-5408 | 256 | Rotameter, SS tube |  | P43 |  | 2"-N-50-113-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 180-1800 Nm3/h | [5 empty] | Gas | 6 bar g | 75 °C |  |  | 1 | 1.41 | 28.01 | AISI 316 | By vendor, Class 150, RF | [15 empty] | F | 5408 |  | FI-5408
S-02115 | FI-5422 | 256 | Rotameter, SS tube |  |  |  | 2"-N-50-108-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 180-1800 Nm3/h | [5 empty] | Gas | 6 bar g | 75 °C |  |  | 1 | 1.41 | 28.01 | AISI 316 | By vendor, Class 150, RF | [15 empty] | F | 5422 |  | FI-5422
S-02115 | FI-5442 | 256 | Rotameter, SS tube |  | P45 |  | 2"-N-50-111-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 2.5-25 Nm3/h | [5 empty] | Gas | 6 bar g | 75 °C |  |  | 1 | 1.41 | 28.01 | AISI 316 | By vendor, Class 150, RF | [15 empty] | F | 5442 |  | FI-5442
S-02115 | LG-1005 | 259 | Level Gauge |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 36.8 kg/m3 | 995 kg/m3 | [23 empty] | L | 1005 |  | LG-1005
S-02115 | LG-2017 | 259 | Level Gauge |  | P02 |  | D 2011 |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  |  | 789 kg/m3 | [23 empty] | L | 2017 |  | LG-2017
S-02115 | LG/LI-2373 | 259 | Level Gauge |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Hydrastep | By Steam Drum Vendor | By Steam Drum Vendor |  | By Steam Drum Vendor | Local indicator/4-20 mA output | 57.5 kg/m3 | 683 kg/m3 | [23 empty] | L | 2373 |  | LI-2373
S-02115 | LG-2374 | 259 | Level Gauge |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Transparent, Bi-color | By Steam Drum Vendor | By Steam Drum Vendor |  | CS | Mica shield, Illuminator | 57.5 kg/m3 | 683 kg/m3 | [23 empty] | L | 2374 |  | LG-2374
S-02115 | LG-2405 | 259 | Level Gauge |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 9.78 kg/m3 | 903 kg/m3 | [23 empty] | L | 2405 |  | LG-2405
S-02115 | LG-2420 | 259 | Level Gauge |  | P19 |  | D 2003 |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 9.54 kg/m3 | 909 kg/m3 | [23 empty] | L | 2420 |  | LG-2420
S-02115 | LG-2443 | 259 | Level Gauge |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 9.39 kg/m3 | 929 kg/m3 | [23 empty] | L | 2443 |  | LG-2443
S-02115 | LG-2475 | 259 | Level Gauge |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 10.7 kg/m3 | 989 kg/m3 | [23 empty] | L | 2475 |  | LG-2475
S-02115 | LG/LI-3043 | 259 | Level Gauge |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Hydrastep | By Steam Drum Vendor | By Steam Drum Vendor |  | By Steam Drum Vendor | Local indicator/4-20 mA output | 17.4 kg/m3 | 811 kg/m3 | [23 empty] | L | 3043 |  | LI-3043
S-02115 | LG-3044 | 259 | Level Gauge |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Transparent, Bi-color | By Steam Drum Vendor | By Steam Drum Vendor |  | CS | Mica shield, Illuminator | 17.4 kg/m3 | 811 kg/m3 | [23 empty] | L | 3044 |  | LG-3044
S-02115 | LG-3162 | 259 | Level Gauge |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 35.1 kg/m3 | 757 kg/m3 | [23 empty] | L | 3162 |  | LG-3162
S-02115 | LG-3193 | 259 | Level Gauge |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 5.69 kg/m3 | 781 kg/m3 | [23 empty] | L | 3193 |  | LG-3193
S-02115 | LG-5038 | 259 | Level Gauge |  | P30 |  | E 2024 1 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.17 kg/m3 | 748 kg/m3 | [23 empty] | L | 5038 |  | LG-5038
S-02115 | LG-5043 | 259 | Level Gauge |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.96 kg/m3 | 753 kg/m3 | [23 empty] | L | 5043 |  | LG-5043
S-02115 | LG-5061 | 259 | Level Gauge |  | P31 |  | E 5001 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.17 kg/m3 | 748 kg/m3 | [23 empty] | L | 5061 |  | LG-5061
S-02115 | LG-5066 | 259 | Level Gauge |  | P30 |  | E 2024 2 |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.17 kg/m3 | 748 kg/m3 | [23 empty] | L | 5066 |  | LG-5066
S-02115 | LG-5072 | 259 | Level Gauge |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  |  | 928 kg/m3 | [23 empty] | L | 5072 |  | LG-5072
S-02115 | LG-5095 | 259 | Level Gauge |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.26 kg/m3 | 752 kg/m3 | [23 empty] | L | 5095 |  | LG-5095
S-02115 | LG-5163 | 259 | Level Gauge |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.29 kg/m3 | 750 kg/m3 | [23 empty] | L | 5163 |  | LG-5163
S-02115 | LG-5183 | 259 | Level Gauge |  | P34 |  | E 5002 4 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.73 kg/m3 | 786 kg/m3 | [23 empty] | L | 5183 |  | LG-5183
S-02115 | LG-5191 | 259 | Level Gauge |  | P35 |  | E 5002 1 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.73 kg/m3 | 786 kg/m3 | [23 empty] | L | 5191 |  | LG-5191
S-02115 | LG-5192 | 259 | Level Gauge |  | P35 |  | E 5002 2 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.73 kg/m3 | 786 kg/m3 | [23 empty] | L | 5192 |  | LG-5192
S-02115 | LG-5193 | 259 | Level Gauge |  | P35 |  | E 5002 3 |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.73 kg/m3 | 786 kg/m3 | [23 empty] | L | 5193 |  | LG-5193
S-02115 | LG-5205 | 259 | Level Gauge |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  |  | 750 kg/m3 | [23 empty] | L | 5205 |  | LG-5205
S-02115 | LG/LI-5232 | 259 | Level Gauge |  | U15 |  | TK 5080 |  |  |  |  | bar g |  |  |  | °C | Magnetic | By vendor | By vendor |  | AISI 316 | Magnetostrictive level transm. |  | By vendor kg/m3 | [23 empty] | L | 5232 |  | LI-5232
S-02115 | LG-5272 | 259 | Level Gauge |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 4.07 kg/m3 | 918 kg/m3 | [23 empty] | L | 5272 |  | LG-5272
S-02115 | LG-5279 | 259 | Level Gauge |  | P38 |  | E 2023 |  |  | 7.5 | 3.6 | bar g |  | 149 | 175 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.42 kg/m3 | 918 kg/m3 | [23 empty] | L | 5279 |  | LG-5279
S-02115 | LG-5309 | 259 | Level Gauge |  | P39 |  | E 5003 1 Shell |  |  | 7.5 | 3.6 |  |  | 149 | 175 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.42 kg/m3 | 918 kg/m3 | [23 empty] | L | 5309 |  | LG-5309
S-02115 | LG-5311 | 259 | Level Gauge |  | P39 |  | E 5003 2 Shell |  |  | 7.5 | 3.6 |  |  | 149 | 175 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 2.42 kg/m3 | 918 kg/m3 | [23 empty] | L | 5311 |  | LG-5311
S-02115 | LG-5323 | 259 | Level Gauge |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  |  | 711 kg/m3 | [23 empty] | L | 5323 |  | LG-5323
S-02115 | LG-5502 | 259 | Level Gauge |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  |  | 991 kg/m3 | [23 empty] | L | 5502 |  | LG-5502
S-02115 | LG/LI-5511 | 259 | Level Gauge |  | U24 |  | TK 5050 | [8 empty] | °C | Magnetic | By vendor | By vendor |  | AISI 316 | Magnetostrictive level transm. |  | By vendor kg/m3 | [23 empty] | L | 5511 |  | LI-5511
S-02115 | LG-6023/1 | 259 | Level Gauge |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 20 kg/m3 | 834 kg/m3 | [23 empty] | L | 6023 | 1 | LG-6023/1
S-02115 | LG-6023/2 | 259 | Level Gauge |  | P06 |  | T 6001 2 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 20 kg/m3 | 834 kg/m3 | [23 empty] | L | 6023 | 2 | LG-6023/2
S-02115 | LG/LI-6033/1 | 259 | Level Gauge |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 | Magnetostrictive level transm. | 20.9 kg/m3 | 900 kg/m3 | [23 empty] | L | 6033 | 1 | LI-6033/1
S-02115 | LG/LI-6033/2 | 259 | Level Gauge |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 | Magnetostrictive level transm. | 20.9 kg/m3 | 900 kg/m3 | [23 empty] | L | 6033 | 2 | LI-6033/2
S-02115 | LG/LI-6034/1 | 259 | Level Gauge |  | P06 |  | T 6001 1 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 | Magnetostrictive level transm. | 20.9 kg/m3 | 900 kg/m3 | [23 empty] | L | 6034 | 1 | LI-6034/1
S-02115 | LG/LI-6034/2 | 259 | Level Gauge |  | P06 |  | T 6001 2 Top |  |  | 45 | 42.8 | bar g |  | 168 | 300 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 | Magnetostrictive level transm. | 20.9 kg/m3 | 900 kg/m3 | [23 empty] | L | 6034 | 2 | LI-6034/2
S-02115 | LG-6052 | 259 | Level Gauge |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 22.6 kg/m3 | 827 kg/m3 | [23 empty] | L | 6052 |  | LG-6052
S-02115 | LG-6084 | 259 | Level Gauge |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 0.6 kg/m3 | 958 kg/m3 | [23 empty] | L | 6084 |  | LG-6084
S-02115 | LG-7092 | 259 | Level Gauge |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 1.14 kg/m3 | 943 kg/m3 | [23 empty] | L | 7092 |  | LG-7092
S-02115 | LG/LI-7162 | 259 | Level Gauge |  | U12 |  | TK 7050 |  |  |  |  | bar g |  |  |  | °C | Magnetic | By vendor | By vendor |  | AISI 316 | Magnetostrictive level transm. |  | By vendor kg/m3 | [23 empty] | L | 7162 |  | LI-7162
S-02115 | LG/LI-7192 | 259 | Level Gauge |  | U13 |  | TK 7060 |  |  |  |  | bar g |  |  |  | °C | Magnetic | By vendor | By vendor |  | AISI 316 | Magnetostrictive level transm. |  | By vendor kg/m3 | [23 empty] | L | 7192 |  | LI-7192
S-02115 | LG/LI-7212 | 259 | Level Gauge |  | U14 |  | TK 7070 |  |  |  |  | bar g |  |  |  | °C | Magnetic | By vendor | By vendor |  | AISI 316 | Magnetostrictive level transm. |  | By vendor kg/m3 | [23 empty] | L | 7212 |  | LI-7212
S-02115 | LG-7252 | 259 | Level Gauge |  | U16 |  | D 7002 |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 4.42 kg/m3 | 894 kg/m3 | [23 empty] | L | 7252 |  | LG-7252
S-02115 | LG-7255 | 259 | Level Gauge |  | U16 |  | D 7003 |  |  |  | 102 | bar g |  | 313 |  | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 0.598 kg/m3 | 958 kg/m3 | [23 empty] | L | 7255 |  | LG-7255
S-02115 | LG-7257 | 259 | Level Gauge |  | U16 |  | D 7004 |  |  |  | 40.8 | bar g |  | 253 |  | °C | Magnetic | By Detail Engineer | By Detail Engineer |  | AISI 316 |  | 0.598 kg/m3 | 958 kg/m3 | [23 empty] | L | 7257 |  | LG-7257
S-02115 | PG-1002 | 260 | Pressure Gauge |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 1002 |  | PG-1002
S-02115 | PG-1007 | 260 | Pressure Gauge |  | P01 |  | 14"-NG-10-103-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 1007 |  | PG-1007
S-02115 | PG-1033 | 260 | Pressure Gauge |  | P04 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 1033 |  | PG-1033
S-02115 | PG-1036 | 260 | Pressure Gauge |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 1036 |  | PG-1036
S-02115 | PG-1040 | 260 | Pressure Gauge |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 1040 |  | PG-1040
S-02115 | PG-1046 | 260 | Pressure Gauge |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 1046 |  | PG-1046
S-02115 | PG-1048 | 260 | Pressure Gauge |  | P04 |  | 1½"-N-10-103-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 70 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 1048 |  | PG-1048
S-02115 | PG-2002 | 260 | Pressure Gauge |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2002 |  | PG-2002
S-02115 | PG-2005 | 260 | Pressure Gauge |  | P02 |  | 10"-PO-20-107-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2005 |  | PG-2005
S-02115 | PG-2006 | 260 | Pressure Gauge |  | P02 |  | 10"-PO-20-107-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2006 |  | PG-2006
S-02115 | PG-2018 | 260 | Pressure Gauge |  | P02 |  | 2"-HPC-20-104-F24-P |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2018 |  | PG-2018
S-02115 | PG-2031 | 260 | Pressure Gauge |  | P03 |  | 4"-HPS-70-103-F34-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2031 |  | PG-2031
S-02115 | PG-2033 | 260 | Pressure Gauge |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 2033 |  | PG-2033
S-02115 | PG-2034 | 260 | Pressure Gauge |  | P03 |  | 4"-HPS-20-107-F44-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 2034 |  | PG-2034
S-02115 | PG-2075 | 260 | Pressure Gauge |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 2075 |  | PG-2075
S-02115 | PG-2096 | 260 | Pressure Gauge |  | P10 |  | 12"-HPS-20-104-F24-H |  |  | 52 | 42.1 | bar g |  | 343 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 2096 |  | PG-2096
S-02115 | PG-2100 | 260 | Pressure Gauge |  | P10 |  | 4"-N-20-112-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 2100 |  | PG-2100
S-02115 | PG-2101 | 260 | Pressure Gauge |  | P10 |  | 4"-N-20-113-F24-N |  |  | 46 | 6 | bar g |  | 40 | 290 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2101 |  | PG-2101
S-02115 | PG-2116 | 260 | Pressure Gauge |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 2116 |  | PG-2116
S-02115 | PG-2120 | 260 | Pressure Gauge |  | P11 |  | 16"-LPS-20-102-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 0-16 bar g | Bourdon |  | Yes | [27 empty] | P | 2120 |  | PG-2120
S-02115 | PG-2164 | 260 | Pressure Gauge |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 2164 |  | PG-2164
S-02115 | PG-2170 | 260 | Pressure Gauge |  | P12 |  | 12"-LPS-20-106-D24-H |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 0-16 bar g | Bourdon |  | Yes | [27 empty] | P | 2170 |  | PG-2170
S-02115 | PG-2230 | 260 | Pressure Gauge |  | P13 |  | 3"-PRC-20-130-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2230 |  | PG-2230
S-02115 | PG-2231 | 260 | Pressure Gauge |  | P13 |  | 3"-BFW-70-103-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2231 |  | PG-2231
S-02115 | PG-2251 | 260 | Pressure Gauge |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2251 |  | PG-2251
S-02115 | PG-2267 | 260 | Pressure Gauge |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2267 |  | PG-2267
S-02115 | PG-2281 | 260 | Pressure Gauge |  | P15 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2281 |  | PG-2281
S-02115 | PG-2286/1 | 260 | Pressure Gauge |  | P15 |  | 4"-FG-20-115-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2286 | 1 | PG-2286/1
S-02115 | PG-2286/2 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-116-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2286 | 2 | PG-2286/2
S-02115 | PG-2286/3 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-117-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2286 | 3 | PG-2286/3
S-02115 | PG-2286/4 | 260 | Pressure Gauge |  | P15 |  | 6"-FG-20-118-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2286 | 4 | PG-2286/4
S-02115 | PG-2287/1 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2287 | 1 | PG-2287/1
S-02115 | PG-2287/2 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2287 | 2 | PG-2287/2
S-02115 | PG-2287/3 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2287 | 3 | PG-2287/3
S-02115 | PG-2287/4 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2287 | 4 | PG-2287/4
S-02115 | PG-2288/1 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2288 | 1 | PG-2288/1
S-02115 | PG-2288/2 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2288 | 2 | PG-2288/2
S-02115 | PG-2288/3 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2288 | 3 | PG-2288/3
S-02115 | PG-2288/4 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2288 | 4 | PG-2288/4
S-02115 | PG-2289/1 | 260 | Pressure Gauge |  | P15 |  | 4"-FG-20-107-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2289 | 1 | PG-2289/1
S-02115 | PG-2289/2 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-108-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2289 | 2 | PG-2289/2
S-02115 | PG-2289/3 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-109-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2289 | 3 | PG-2289/3
S-02115 | PG-2289/4 | 260 | Pressure Gauge |  | P15 |  | 6"-FG-20-110-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2289 | 4 | PG-2289/4
S-02115 | PG-2290/1 | 260 | Pressure Gauge |  | P15 |  | 4"-FG-20-111-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2290 | 1 | PG-2290/1
S-02115 | PG-2290/2 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-112-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2290 | 2 | PG-2290/2
S-02115 | PG-2290/3 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-113-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2290 | 3 | PG-2290/3
S-02115 | PG-2290/4 | 260 | Pressure Gauge |  | P15 |  | 6"-FG-20-114-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2290 | 4 | PG-2290/4
S-02115 | PG-2291/1 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2291 | 1 | PG-2291/1
S-02115 | PG-2291/2 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2291 | 2 | PG-2291/2
S-02115 | PG-2291/3 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2291 | 3 | PG-2291/3
S-02115 | PG-2291/4 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2291 | 4 | PG-2291/4
S-02115 | PG-2292/1 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2292 | 1 | PG-2292/1
S-02115 | PG-2292/2 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2292 | 2 | PG-2292/2
S-02115 | PG-2292/3 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2292 | 3 | PG-2292/3
S-02115 | PG-2292/4 | 260 | Pressure Gauge |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 0-40 mbar g | Capsule |  |  | Yes | [26 empty] | P | 2292 | 4 | PG-2292/4
S-02115 | PG-2293/1 | 260 | Pressure Gauge |  | P15 |  | 4"-FG-20-120-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2293 | 1 | PG-2293/1
S-02115 | PG-2293/2 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-121-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2293 | 2 | PG-2293/2
S-02115 | PG-2293/3 | 260 | Pressure Gauge |  | P15 |  | 8"-FG-20-122-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2293 | 3 | PG-2293/3
S-02115 | PG-2293/4 | 260 | Pressure Gauge |  | P15 |  | 6"-FG-20-123-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 2293 | 4 | PG-2293/4
S-02115 | PG-2294 | 260 | Pressure Gauge |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | -6 - +4 mbar g | Capsule | [29 empty] | P | 2294 |  | PG-2294
S-02115 | PG-2296 | 260 | Pressure Gauge |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | -6 - +4 mbar g | Capsule | [29 empty] | P | 2296 |  | PG-2296
S-02115 | PG-2362 | 260 | Pressure Gauge |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 0-160 bar g | Bourdon |  | Yes | [27 empty] | P | 2362 |  | PG-2362
S-02115 | PG-2364 | 260 | Pressure Gauge |  | P17 |  | 24"-HHPS-20-112-H34-H |  |  | 112 | 98 | bar g |  | 454 | 490 | °C | 0-160 bar g | Bourdon |  | Yes | [27 empty] | P | 2364 |  | PG-2364
S-02115 | PG-2375 | 260 | Pressure Gauge |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 0-160 bar g | Bourdon |  | Yes | [27 empty] | P | 2375 |  | PG-2375
S-02115 | PG-2408 | 260 | Pressure Gauge |  | P19 |  | 4"-PRC-20-116-G40-H |  |  | 71 | 27 | bar g |  | 165 | 200 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2408 |  | PG-2408
S-02115 | PG-2411 | 260 | Pressure Gauge |  | P19 |  | 3"-PRC-20-114-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2411 |  | PG-2411
S-02115 | PG-2412 | 260 | Pressure Gauge |  | P19 |  | 4"-PRC-20-115-G40-H |  |  | 71 | 27 | bar g |  | 165 | 200 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2412 |  | PG-2412
S-02115 | PG-2415 | 260 | Pressure Gauge |  | P19 |  | 3"-PRC-20-110-G40-H |  |  | 71 | 55 | bar g |  | 165 | 200 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2415 |  | PG-2415
S-02115 | PG-2445 | 260 | Pressure Gauge |  | P20 |  | 8"-PRC-20-121-G40-H |  |  | 71 | 26 | bar g |  | 138 | 200 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2445 |  | PG-2445
S-02115 | PG-2448 | 260 | Pressure Gauge |  | P20 |  | 6"-PRC-20-118-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2448 |  | PG-2448
S-02115 | PG-2449 | 260 | Pressure Gauge |  | P20 |  | 8"-PRC-20-120-G40-H |  |  | 71 | 26 | bar g |  | 138 | 200 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2449 |  | PG-2449
S-02115 | PG-2452 | 260 | Pressure Gauge |  | P20 |  | 6"-PRC-20-126-G40-H |  |  | 71 | 53 | bar g |  | 138 | 200 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2452 |  | PG-2452
S-02115 | PG-2454 | 260 | Pressure Gauge |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 2454 |  | PG-2454
S-02115 | PG-2485 | 260 | Pressure Gauge |  | P21 |  | 6"-PRC-20-127-G40-N |  |  | 80 | 25 | bar g |  | 48 | 100 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2485 |  | PG-2485
S-02115 | PG-2488 | 260 | Pressure Gauge |  | P21 |  | 4"-PRC-20-104-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2488 |  | PG-2488
S-02115 | PG-2489 | 260 | Pressure Gauge |  | P21 |  | 6"-PRC-20-128-G40-N |  |  | 80 | 25 | bar g |  | 48 | 100 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2489 |  | PG-2489
S-02115 | PG-2492 | 260 | Pressure Gauge |  | P21 |  | 4"-PRC-20-129-G40-N |  |  | 80 | 53 | bar g |  | 49 | 100 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2492 |  | PG-2492
S-02115 | PG-2539 | 260 | Pressure Gauge |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 2539 |  | PG-2539
S-02115 | PG-2552 | 260 | Pressure Gauge |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 3 | bar g |  | 35 | 85 | °C | 0-6 bar g | Bourdon | [29 empty] | P | 2552 |  | PG-2552
S-02115 | PG-2573 | 260 | Pressure Gauge |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 2573 |  | PG-2573
S-02115 | PG-2578 | 260 | Pressure Gauge |  | U02 |  | 3"-N-20-115-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 2578 |  | PG-2578
S-02115 | PG-2580 | 260 | Pressure Gauge |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 2580 |  | PG-2580
S-02115 | PG-2602 | 260 | Pressure Gauge |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 2602 |  | PG-2602
S-02115 | PG-2606 | 260 | Pressure Gauge |  | U17 |  | 3"-HG-20-103-F24-N |  |  | 55 | 50.4 | bar g |  | 48 | 200 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 2606 |  | PG-2606
S-02115 | PG-3006 | 260 | Pressure Gauge |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 3006 |  | PG-3006
S-02115 | PG-3009 | 260 | Pressure Gauge |  | P22 |  | 3"-SG-30-129-D40-N |  |  | 29 | 10 | bar g |  | 48 | 100 | °C | 0-16 bar g | Bourdon |  |  | Yes | [26 empty] | P | 3009 |  | PG-3009
S-02115 | PG-3011 | 260 | Pressure Gauge |  | P22 |  | 3"-HG-30-101-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 3011 |  | PG-3011
S-02115 | PG-3012 | 260 | Pressure Gauge |  | P22 |  | 3"-HG-30-101-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 0-60 bar g | Bourdon | [29 empty] | P | 3012 |  | PG-3012
S-02115 | PG-3014 | 260 | Pressure Gauge |  | P22 |  | 3"-PA-30-101-B24-N |  |  | 10.5 | 7.5 | bar g |  | 35 | 75 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 3014 |  | PG-3014
S-02115 | PG-3015 | 260 | Pressure Gauge |  | P22 |  | 3"-PA-30-101-B24-N |  |  | 10.5 | 7.5 | bar g |  | 35 | 75 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 3015 |  | PG-3015
S-02115 | PG-3017 | 260 | Pressure Gauge |  | P22 |  | 3"-SG-30-150-D24-N |  |  | 29 | 6 | bar g |  | 48 | 100 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 3017 |  | PG-3017
S-02115 | PG-3046 | 260 | Pressure Gauge |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 0-60 bar g | Bourdon |  | Yes | [27 empty] | P | 3046 |  | PG-3046
S-02115 | PG-3056 | 260 | Pressure Gauge |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 0-60 bar g | Bourdon |  | Yes | [27 empty] | P | 3056 |  | PG-3056
S-02115 | PG-3083 | 260 | Pressure Gauge |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-60 bar g | Bourdon |  | Yes | [27 empty] | P | 3083 |  | PG-3083
S-02115 | PG-3165 | 260 | Pressure Gauge |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 0-160 bar g | Bourdon | [29 empty] | P | 3165 |  | PG-3165
S-02115 | PG-3191 | 260 | Pressure Gauge |  | P28 |  | 12"-PMC-30-105-G40-N |  |  | 100 | 32 | bar g |  | 47 | 100 | °C | 0-60 bar g | Bourdon |  |  | Yes | [26 empty] | P | 3191 |  | PG-3191
S-02115 | PG-3195 | 260 | Pressure Gauge |  | P28 |  | D 3002 Top |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 3195 |  | PG-3195
S-02115 | PG-5005 | 260 | Pressure Gauge |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | -15 - +25 mbar g | Capsule | [29 empty] | P | 5005 |  | PG-5005
S-02115 | PG-5011 | 260 | Pressure Gauge |  | P29 |  | 16"-PMC-50-101-B40-N |  |  | 13 | 1 | bar g |  | 47 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5011 |  | PG-5011
S-02115 | PG-5014 | 260 | Pressure Gauge |  | P29 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5014 |  | PG-5014
S-02115 | PG-5015 | 260 | Pressure Gauge |  | P29 |  | 16"-PMC-50-102-B40-N |  |  | 13 | 1 | bar g |  | 47 | 100 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5015 |  | PG-5015
S-02115 | PG-5018 | 260 | Pressure Gauge |  | P29 |  | 10"-PMC-50-104-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5018 |  | PG-5018
S-02115 | PG-5046 | 260 | Pressure Gauge |  | P30 |  | 2"N-50-103-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 70 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5046 |  | PG-5046
S-02115 | PG-5075 | 260 | Pressure Gauge |  | P31 |  | 8"-LPC-50-110-D24-H |  |  | 18 | 2.4 | bar g |  | 138 | 190 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5075 |  | PG-5075
S-02115 | PG-5078 | 260 | Pressure Gauge |  | P31 |  | 4"-LPC-50-108-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5078 |  | PG-5078
S-02115 | PG-5079 | 260 | Pressure Gauge |  | P31 |  | 8"-LPC-50-104-D24-H |  |  | 18 | 2.4 | bar g |  | 168 | 190 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5079 |  | PG-5079
S-02115 | PG-5082 | 260 | Pressure Gauge |  | P31 |  | 4"-LPC-50-107-D24-H |  |  | 18 | 5.7 | bar g |  | 138 | 190 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5082 |  | PG-5082
S-02115 | PG-5096 | 260 | Pressure Gauge |  | P32 |  | D 5001 |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | 0-1.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5096 |  | PG-5096
S-02115 | PG-5099 | 260 | Pressure Gauge |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | 0-1.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5099 |  | PG-5099
S-02115 | PG-5102 | 260 | Pressure Gauge |  | P32 |  | 8"-PMC-50-123-B24-N |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5102 |  | PG-5102
S-02115 | PG-5103 | 260 | Pressure Gauge |  | P32 |  | 10"-PMC-50-122-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | 0-1.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5103 |  | PG-5103
S-02115 | PG-5106 | 260 | Pressure Gauge |  | P32 |  | 8"-PMC-50-124-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5106 |  | PG-5106
S-02115 | PG-5112 | 260 | Pressure Gauge |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 0-1.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5112 |  | PG-5112
S-02115 | PG-5113 | 260 | Pressure Gauge |  | P32 |  | 6"-PG-50-102-B24-N |  |  | 3.5 | 0.2 | bar g |  | 47 | 75 | °C | 0-0.4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5113 |  | PG-5113
S-02115 | PG-5131 | 260 | Pressure Gauge |  | P33 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | 0-2.5 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5131 |  | PG-5131
S-02115 | PG-5134 | 260 | Pressure Gauge |  | P33 |  | 10"-PMC-50-132-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 0-6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5134 |  | PG-5134
S-02115 | PG-5135 | 260 | Pressure Gauge |  | P33 |  | 16"-PMC-50-131-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | 0-2.5 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5135 |  | PG-5135
S-02115 | PG-5138 | 260 | Pressure Gauge |  | P33 |  | 10"-PMC-50-133-B24-H |  |  | 10 | 2.5 | bar g |  | 88 | 160 | °C | 0-6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5138 |  | PG-5138
S-02115 | PG-5178 | 260 | Pressure Gauge |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | 0-400 mbar g | Diaphragm |  |  | Yes | [26 empty] | P | 5178 |  | PG-5178
S-02115 | PG-5206 | 260 | Pressure Gauge |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 0 - 400 mbar g | Diaphragm |  |  | Yes | [26 empty] | P | 5206 |  | PG-5206
S-02115 | PG-5210 | 260 | Pressure Gauge |  | P36 |  | 20"-PMP-50-102-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | 0-1 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5210 |  | PG-5210
S-02115 | PG-5213 | 260 | Pressure Gauge |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5213 |  | PG-5213
S-02115 | PG-5214 | 260 | Pressure Gauge |  | P36 |  | 20"-PMP-50-103-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | 0-1 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5214 |  | PG-5214
S-02115 | PG-5217 | 260 | Pressure Gauge |  | P36 |  | 12"-PMP-50-105-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 0-10 bar g | Bourdon | [29 empty] | P | 5217 |  | PG-5217
S-02115 | PG-5231 | 260 | Pressure Gauge |  | P37 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | 0-1.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5231 |  | PG-5231
S-02115 | PG-5232 | 260 | Pressure Gauge |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | 0-4 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 5232 |  | PG-5232
S-02115 | PG-5234 | 260 | Pressure Gauge |  | P37 |  | 8"-PMC-50-152-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 5234 |  | PG-5234
S-02115 | PG-5235 | 260 | Pressure Gauge |  | P37 |  | 10"-PMC-50-151-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | 0-1.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5235 |  | PG-5235
S-02115 | PG-5237 | 260 | Pressure Gauge |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | 0-4 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 5237 |  | PG-5237
S-02115 | PG-5238 | 260 | Pressure Gauge |  | P37 |  | 8"-PMC-50-153-D24-H |  |  | 16 | 6.5 | bar g |  | 86 | 160 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 5238 |  | PG-5238
S-02115 | PG-5303 | 260 | Pressure Gauge |  | P39 |  | 24"-LPS-50-108-D24-H |  |  | 9.5 | 6.5 | bar g |  | 188 | 340 | °C | 0-10 bar g | Bourdon |  | Yes | [27 empty] | P | 5303 |  | PG-5303
S-02115 | PG-5306 | 260 | Pressure Gauge |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 0-16 bar g | Bourdon |  | Yes | [27 empty] | P | 5306 |  | PG-5306
S-02115 | PG-5324 | 260 | Pressure Gauge |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | 0-6 bar g | Bourdon | [29 empty] | P | 5324 |  | PG-5324
S-02115 | PG-5327 | 260 | Pressure Gauge |  | P40 |  | 24"-PMP-50-130-D24-H |  |  | 19 | 2.6 | bar g |  | 101 | 165 | °C | 0-6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5327 |  | PG-5327
S-02115 | PG-5330 | 260 | Pressure Gauge |  | P40 |  | 6"-PMP-50-140-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 5330 |  | PG-5330
S-02115 | PG-5331 | 260 | Pressure Gauge |  | P40 |  | 24"-PMP-50-131-D24-H |  |  | 19 | 2.6 | bar g |  | 101 | 165 | °C | 0-6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5331 |  | PG-5331
S-02115 | PG-5334 | 260 | Pressure Gauge |  | P40 |  | 12"-PMP-50-133-D24-H |  |  | 19 | 3.6 | bar g |  | 101 | 165 | °C | 0-16 bar g | Bourdon | [29 empty] | P | 5334 |  | PG-5334
S-02115 | PG-5351 | 260 | Pressure Gauge |  | P41 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5351 |  | PG-5351
S-02115 | PG-5354 | 260 | Pressure Gauge |  | P41 |  | 6"-PMW-50-122-D24-H |  |  | 15 | 4.5 | bar g |  | 149 | 175 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5354 |  | PG-5354
S-02115 | PG-5355 | 260 | Pressure Gauge |  | P41 |  | 3"-PMW-50-121-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5355 |  | PG-5355
S-02115 | PG-5358 | 260 | Pressure Gauge |  | P41 |  | 6"-PMW-50-123-D24-H |  |  | 15 | 4.5 | bar g |  | 149 | 175 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5358 |  | PG-5358
S-02115 | PG-5359 | 260 | Pressure Gauge |  | P41 |  | 6"-PMW-50-130-F24-H |  |  | 82 | 3.6 | bar g |  | 149 | 175 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5359 |  | PG-5359
S-02115 | PG-5362 | 260 | Pressure Gauge |  | P41 |  | 3"-PMW-50-132-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 5362 |  | PG-5362
S-02115 | PG-5363 | 260 | Pressure Gauge |  | P41 |  | 6"-PMW-50-131-F24-H |  |  | 82 | 3.6 | bar g |  | 149 | 175 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5363 |  | PG-5363
S-02115 | PG-5366 | 260 | Pressure Gauge |  | P41 |  | 3"-PMW-50-133-F24-H |  |  | 82 | 50 | bar g |  | 150 | 175 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 5366 |  | PG-5366
S-02115 | PG-5388 | 260 | Pressure Gauge |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 0-6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5388 |  | PG-5388
S-02115 | PG-5399 | 260 | Pressure Gauge |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | -15 - +25 mbar g | Capsule | [29 empty] | P | 5399 |  | PG-5399
S-02115 | PG-5402 | 260 | Pressure Gauge |  | P43 |  | 4"-PMP-50-160-F24-N |  |  | 52 | 1 | bar g |  | 48 | 75 | °C | 0-4 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 5402 |  | PG-5402
S-02115 | PG-5406 | 260 | Pressure Gauge |  | P43 |  | 3"-PMP-50-161-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | 0-100 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 5406 |  | PG-5406
S-02115 | PG-5416 | 260 | Pressure Gauge |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | -15 - +25 mbar g | Capsule | [29 empty] | P | 5416 |  | PG-5416
S-02115 | PG-5423 | 260 | Pressure Gauge |  | P44 |  | 10"-PMP-50-150-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5423 |  | PG-5423
S-02115 | PG-5426 | 260 | Pressure Gauge |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5426 |  | PG-5426
S-02115 | PG-5427 | 260 | Pressure Gauge |  | P44 |  | 10"-PMP-50-151-B24-N |  |  | 14 | 1 | bar g |  | 48 | 75 | °C | 0-4 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5427 |  | PG-5427
S-02115 | PG-5430 | 260 | Pressure Gauge |  | P44 |  | 8"-PMP-50-154-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5430 |  | PG-5430
S-02115 | PG-5449 | 260 | Pressure Gauge |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | -15 - +25 mbar g | Capsule | [29 empty] | P | 5449 |  | PG-5449
S-02115 | PG-5453 | 260 | Pressure Gauge |  | P45 |  | 2"-LOS-50-120-F24-N |  |  | 60 | 0 | bar g |  | 48 | 75 | °C | 0-1 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 5453 |  | PG-5453
S-02115 | PG-5456 | 260 | Pressure Gauge |  | P45 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 0-100 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 5456 |  | PG-5456
S-02115 | PG-5457 | 260 | Pressure Gauge |  | P45 |  | 2"-LOS-50-121-F24-N |  |  | 60 | 0 | bar g |  | 48 | 75 | °C | 0-1 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 5457 |  | PG-5457
S-02115 | PG-5460 | 260 | Pressure Gauge |  | P45 |  | 2"-LOS-50-123-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 0-100 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 5460 |  | PG-5460
S-02115 | PG-5501 | 260 | Pressure Gauge |  | U23B |  | 6"-PMW-50-148-F24-N |  |  | 82 | 0 | bar g |  | 43 | 100 | °C | 0-0.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5501 |  | PG-5501
S-02115 | PG-5502 | 260 | Pressure Gauge |  | U23B |  | 3"-PMW-50-149-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 5502 |  | PG-5502
S-02115 | PG-5503 | 260 | Pressure Gauge |  | U23B |  | 6"-PMW-50-151-F24-H |  |  | 82 | 0 | bar g |  | 43 | 100 | °C | 0-0.6 bar g | Bourdon |  |  | Yes | [26 empty] | P | 5503 |  | PG-5503
S-02115 | PG-5504 | 260 | Pressure Gauge |  | U23B |  | 3"-PMW-50-152-F24-N |  |  | 82 | 50 | bar g |  | 43 | 100 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 5504 |  | PG-5504
S-02115 | PG-5511 | 260 | Pressure Gauge |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 0-4 bar g |  |  |  | Yes |  | Yes | [24 empty] | P | 5511 |  | PG-5511
S-02115 | PG-5513 | 260 | Pressure Gauge |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 0-4 bar g |  |  |  | Yes |  | Yes | [24 empty] | P | 5513 |  | PG-5513
S-02115 | PG-6002 | 260 | Pressure Gauge |  | P05 |  | 18"-MPC-60-101-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | 0-60 bar g | Bourdon |  |  | Yes | [26 empty] | P | 6002 |  | PG-6002
S-02115 | PG-6005 | 260 | Pressure Gauge |  | P05 |  | 10"-MPC-60-106-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6005 |  | PG-6005
S-02115 | PG-6006 | 260 | Pressure Gauge |  | P05 |  | 18"-MPC-60-102-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | 0-60 bar g | Bourdon |  |  | Yes | [26 empty] | P | 6006 |  | PG-6006
S-02115 | PG-6009 | 260 | Pressure Gauge |  | P05 |  | 10"-MPC-60-108-F24-H |  |  | 73 | 45 | bar g |  | 241 | 260 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6009 |  | PG-6009
S-02115 | PG-6023 | 260 | Pressure Gauge |  | P06 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6023 |  | PG-6023
S-02115 | PG-6029 | 260 | Pressure Gauge |  | P06 |  | 8"-PRC-60-103-G40-H |  |  | 71 | 44 | bar g |  | 115 | 180 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6029 |  | PG-6029
S-02115 | PG-6030 | 260 | Pressure Gauge |  | P06 |  | 8"-PRC-60-104-G40-H |  |  | 71 | 44 | bar g |  | 115 | 180 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6030 |  | PG-6030
S-02115 | PG-6055 | 260 | Pressure Gauge |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6055 |  | PG-6055
S-02115 | PG-6060 | 260 | Pressure Gauge |  | P07 |  | 16"-PRC-60-109-G40-H |  |  | 72 | 43 | bar g |  | 225 | 290 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6060 |  | PG-6060
S-02115 | PG-6063 | 260 | Pressure Gauge |  | P07 |  | 10"-PRC-60-111-G40-H |  |  | 72 | 44 | bar g |  | 225 | 290 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6063 |  | PG-6063
S-02115 | PG-6064 | 260 | Pressure Gauge |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6064 |  | PG-6064
S-02115 | PG-6067 | 260 | Pressure Gauge |  | P07 |  | 10"-PRC-60-112-G40-H |  |  | 72 | 44 | bar g |  | 225 | 280 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 6067 |  | PG-6067
S-02115 | PG-6081 | 260 | Pressure Gauge |  | P08 |  | 4"-BD-60-117-B40-P |  |  | 9 | 0 | bar g |  | 100 | 125 | °C | 0-1 bar g | Bourdon |  |  | Yes | [26 empty] | P | 6081 |  | PG-6081
S-02115 | PG-6082 | 260 | Pressure Gauge |  | P08 |  | 4"-BD-60-119-B40-P |  |  | 9 | 3 | bar g |  | 78 | 150 | °C | 0-6 bar g | Bourdon | [29 empty] | P | 6082 |  | PG-6082
S-02115 | PG-6086 | 260 | Pressure Gauge |  | P08 |  | 4"-BD-60-117-B40-P |  |  | 9 | 0 | bar g |  | 100 | 125 | °C | 0-1 bar g | Bourdon |  |  | Yes | [26 empty] | P | 6086 |  | PG-6086
S-02115 | PG-6087 | 260 | Pressure Gauge |  | P08 |  | 4"-BD-60-123-B40-P |  |  | 7 | 3 | bar g |  | 100 | 125 | °C | 0-6 bar g | Bourdon | [29 empty] | P | 6087 |  | PG-6087
S-02115 | PG-7008 | 260 | Pressure Gauge |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 7008 |  | PG-7008
S-02115 | PG-7022 | 260 | Pressure Gauge |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 7022 |  | PG-7022
S-02115 | PG-7035 | 260 | Pressure Gauge |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 0-60 bar g | Bourdon |  | Yes | [27 empty] | P | 7035 |  | PG-7035
S-02115 | PG-7054 | 260 | Pressure Gauge |  | U06 |  | 16"-LPS-70-138-D24-H |  |  | 9.5 | 7 | bar g |  | 240 | 340 | °C | 0-16 bar g | Bourdon |  | Yes | [27 empty] | P | 7054 |  | PG-7054
S-02115 | PG-7062 | 260 | Pressure Gauge |  | U18 |  | 10"-DMW-70-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 7062 |  | PG-7062
S-02115 | PG-7063 | 260 | Pressure Gauge |  | U18 |  | 10"-DMW-70-109-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-10 bar g | Bourdon |  |  | Yes | [26 empty] | P | 7063 |  | PG-7063
S-02115 | PG-7093 | 260 | Pressure Gauge |  | U09 |  | D 7001 Top |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 0-2.5 bar g | Bourdon |  | Yes | Yes | [26 empty] | P | 7093 |  | PG-7093
S-02115 | PG-7102 | 260 | Pressure Gauge |  | U22 |  | 2"-PRC-70-139-G40-N |  |  | 71 | 1 | bar g |  | 65 | 100 | °C | 0-1.6 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 7102 |  | PG-7102
S-02115 | PG-7103 | 260 | Pressure Gauge |  | U22 |  | 2"-PRC-70-141-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | 0-100 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7103 |  | PG-7103
S-02115 | PG-7105 | 260 | Pressure Gauge |  | U22 |  | 2"-PRC-70-143-G40-N |  |  | 71 | 1 | bar g |  | 65 | 100 | °C | 0-1.6 bar g | Bourdon |  |  | Yes |  | Yes | [24 empty] | P | 7105 |  | PG-7105
S-02115 | PG-7106 | 260 | Pressure Gauge |  | U22 |  | 2"-PRC-70-144-G40-N |  |  | 71 | 45 | bar g |  | 65 | 100 | °C | 0-100 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7106 |  | PG-7106
S-02115 | PG-7111 | 260 | Pressure Gauge |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-4 bar g | Bourdon | [29 empty] | P | 7111 |  | PG-7111
S-02115 | PG-7113 | 260 | Pressure Gauge |  | U10 |  | 8"-BFW-70-160-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-250 bar g | Bourdon | [29 empty] | P | 7113 |  | PG-7113
S-02115 | PG-7114 | 260 | Pressure Gauge |  | U10 |  | 6"-BFW-70-138-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 7114 |  | PG-7114
S-02115 | PG-7115 | 260 | Pressure Gauge |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-4 bar g | Bourdon | [29 empty] | P | 7115 |  | PG-7115
S-02115 | PG-7117 | 260 | Pressure Gauge |  | U10 |  | 8"-BFW-70-133-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-250 bar g | Bourdon | [29 empty] | P | 7117 |  | PG-7117
S-02115 | PG-7118 | 260 | Pressure Gauge |  | U10 |  | 4"-BFW-70-149-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 7118 |  | PG-7118
S-02115 | PG-7119 | 260 | Pressure Gauge |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 0-4 bar g | Bourdon | [29 empty] | P | 7119 |  | PG-7119
S-02115 | PG-7123 | 260 | Pressure Gauge |  | U10 |  | 8"-BFW-70-147-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 0-250 bar g | Bourdon | [29 empty] | P | 7123 |  | PG-7123
S-02115 | PG-7124 | 260 | Pressure Gauge |  | U10 |  | 4"-BFW-70-148-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | 0-100 bar g | Bourdon | [29 empty] | P | 7124 |  | PG-7124
S-02115 | PG-7128 | 260 | Pressure Gauge |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 7128 |  | PG-7128
S-02115 | PG-7133 | 260 | Pressure Gauge |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-100 bar g | Bourdon |  | Yes | [27 empty] | P | 7133 |  | PG-7133
S-02115 | PG-7138 | 260 | Pressure Gauge |  | U10 |  | 14"-LPS-70-121-D24-H |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 0-16 bar g | Bourdon |  | Yes | [27 empty] | P | 7138 |  | PG-7138
S-02115 | PG-7139 | 260 | Pressure Gauge |  | U10 |  | 14"-LPS-70-125-D24-H |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 0-16 bar g | Bourdon |  | Yes | [27 empty] | P | 7139 |  | PG-7139
S-02115 | PG-7164 | 260 | Pressure Gauge |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | 0-160 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7164 |  | PG-7164
S-02115 | PG-7167 | 260 | Pressure Gauge |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | 0-160 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7167 |  | PG-7167
S-02115 | PG-7170 | 260 | Pressure Gauge |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | 0-60 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7170 |  | PG-7170
S-02115 | PG-7173 | 260 | Pressure Gauge |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | 0-60 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7173 |  | PG-7173
S-02115 | PG-7194 | 260 | Pressure Gauge |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 0-6 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7194 |  | PG-7194
S-02115 | PG-7197 | 260 | Pressure Gauge |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 0-6 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7197 |  | PG-7197
S-02115 | PG-7214 | 260 | Pressure Gauge |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 0-6 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7214 |  | PG-7214
S-02115 | PG-7217 | 260 | Pressure Gauge |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 0-6 bar g | Bourdon |  |  |  |  | Yes | [24 empty] | P | 7217 |  | PG-7217
S-02115 | PG-8011 | 260 | Pressure Gauge |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | 0-2.5 bar g | Bourdon |  |  | Yes | [26 empty] | P | 8011 |  | PG-8011
S-02115 | PG-8012 | 260 | Pressure Gauge |  | U21 |  | -IA-80-101- |  |  |  |  | bar g |  |  |  | °C | By detailed engineering bar g | Bourdon | [29 empty] | P | 8012 |  | PG-8012
S-02115 | PDI-2574 | 261 | D/P Indicator |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-1 bar | [30 empty] | P | 2574 |  | PDI-2574
S-02115 | TG-1002 | 262 | Thermometer, Bimetal |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 0-120 °C | [30 empty] | T | 1002 |  | TG-1002
S-02115 | TG-2002 | 262 | Thermometer, Bimetal |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 0-120 °C | [30 empty] | T | 2002 |  | TG-2002
S-02115 | TG-2011 | 262 | Thermometer, Bimetal |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | 0-120 °C | [30 empty] | T | 2011 |  | TG-2011
S-02115 | TG-2012 | 262 | Thermometer, Bimetal |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | 0-400 °C | [30 empty] | T | 2012 |  | TG-2012
S-02115 | TG-2013 | 262 | Thermometer, Bimetal |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | 0-400 °C | [30 empty] | T | 2013 |  | TG-2013
S-02115 | TG-2116 | 262 | Thermometer, Bimetal |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-600 °C | [30 empty] | T | 2116 |  | TG-2116
S-02115 | TG-2120 | 262 | Thermometer, Bimetal |  | P11 |  | 16"-LPS-20-102-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 0-400 °C | [30 empty] | T | 2120 |  | TG-2120
S-02115 | TG-2164 | 262 | Thermometer, Bimetal |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-600 °C | [30 empty] | T | 2164 |  | TG-2164
S-02115 | TG-2170 | 262 | Thermometer, Bimetal |  | P12 |  | 12"-LPS-20-106-D24-H |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 0-400 °C | [30 empty] | T | 2170 |  | TG-2170
S-02115 | TG-2401 | 262 | Thermometer, Bimetal |  | P19 |  | 24"-RFG |  |  | 29 | 25.8 | bar g |  | 251 | 280 | °C | 0-400 °C | [30 empty] | T | 2401 |  | TG-2401
S-02115 | TG-2403 | 262 | Thermometer, Bimetal |  | P19 |  | 24"-RFG |  |  | 29 | 25.8 | bar g |  | 208 | 280 | °C | 0-400 °C | [30 empty] | T | 2403 |  | TG-2403
S-02115 | TG-2404 | 262 | Thermometer, Bimetal |  | P19 |  | 12"-BFW |  |  | 113 | 104 | bar g |  | 166 | 310 | °C | 0-400 °C | [30 empty] | T | 2404 |  | TG-2404
S-02115 | TG-2405 | 262 | Thermometer, Bimetal |  | P19 |  | 12"-BFW |  |  | 113 | 104 | bar g |  | 210 | 310 | °C | 0-400 °C | [30 empty] | T | 2405 |  | TG-2405
S-02115 | TG-2454 | 262 | Thermometer, Bimetal |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 0-120 °C | [30 empty] | T | 2454 |  | TG-2454
S-02115 | TG-2456 | 262 | Thermometer, Bimetal |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 0-250 °C | [30 empty] | T | 2456 |  | TG-2456
S-02115 | TG-2494 | 262 | Thermometer, Bimetal |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 2494 |  | TG-2494
S-02115 | TG-2574 | 262 | Thermometer, Bimetal |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 0-120 °C | [30 empty] | T | 2574 |  | TG-2574
S-02115 | TG-3025 | 262 | Thermometer, Bimetal |  | P22 |  | 20"-CWR-30-101-B24-N |  |  | 7 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 3025 |  | TG-3025
S-02115 | TG-3051 | 262 | Thermometer, Bimetal |  | P23 |  | Downcomers |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 0-400 °C | [30 empty] | T | 3051 |  | TG-3051
S-02115 | TG-3074 | 262 | Thermometer, Bimetal |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | [30 empty] | T | 3074 |  | TG-3074
S-02115 | TG-3078 | 262 | Thermometer, Bimetal |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | [30 empty] | T | 3078 |  | TG-3078
S-02115 | TG-3082 | 262 | Thermometer, Bimetal |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 0-400 °C | [30 empty] | T | 3082 |  | TG-3082
S-02115 | TG-3085 | 262 | Thermometer, Bimetal |  | P24 |  | 16"-MPS-30-132-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 0-500 °C | [30 empty] | T | 3085 |  | TG-3085
S-02115 | TG-3086 | 262 | Thermometer, Bimetal |  | P24 |  | 16"-MPC-30-131-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 0-500 °C | [30 empty] | T | 3086 |  | TG-3086
S-02115 | TG-3088 | 262 | Thermometer, Bimetal |  | P24 |  | 16"-MPS-30-128-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 0-500 °C | [30 empty] | T | 3088 |  | TG-3088
S-02115 | TG-3089 | 262 | Thermometer, Bimetal |  | P24 |  | 16"-MPC-30-127-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 0-500 °C | [30 empty] | T | 3089 |  | TG-3089
S-02115 | TG-3091 | 262 | Thermometer, Bimetal |  | P24 |  | 16"-MPS-30-123-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 0-500 °C | [30 empty] | T | 3091 |  | TG-3091
S-02115 | TG-3092 | 262 | Thermometer, Bimetal |  | P24 |  | 16"-MPC-30-122-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 280 | °C | 0-400 °C | [30 empty] | T | 3092 |  | TG-3092
S-02115 | TG-3143 | 262 | Thermometer, Bimetal |  | P26 |  | 24"-CWR-30-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 3143 |  | TG-3143
S-02115 | TG-3146 | 262 | Thermometer, Bimetal |  | P26 |  | 14"-CWR-30-106-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 3146 |  | TG-3146
S-02115 | TG-3149 | 262 | Thermometer, Bimetal |  | P26 |  | 14"-CWR-30-105-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 3149 |  | TG-3149
S-02115 | TG-5008 | 262 | Thermometer, Bimetal |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 0-120 °C | [30 empty] | T | 5008 |  | TG-5008
S-02115 | TG-5108 | 262 | Thermometer, Bimetal |  | P32 |  | 3"-CWR-50-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5108 |  | TG-5108
S-02115 | TG-5220 | 262 | Thermometer, Bimetal |  | P36 |  | 6"-CWR-50-104-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5220 |  | TG-5220
S-02115 | TG-5276 | 262 | Thermometer, Bimetal |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 0-250 °C | [30 empty] | T | 5276 |  | TG-5276
S-02115 | TG-5339 | 262 | Thermometer, Bimetal |  | P40 |  | 10"-CWR-50-103-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5339 |  | TG-5339
S-02115 | TG-5370 | 262 | Thermometer, Bimetal |  | P41 |  | 3"-CWR-50-112-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5370 |  | TG-5370
S-02115 | TG-5394 | 262 | Thermometer, Bimetal |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | 0-120 °C | [30 empty] | T | 5394 |  | TG-5394
S-02115 | TG-5411 | 262 | Thermometer, Bimetal |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 0-120 °C | [30 empty] | T | 5411 |  | TG-5411
S-02115 | TG-5444 | 262 | Thermometer, Bimetal |  | P45 |  | 3"-CWR-50-115-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5444 |  | TG-5444
S-02115 | TG-5445 | 262 | Thermometer, Bimetal |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5445 |  | TG-5445
S-02115 | TG-5501 | 262 | Thermometer, Bimetal |  | U23A |  | 4"-CWR-50-118-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 5501 |  | TG-5501
S-02115 | TG-6082 | 262 | Thermometer, Bimetal |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | 0-250 °C | [30 empty] | T | 6082 |  | TG-6082
S-02115 | TG-6083 | 262 | Thermometer, Bimetal |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 0-400 °C | [30 empty] | T | 6083 |  | TG-6083
S-02115 | TG-6085 | 262 | Thermometer, Bimetal |  | P08 |  | 3"-CWR-60-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 6085 |  | TG-6085
S-02115 | TG-6086 | 262 | Thermometer, Bimetal |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | 0-120 °C | [30 empty] | T | 6086 |  | TG-6086
S-02115 | TG-7008 | 262 | Thermometer, Bimetal |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 0-600 °C | [30 empty] | T | 7008 |  | TG-7008
S-02115 | TG-7022 | 262 | Thermometer, Bimetal |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 0-600 °C | [30 empty] | T | 7022 |  | TG-7022
S-02115 | TG-7128 | 262 | Thermometer, Bimetal |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-600 °C | [30 empty] | T | 7128 |  | TG-7128
S-02115 | TG-7133 | 262 | Thermometer, Bimetal |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 0-600 °C | [30 empty] | T | 7133 |  | TG-7133
S-02115 | TG-7138 | 262 | Thermometer, Bimetal |  | U10 |  | 14"-LPS-70-121-D24-H |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 0-400 °C | [30 empty] | T | 7138 |  | TG-7138
S-02115 | TG-7139 | 262 | Thermometer, Bimetal |  | U10 |  | 14"-LPS-70-125-D24-H |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 0-400 °C | [30 empty] | T | 7139 |  | TG-7139
S-02115 | TG-7256 | 262 | Thermometer, Bimetal |  | U16 |  | 4"-CWR-70-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 0-120 °C | [30 empty] | T | 7256 |  | TG-7256
S-02115 | LI1-5001 | 263 | Receiver Indicator, Local |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 5001 |  | LI-5001
S-02115 | LI1-5396 | 263 | Receiver Indicator, Local |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 5396 |  | LI-5396
S-02115 | LI1-5413 | 263 | Receiver Indicator, Local |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 5413 |  | LI-5413
S-02115 | LI1-5446 | 263 | Receiver Indicator, Local |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 5446 |  | LI-5446
S-02115 | LI1-7001 | 263 | Receiver Indicator, Local |  | U18 |  | TK 7001 1 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 7001 |  | LI-7001
S-02115 | LI1-7002 | 263 | Receiver Indicator, Local |  | U18 |  | TK 7001 2 |  |  |  | Atmospheric | bar g |  | 35 | 85 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 7002 |  | LI-7002
S-02115 | LI1-7101 | 263 | Receiver Indicator, Local |  | U22 |  | TK 7002 |  |  | Atmospheric | Atmospheric | bar g |  | 65 | 100 | °C | 0-100 % | 4-20 mA | [29 empty] | L | 7101 |  | LI-7101
S-02115 | HS-2095 | 276 | Manual Oper. Switch |  | P10 | [10 empty] | °C | Hand operated | [30 empty] | H | 2095 |  | HS-2095
S-02115 | HS-2098 | 276 | Manual Oper. Switch |  | P10 | [10 empty] | °C | Hand operated | [30 empty] | H | 2098 |  | HS-2098
S-02115 | HS-2544 | 276 | Manual Oper. Switch |  | U01 | [10 empty] | °C | Hand operated | [30 empty] | H | 2544 |  | HS-2544
S-02115 | FSAL-2007 | 281 | Safety Interlock Circuit |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | IS-2 | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FFSAH-2008 | 281 | Safety Interlock Circuit |  | P02 | [10 empty] | °C | IS-2 | [30 empty] | F | 2008 |  | FFSAH-2008
S-02115 | FSAL-2040 | 281 | Safety Interlock Circuit |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | IS-2 | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FSAL-2062 | 281 | Safety Interlock Circuit |  | P09 | [10 empty] | °C | IS-1, I-20 | [30 empty] | F | 2062 |  | FSAL-2062
S-02115 | FFSAL-2064 | 281 | Safety Interlock Circuit |  | P09 | [10 empty] | °C | IS-1, I-20 | [30 empty] | F | 2064 |  | FFSAL-2064
S-02115 | FSAL-2582 | 281 | Safety Interlock Circuit |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | IS-1 | [30 empty] | F | 2582 |  | FI-2582
S-02115 | FSAL-6070 | 281 | Safety Interlock Circuit |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | IS-1, I-20 | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | LSAH-1004 | 281 | Safety Interlock Circuit |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | IS-1 | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LSAL-1004 | 281 | Safety Interlock Circuit |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | IS-5 | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LSAL-2372 | 281 | Safety Interlock Circuit |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | IS-1 | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LSAL-2404 | 281 | Safety Interlock Circuit |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | IS-33 | [30 empty] | L | 2404 |  | LI-2404
S-02115 | LSAL-2442 | 281 | Safety Interlock Circuit |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | IS-34 | [30 empty] | L | 2442 |  | LI-2442
S-02115 | LSAH-2474 | 281 | Safety Interlock Circuit |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | IS-40 | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LSAL-2474 | 281 | Safety Interlock Circuit |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | IS-35 | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LSAL-3042 | 281 | Safety Interlock Circuit |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | IS-3 | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LSAH-3161 | 281 | Safety Interlock Circuit |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | IS-3 | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LSAL-3161 | 281 | Safety Interlock Circuit |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | IS-42 | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LSAH-3192 | 281 | Safety Interlock Circuit |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | IS-42 | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LSAL-3192 | 281 | Safety Interlock Circuit |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | IS-43 | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LSAH-5002 | 281 | Safety Interlock Circuit |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | IS-44 | [30 empty] | L | 5002 |  | LI-5002
S-02115 | LSAL-5002 | 281 | Safety Interlock Circuit |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | IS-53 | [30 empty] | L | 5002 |  | LI-5002
S-02115 | LSAL-5042 | 281 | Safety Interlock Circuit |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | IS-54 | [30 empty] | L | 5042 |  | LI-5042
S-02115 | LSAL-5071 | 281 | Safety Interlock Circuit |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | IS-55 | [30 empty] | L | 5071 |  | LI-5071
S-02115 | LSAL-5094 | 281 | Safety Interlock Circuit |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | IS-56 | [30 empty] | L | 5094 |  | LI-5094
S-02115 | LSAL-5162 | 281 | Safety Interlock Circuit |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | IS-57 | [30 empty] | L | 5162 |  | LI-5162
S-02115 | LSAL-5204 | 281 | Safety Interlock Circuit |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | IS-58 | [30 empty] | L | 5204 |  | LI-5204
S-02115 | LSAL-5271 | 281 | Safety Interlock Circuit |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | IS-59 | [30 empty] | L | 5271 |  | LI-5271
S-02115 | LSAL-5322 | 281 | Safety Interlock Circuit |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | IS-60 | [30 empty] | L | 5322 |  | LI-5322
S-02115 | LSAH-5397 | 281 | Safety Interlock Circuit |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | IS-62, I-50 | [30 empty] | L | 5397 |  | LI-5397
S-02115 | LSAL-5397 | 281 | Safety Interlock Circuit |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | IS-64 | [30 empty] | L | 5397 |  | LI-5397
S-02115 | LSAH-5414 | 281 | Safety Interlock Circuit |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | IS-63, I-50 | [30 empty] | L | 5414 |  | LI-5414
S-02115 | LSAL-5414 | 281 | Safety Interlock Circuit |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | IS-65 | [30 empty] | L | 5414 |  | LI-5414
S-02115 | LSAL-5501 | 281 | Safety Interlock Circuit |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | IS-67 | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LSAL-6022/1 | 281 | Safety Interlock Circuit |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | IS-30 | [30 empty] | L | 6022 | 1 | LI-6022/1
S-02115 | LSAL-6022/2 | 281 | Safety Interlock Circuit |  | P06 |  | T 6001 2 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | IS-30 | [30 empty] | L | 6022 | 2 | LI-6022/2
S-02115 | LSAH-6051 | 281 | Safety Interlock Circuit |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | IS-1 | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LSAL-6051 | 281 | Safety Interlock Circuit |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | IS-31 | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LSAL-7091 | 281 | Safety Interlock Circuit |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | IS-70 | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | PDSAL-2036 | 281 | Safety Interlock Circuit |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | IS-21 | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PSAL-2163 | 281 | Safety Interlock Circuit |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | IS-1 | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PSAH-2224 | 281 | Safety Interlock Circuit |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | IS-1 | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PSAL-2224 | 281 | Safety Interlock Circuit |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | IS-1 | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PSAH-2554 | 281 | Safety Interlock Circuit |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | IS-1 | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PSAL-2554 | 281 | Safety Interlock Circuit |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | IS-14 | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PSAL-2556 | 281 | Safety Interlock Circuit |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | IS-1 | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PSAH-5207 | 281 | Safety Interlock Circuit |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | IS-4 | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PSAL-7112 | 281 | Safety Interlock Circuit |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | IS-71 | [30 empty] | P | 7112 |  | PI-7112
S-02115 | PSAL-7116 | 281 | Safety Interlock Circuit |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | IS-72 | [30 empty] | P | 7116 |  | PI-7116
S-02115 | PSAL-7120 | 281 | Safety Interlock Circuit |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | IS-73 | [30 empty] | P | 7120 |  | PI-7120
S-02115 | TSAL-2047 | 281 | Safety Interlock Circuit |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | IS-2 | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TSAH-2221 | 281 | Safety Interlock Circuit |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | IS-1 | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TSAH-2305 | 281 | Safety Interlock Circuit |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | IS-1 | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TSAH-2325 | 281 | Safety Interlock Circuit |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | IS-2 | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TSAH-2329 | 281 | Safety Interlock Circuit |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | IS-2 | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TSAH-2333 | 281 | Safety Interlock Circuit |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | IS-2 | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TSAH-2334 | 281 | Safety Interlock Circuit |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | IS-2 | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TSAH-2335 | 281 | Safety Interlock Circuit |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | IS-1 | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TSAH-2336 | 281 | Safety Interlock Circuit |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | IS-1 | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TSAH-2360 | 281 | Safety Interlock Circuit |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | IS-1 | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TSAH-3072 | 281 | Safety Interlock Circuit |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | IS-3 | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TSAH-3076 | 281 | Safety Interlock Circuit |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | IS-3 | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TSAH-3080 | 281 | Safety Interlock Circuit |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | IS-3 | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TSAH-7071 | 281 | Safety Interlock Circuit |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | IS-2 | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | USY-2118 | 281 | Safety Interlock Circuit |  | P11 | [10 empty] | °C | IS-11 | [30 empty] | U | 2118 |  | USY-2118
S-02115 | USY-2169 | 281 | Safety Interlock Circuit |  | P12 | [10 empty] | °C | IS-13 | [30 empty] | U | 2169 |  | USY-2169
S-02115 | AS_I/A-1001 | 281.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AS_I/B-1001 | 281.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AS_I/C-1001 | 281.01 | Analog Input |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | A | 1001 |  | AI-1001
S-02115 | FS_I/A-2007 | 281.01 | Analog Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 4-20 mA | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FS_I/B-2007 | 281.01 | Analog Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 4-20 mA | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FS_I/C-2007 | 281.01 | Analog Input |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 4-20 mA | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FS_I/A-2040 | 281.01 | Analog Input |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FS_I/B-2040 | 281.01 | Analog Input |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FS_I/C-2040 | 281.01 | Analog Input |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FS_I/A-2061 | 281.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FS_I/B-2061 | 281.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FS_I/C-2061 | 281.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FS_I/A-2072 | 281.01 | Analog Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FS_I/B-2072 | 281.01 | Analog Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FS_I/C-2072 | 281.01 | Analog Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FS_I/A-2233 | 281.01 | Analog Input |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 4-20 mA | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FS_I/B-2233 | 281.01 | Analog Input |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 4-20 mA | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FS_I/C-2233 | 281.01 | Analog Input |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 4-20 mA | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FS_I-2582 | 281.01 | Analog Input |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 4-20 mA |  | PST-2582 | [28 empty] | F | 2582 |  | FI-2582
S-02115 | FS_I/A-6070 | 281.01 | Analog Input |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 4-20 mA | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FS_I/B-6070 | 281.01 | Analog Input |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 4-20 mA | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FS_I/C-6070 | 281.01 | Analog Input |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 4-20 mA | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | LS_I/A-1004 | 281.01 | Analog Input |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LS_I/B-1004 | 281.01 | Analog Input |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LS_I/C-1004 | 281.01 | Analog Input |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4-20 mA | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LS_I/A-2372 | 281.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LS_I/B-2372 | 281.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LS_I/C-2372 | 281.01 | Analog Input |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LS_I-2404 | 281.01 | Analog Input |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 4-20 mA | [30 empty] | L | 2404 |  | LI-2404
S-02115 | LS_I-2442 | 281.01 | Analog Input |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | 4-20 mA | [30 empty] | L | 2442 |  | LI-2442
S-02115 | LS_I/A-2474 | 281.01 | Analog Input |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LS_I/B-2474 | 281.01 | Analog Input |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LS_I/C-2474 | 281.01 | Analog Input |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LS_I/A-3042 | 281.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LS_I/B-3042 | 281.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LS_I/C-3042 | 281.01 | Analog Input |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LS_I/A-3161 | 281.01 | Analog Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LS_I/B-3161 | 281.01 | Analog Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LS_I/C-3161 | 281.01 | Analog Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LS_I/A-3192 | 281.01 | Analog Input |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 4-20 mA | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LS_I/B-3192 | 281.01 | Analog Input |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 4-20 mA | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LS_I/C-3192 | 281.01 | Analog Input |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 4-20 mA | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LS_I-5002 | 281.01 | Analog Input |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 4-20 mA | [30 empty] | L | 5002 |  | LI-5002
S-02115 | LS_I-5042 | 281.01 | Analog Input |  | P30 |  | T 5001 Bottom |  |  | 3.5 | 1 | bar g |  | 88 | 150 | °C | 4-20 mA | [30 empty] | L | 5042 |  | LI-5042
S-02115 | LS_I-5071 | 281.01 | Analog Input |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | 4-20 mA | [30 empty] | L | 5071 |  | LI-5071
S-02115 | LS_I-5094 | 281.01 | Analog Input |  | P32 |  | D 5001 Bottom |  |  | 3.5 | 0.6 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | L | 5094 |  | LI-5094
S-02115 | LS_I-5162 | 281.01 | Analog Input |  | P34 |  | T 5002 Bottom |  |  | 3.5 | 0.7 | bar g |  | 86 | 150 | °C | 4-20 mA | [30 empty] | L | 5162 |  | LI-5162
S-02115 | LS_I-5204 | 281.01 | Analog Input |  | P36 |  | D 5002 Bottom |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | L | 5204 |  | LI-5204
S-02115 | LS_I-5271 | 281.01 | Analog Input |  | P38 |  | T 5003 Bottom |  |  | 6 | 3.6 | bar g |  | 149 | 175 | °C | 2020-04-01 | [30 empty] | L | 5271 |  | LI-5271
S-02115 | LS_I-5322 | 281.01 | Analog Input |  | P40 |  | D 5003 |  |  | 6 | 2.7 | bar g |  | 101 | 165 | °C | 4-20 mA | [30 empty] | L | 5322 |  | LI-5322
S-02115 | LS_I-5397 | 281.01 | Analog Input |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | 4-20 mA | [30 empty] | L | 5397 |  | LI-5397
S-02115 | LS_I-5414 | 281.01 | Analog Input |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 4-20 mA | [30 empty] | L | 5414 |  | LI-5414
S-02115 | LS_I-5447 | 281.01 | Analog Input |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 4-20 mA | [30 empty] | L | 5447 |  | LI-5447
S-02115 | LS_I/A-5501 | 281.01 | Analog Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 4-20 mA | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LS_I/B-5501 | 281.01 | Analog Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 4-20 mA | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LS_I/C-5501 | 281.01 | Analog Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 4-20 mA | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LS_I-6022/1 | 281.01 | Analog Input |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | 4-20 mA | [30 empty] | L | 6022 | 1 | LI-6022/1
S-02115 | LS_I-6022/2 | 281.01 | Analog Input |  | P06 |  | T 6001 2 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | 4-20 mA | [30 empty] | L | 6022 | 2 | LI-6022/2
S-02115 | LS_I/A-6051 | 281.01 | Analog Input |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 4-20 mA | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LS_I/B-6051 | 281.01 | Analog Input |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 4-20 mA | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LS_I/C-6051 | 281.01 | Analog Input |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 4-20 mA | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LS_I/A-7091 | 281.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 4-20 mA | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | LS_I/B-7091 | 281.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 4-20 mA | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | LS_I/C-7091 | 281.01 | Analog Input |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 4-20 mA | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | PDS_IA-2036 | 281.01 | Analog Input |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PDS_IB-2036 | 281.01 | Analog Input |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PDS_IC-2036 | 281.01 | Analog Input |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 4-20 mA | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PZI_I-2073 | 281.01 | Analog Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 4-20 mA | [30 empty] | P | 2073 |  | PIC-2073
S-02115 | PS_I/A-2163 | 281.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 4-20 mA | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PS_I/B-2163 | 281.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 4-20 mA | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PS_I/C-2163 | 281.01 | Analog Input |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 4-20 mA | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PS_I/A-2224 | 281.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PS_I/B-2224 | 281.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PS_I/C-2224 | 281.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PS_I/A-2372 | 281.01 | Analog Input |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PS_I/B-2372 | 281.01 | Analog Input |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PS_I/C-2372 | 281.01 | Analog Input |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 4-20 mA | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PS_I/A-2554 | 281.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PS_I/B-2554 | 281.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PS_I/C-2554 | 281.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PS_I/A-2556 | 281.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PS_I/B-2556 | 281.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PS_I/C-2556 | 281.01 | Analog Input |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 4-20 mA | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PS_I-2582 | 281.01 | Analog Input |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 4-20 mA |  | of FSAL-2582 | [28 empty] | P | 2582 |  | PI-2582
S-02115 | PS_I/A-3042 | 281.01 | Analog Input |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PS_I/B-3042 | 281.01 | Analog Input |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PS_I/C-3042 | 281.01 | Analog Input |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 4-20 mA | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PS_I/A-5207 | 281.01 | Analog Input |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PS_I/B-5207 | 281.01 | Analog Input |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PS_I/C-5207 | 281.01 | Analog Input |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 4-20 mA | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PS_I-7112 | 281.01 | Analog Input |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 4-20 mA | [30 empty] | P | 7112 |  | PI-7112
S-02115 | PS_I-7116 | 281.01 | Analog Input |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 4-20 mA | [30 empty] | P | 7116 |  | PI-7116
S-02115 | PS_I-7120 | 281.01 | Analog Input |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 4-20 mA | [30 empty] | P | 7120 |  | PI-7120
S-02115 | TS_I/A-2047 | 281.01 | Analog Input |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 4-20 mA | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TS_I/B-2047 | 281.01 | Analog Input |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 4-20 mA | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TS_I/C-2047 | 281.01 | Analog Input |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 4-20 mA | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TS_I/A-2221 | 281.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TS_I/B-2221 | 281.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TS_I/C-2221 | 281.01 | Analog Input |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 4-20 mA | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TS_I/A-2305 | 281.01 | Analog Input |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 4-20 mA | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TS_I/B-2305 | 281.01 | Analog Input |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 4-20 mA | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TS_I/C-2305 | 281.01 | Analog Input |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 4-20 mA | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TS_I/A-2325 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TS_I/B-2325 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TS_I/C-2325 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TS_I/A-2329 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 4-20 mA | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TS_I/B-2329 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 4-20 mA | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TS_I/C-2329 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 4-20 mA | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TS_I/A-2333 | 281.01 | Analog Input |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TS_I/B-2333 | 281.01 | Analog Input |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TS_I/C-2333 | 281.01 | Analog Input |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TS_I/A-2334 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TS_I/B-2334 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TS_I/C-2334 | 281.01 | Analog Input |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 4-20 mA | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TS_I/A-2335 | 281.01 | Analog Input |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TS_I/B-2335 | 281.01 | Analog Input |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TS_I/C-2335 | 281.01 | Analog Input |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TS_I/A-2336 | 281.01 | Analog Input |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TS_I/B-2336 | 281.01 | Analog Input |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TS_I/C-2336 | 281.01 | Analog Input |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 4-20 mA | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TS_I/A-2360 | 281.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 4-20 mA | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TS_I/B-2360 | 281.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 4-20 mA | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TS_I/C-2360 | 281.01 | Analog Input |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 4-20 mA | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TS_I/A-3072 | 281.01 | Analog Input |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TS_I/B-3072 | 281.01 | Analog Input |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TS_I/C-3072 | 281.01 | Analog Input |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TS_I/A-3076 | 281.01 | Analog Input |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TS_I/B-3076 | 281.01 | Analog Input |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TS_I/C-3076 | 281.01 | Analog Input |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TS_I/A-3080 | 281.01 | Analog Input |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TS_I/B-3080 | 281.01 | Analog Input |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TS_I/C-3080 | 281.01 | Analog Input |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 4-20 mA | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TS_I/A-7071 | 281.01 | Analog Input |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 4-20 mA | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TS_I/B-7071 | 281.01 | Analog Input |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 4-20 mA | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TS_I/C-7071 | 281.01 | Analog Input |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 4-20 mA | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | FZL_I-2061 | 281.02 | Digital Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | On/Off | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FZL_I-2072 | 281.02 | Digital Input |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | On/Off | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FZL_I-2079 | 281.02 | Digital Input |  | P09 |  | 3"-HG-20-110-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | On/Off | [30 empty] | F | 2079 |  | FIC-2079
S-02115 | FZL_I-2091 | 281.02 | Digital Input |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | On/Off | [30 empty] | F | 2091 |  | FIC-2091
S-02115 | FZL_I-2150 | 281.02 | Digital Input |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | On/Off | [30 empty] | F | 2150 |  | FIC-2150
S-02115 | FZL_I-2536 | 281.02 | Digital Input |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | On/Off | [30 empty] | F | 2536 |  | FIC-2536
S-02115 | FZL_I-3171 | 281.02 | Digital Input |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | On/Off | [30 empty] | F | 3171 |  | FIC-3171
S-02115 | HS_I-2095 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | H | 2095 |  | HS-2095
S-02115 | HZH_I-2098 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | H | 2098 |  | HS-2098
S-02115 | HZL_I-2098 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | H | 2098 |  | HS-2098
S-02115 | HZL_I1-2225 | 281.02 | Digital Input |  | P13 | [10 empty] | °C | On/Off | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | HZL_I2-2225 | 281.02 | Digital Input |  | P13 | [10 empty] | °C | On/Off | [30 empty] | H | 2225 |  | HIC-2225
S-02115 | HS_I-2544 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | H | 2544 |  | HS-2544
S-02115 | LZL_I-2403 | 281.02 | Digital Input |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | On/Off | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LZL_IA-3161 | 281.02 | Digital Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | On/Off | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LZL_IB-3161 | 281.02 | Digital Input |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | On/Off | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LZL_I-5501 | 281.02 | Digital Input |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | On/Off | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | PZL_I-2073 | 281.02 | Digital Input |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | On/Off | I-20 | [29 empty] | P | 2073 |  | PIC-2073
S-02115 | UZH_I-1001 | 281.02 | Digital Input |  | P01 | [10 empty] | °C | On/Off | [30 empty] | U | 1001 |  | USY-1001
S-02115 | UZL_I-1001 | 281.02 | Digital Input |  | P01 | [10 empty] | °C | On/Off | [30 empty] | U | 1001 |  | USY-1001
S-02115 | UZH_I-2010 | 281.02 | Digital Input |  | P02 | [10 empty] | °C | On/Off | [30 empty] | U | 2010 |  | USY-2010
S-02115 | UZL_I-2010 | 281.02 | Digital Input |  | P02 | [10 empty] | °C | On/Off | [30 empty] | U | 2010 |  | USY-2010
S-02115 | UZH_I-2021 | 281.02 | Digital Input |  | P02 | [10 empty] | °C | On/Off | [30 empty] | U | 2021 |  | USY-2021
S-02115 | UZL_I-2021 | 281.02 | Digital Input |  | P02 | [10 empty] | °C | On/Off | [30 empty] | U | 2021 |  | USY-2021
S-02115 | UZH_I-2038 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2038 |  | USY-2038
S-02115 | UZL_I-2038 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2038 |  | USY-2038
S-02115 | UZH_I-2043 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2043 |  | USY-2043
S-02115 | UZL_I-2043 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2043 |  | USY-2043
S-02115 | UZH_I-2045 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2045 |  | USY-2045
S-02115 | UZL_I-2045 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2045 |  | USY-2045
S-02115 | UZH_I-2048 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2048 |  | USY-2048
S-02115 | UZL_I-2048 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2048 |  | USY-2048
S-02115 | UZH_I-2049 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2049 |  | USY-2049
S-02115 | UZL_I-2049 | 281.02 | Digital Input |  | P03 | [10 empty] | °C | On/Off | [30 empty] | U | 2049 |  | USY-2049
S-02115 | UZH_I-2092 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | U | 2092 |  | USY-2092
S-02115 | UZL_I-2092 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | U | 2092 |  | USY-2092
S-02115 | UZH_I-2093 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | U | 2093 |  | USY-2093
S-02115 | UZL_I-2093 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | U | 2093 |  | USY-2093
S-02115 | UZH_I-2094 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | U | 2094 |  | USY-2094
S-02115 | UZL_I-2094 | 281.02 | Digital Input |  | P10 | [10 empty] | °C | On/Off | [30 empty] | U | 2094 |  | USY-2094
S-02115 | UZH_I-2117 | 281.02 | Digital Input |  | P11 | [10 empty] | °C | On/Off | [30 empty] | U | 2117 |  | USY-2117
S-02115 | UZL_I-2117 | 281.02 | Digital Input |  | P11 | [10 empty] | °C | On/Off | [30 empty] | U | 2117 |  | USY-2117
S-02115 | US_I-2118 | 281.02 | Digital Input |  | P11 | [10 empty] | °C | On/Off | [30 empty] | U | 2118 |  | USY-2118
S-02115 | UZH_I-2166 | 281.02 | Digital Input |  | P12 | [10 empty] | °C | On/Off | [30 empty] | U | 2166 |  | USY-2166
S-02115 | UZL_I-2166 | 281.02 | Digital Input |  | P12 | [10 empty] | °C | On/Off | [30 empty] | U | 2166 |  | USY-2166
S-02115 | US_I-2169 | 281.02 | Digital Input |  | P12 | [10 empty] | °C | On/Off | [30 empty] | U | 2169 |  | USY-2169
S-02115 | UZH_I-2381 | 281.02 | Digital Input |  | P18 | [10 empty] | °C | On/Off | [30 empty] | U | 2381 |  | USY-2381
S-02115 | UZL_I-2381 | 281.02 | Digital Input |  | P18 | [10 empty] | °C | On/Off | [30 empty] | U | 2381 |  | USY-2381
S-02115 | UZH_I-2482 | 281.02 | Digital Input |  | P21 | [10 empty] | °C | On/Off | [30 empty] | U | 2482 |  | USY-2482
S-02115 | UZL_I-2482 | 281.02 | Digital Input |  | P21 | [10 empty] | °C | On/Off | [30 empty] | U | 2482 |  | USY-2482
S-02115 | UZH_I-2541 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2541 |  | USY-2541
S-02115 | UZL_I-2541 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2541 |  | USY-2541
S-02115 | UZH_I-2542 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2542 |  | USY-2542
S-02115 | UZL_I-2542 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2542 |  | USY-2542
S-02115 | UZH_I-2543 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2543 |  | USY-2543
S-02115 | UZL_I-2543 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2543 |  | USY-2543
S-02115 | UZH_I-2544 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2544 |  | USY-2544
S-02115 | UZL_I-2544 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2544 |  | USY-2544
S-02115 | UZH_I-2545 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2545 |  | USY-2545
S-02115 | UZL_I-2545 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2545 |  | USY-2545
S-02115 | UZH_I-2547 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2547 |  | USY-2547
S-02115 | UZL_I-2547 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2547 |  | USY-2547
S-02115 | UZH_I-2548 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2548 |  | USY-2548
S-02115 | UZL_I-2548 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2548 |  | USY-2548
S-02115 | UZH_I-2549 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2549 |  | USY-2549
S-02115 | UZL_I-2549 | 281.02 | Digital Input |  | U01 | [10 empty] | °C | On/Off | [30 empty] | U | 2549 |  | USY-2549
S-02115 | UZH_I-3018 | 281.02 | Digital Input |  | P22 | [10 empty] | °C | On/Off | [30 empty] | U | 3018 |  | USY-3018
S-02115 | UZL_I-3018 | 281.02 | Digital Input |  | P22 | [10 empty] | °C | On/Off | [30 empty] | U | 3018 |  | USY-3018
S-02115 | UZH_I-3052 | 281.02 | Digital Input |  | P23 | [10 empty] | °C | On/Off | [30 empty] | U | 3052 |  | USY-3052
S-02115 | UZL_I-3052 | 281.02 | Digital Input |  | P23 | [10 empty] | °C | On/Off | [30 empty] | U | 3052 |  | USY-3052
S-02115 | UZH_I-3172 | 281.02 | Digital Input |  | P27 | [10 empty] | °C | On/Off | [30 empty] | U | 3172 |  | USY-3172
S-02115 | UZL_I-3172 | 281.02 | Digital Input |  | P27 | [10 empty] | °C | On/Off | [30 empty] | U | 3172 |  | USY-3172
S-02115 | UZH_I-5302 | 281.02 | Digital Input |  | P39 | [10 empty] | °C | On/Off | [30 empty] | U | 5302 |  | USY-5302
S-02115 | UZL_I-5302 | 281.02 | Digital Input |  | P39 | [10 empty] | °C | On/Off | [30 empty] | U | 5302 |  | USY-5302
S-02115 | UZH_I-5391 | 281.02 | Digital Input |  | P43 | [10 empty] | °C | On/Off | [30 empty] | U | 5391 |  | USY-5391
S-02115 | UZL_I-5391 | 281.02 | Digital Input |  | P43 | [10 empty] | °C | On/Off | [30 empty] | U | 5391 |  | USY-5391
S-02115 | UZH_I-5392 | 281.02 | Digital Input |  | P43 | [10 empty] | °C | On/Off | [30 empty] | U | 5392 |  | USY-5392
S-02115 | UZL_I-5392 | 281.02 | Digital Input |  | P43 | [10 empty] | °C | On/Off | [30 empty] | U | 5392 |  | USY-5392
S-02115 | UZH_I-5393 | 281.02 | Digital Input |  | P43 | [10 empty] | °C | On/Off | [30 empty] | U | 5393 |  | USY-5393
S-02115 | UZL_I-5393 | 281.02 | Digital Input |  | P43 | [10 empty] | °C | On/Off | [30 empty] | U | 5393 |  | USY-5393
S-02115 | UZH_I-5420 | 281.02 | Digital Input |  | P44 | [10 empty] | °C | On/Off | [30 empty] | U | 5420 |  | USY-5420
S-02115 | UZL_I-5420 | 281.02 | Digital Input |  | P44 | [10 empty] | °C | On/Off | [30 empty] | U | 5420 |  | USY-5420
S-02115 | UZH_I-5421 | 281.02 | Digital Input |  | P44 | [10 empty] | °C | On/Off | [30 empty] | U | 5421 |  | USY-5421
S-02115 | UZL_I-5421 | 281.02 | Digital Input |  | P44 | [10 empty] | °C | On/Off | [30 empty] | U | 5421 |  | USY-5421
S-02115 | UZH_I-5422 | 281.02 | Digital Input |  | P44 | [10 empty] | °C | On/Off | [30 empty] | U | 5422 |  | USY-5422
S-02115 | UZL_I-5422 | 281.02 | Digital Input |  | P44 | [10 empty] | °C | On/Off | [30 empty] | U | 5422 |  | USY-5422
S-02115 | UZH_I-6081 | 281.02 | Digital Input |  | P08 | [10 empty] | °C | On/Off | [30 empty] | U | 6081 |  | USY-6081
S-02115 | UZL_I-6081 | 281.02 | Digital Input |  | P08 | [10 empty] | °C | On/Off | [30 empty] | U | 6081 |  | USY-6081
S-02115 | UZH_I-6082 | 281.02 | Digital Input |  | P08 | [10 empty] | °C | On/Off | [30 empty] | U | 6082 |  | USY-6082
S-02115 | UZL_I-6082 | 281.02 | Digital Input |  | P08 | [10 empty] | °C | On/Off | [30 empty] | U | 6082 |  | USY-6082
S-02115 | UZH_I-7130 | 281.02 | Digital Input |  | U10 | [10 empty] | °C | On/Off | [30 empty] | U | 7130 |  | USY-7130
S-02115 | UZL_I-7130 | 281.02 | Digital Input |  | U10 | [10 empty] | °C | On/Off | [30 empty] | U | 7130 |  | USY-7130
S-02115 | UZH_I-7135 | 281.02 | Digital Input |  | U10 | [10 empty] | °C | On/Off | [30 empty] | U | 7135 |  | USY-7135
S-02115 | UZL_I-7135 | 281.02 | Digital Input |  | U10 | [10 empty] | °C | On/Off | [30 empty] | U | 7135 |  | USY-7135
S-02115 | FUS_O-2061 | 281.04 | Digital Output |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | IS-1 | On/Off | [29 empty] | F | 2061 |  | FIC-2061
S-02115 | FUS_O-2091 | 281.04 | Digital Output |  | P10 |  | 12"-PRG-20-106-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | IS-1 | On/Off | [29 empty] | F | 2091 |  | FIC-2091
S-02115 | FUS_O-2150 | 281.04 | Digital Output |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | IS-1 | On/Off | [29 empty] | F | 2150 |  | FIC-2150
S-02115 | FUS_O-2536 | 281.04 | Digital Output |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | IS-14 | On/Off | [29 empty] | F | 2536 |  | FIC-2536
S-02115 | FUS_O-3171 | 281.04 | Digital Output |  | P27 |  | 6"-SG-30-139-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | IS-3 | On/Off | [29 empty] | F | 3171 |  | FIC-3171
S-02115 | FUS_O-5020 | 281.04 | Digital Output |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | IS-44 | [30 empty] | F | 5020 |  | FIC-5020
S-02115 | FUS_O-5107 | 281.04 | Digital Output |  | P32 |  | 2"-LOS-50-101-B24-P |  |  | 13 | 3.8 | bar g |  | 65 | 150 | °C | IS-51 | [30 empty] | F | 5107 |  | FIC-5107
S-02115 | FUS_O-5441 | 281.04 | Digital Output |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | IS-51 | On/Off | [29 empty] | F | 5441 |  | FIC-5441
S-02115 | FUS_O-6081 | 281.04 | Digital Output |  | P08 |  | 2"-BD-60-109-G40-H |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | IS-31, I-36 | On/Off | [29 empty] | F | 6081 |  | FIC-6081
S-02115 | FUS_O-6086 | 281.04 | Digital Output |  | P08 |  | 4"-BD-60-114-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | IS-31, I-36 | On/Off | [29 empty] | F | 6086 |  | FIC-6086
S-02115 | HS_O-2098 | 281.04 | Digital Output |  | P10 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | H | 2098 |  | HS-2098
S-02115 | LUS_O-2403 | 281.04 | Digital Output |  | P19 |  | D 2002 |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | IS-33 | [30 empty] | L | 2403 |  | LIC-2403
S-02115 | LUS_O-2441 | 281.04 | Digital Output |  | P20 |  | D 2004 |  |  | 29 | 25.6 | bar g |  | 138 | 200 | °C | IS-34 | On/Off | [29 empty] | L | 2441 |  | LIC-2441
S-02115 | LUS_O-2474 | 281.04 | Digital Output |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | IS-35 | On/Off | [29 empty] | L | 2474 |  | LIC-2474
S-02115 | LU_O/A-3161 | 281.04 | Digital Output |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | IS-42 | On/Off | [29 empty] | L | 3161 |  | LIC-3161
S-02115 | LU_O/B-3161 | 281.04 | Digital Output |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | IS-42 | On/Off | [29 empty] | L | 3161 |  | LIC-3161
S-02115 | LUS_O-3192 | 281.04 | Digital Output |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | IS-43, IS-44 | On/Off | [29 empty] | L | 3192 |  | LIC-3192
S-02115 | LUS_O-5070 | 281.04 | Digital Output |  | P31 |  | D 5009 |  |  | 10.5 | 2.4 | bar g |  | 138 | 190 | °C | IS-55 | On/Off | [29 empty] | L | 5070 |  | LIC-5070
S-02115 | LUS_O-5501 | 281.04 | Digital Output |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | IS-67 | On/Off | [29 empty] | L | 5501 |  | LIC-5501
S-02115 | LUS_O-6021 | 281.04 | Digital Output |  | P06 |  | T 6001 1 Bottom |  |  | 55 | 42.8 | bar g |  | 226 | 300 | °C | IS-30 | [30 empty] | L | 6021 |  | LIC-6021
S-02115 | PUS_O-2073 | 281.04 | Digital Output |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | IS-2 | On/Off | [29 empty] | P | 2073 |  | PIC-2073
S-02115 | PUS_O-5069 | 281.04 | Digital Output |  | P31 |  | 14"-LPS-50-103-D24-H |  |  | 9.5 | 2.4 | bar g |  | 187 | 340 | °C | IS-4 | On/Off | [29 empty] | P | 5069 |  | PIC-5069
S-02115 | US_O-1001 | 281.04 | Digital Output |  | P01 | [10 empty] | °C | IS-5 | On/Off | [29 empty] | U | 1001 |  | USY-1001
S-02115 | US_O-2010 | 281.04 | Digital Output |  | P02 | [10 empty] | °C | IS-2 | On/Off | [29 empty] | U | 2010 |  | USY-2010
S-02115 | US_O-2021 | 281.04 | Digital Output |  | P02 | [10 empty] | °C | IS-2 | On/Off | [29 empty] | U | 2021 |  | USY-2021
S-02115 | US_O-2038 | 281.04 | Digital Output |  | P03 | [10 empty] | °C | IS-21 | On/Off | [29 empty] | U | 2038 |  | USY-2038
S-02115 | US_O-2043 | 281.04 | Digital Output |  | P03 | [10 empty] | °C | IS-2 | On/Off | [29 empty] | U | 2043 |  | USY-2043
S-02115 | US_O-2045 | 281.04 | Digital Output |  | P03 | [10 empty] | °C | IS-2 | On/Off | [29 empty] | U | 2045 |  | USY-2045
S-02115 | US_O-2048 | 281.04 | Digital Output |  | P03 | [10 empty] | °C | IS-2 | On/Off | [29 empty] | U | 2048 |  | USY-2048
S-02115 | US_O-2049 | 281.04 | Digital Output |  | P03 | [10 empty] | °C | IS-2 | On/Off | [29 empty] | U | 2049 |  | USY-2049
S-02115 | US_O-2092 | 281.04 | Digital Output |  | P10 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2092 |  | USY-2092
S-02115 | US_O-2093 | 281.04 | Digital Output |  | P10 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2093 |  | USY-2093
S-02115 | US_O-2094 | 281.04 | Digital Output |  | P10 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2094 |  | USY-2094
S-02115 | US_O-2117 | 281.04 | Digital Output |  | P11 | [10 empty] | °C | IS-11 | On/Off | [29 empty] | U | 2117 |  | USY-2117
S-02115 | USY-2122 | 281.04 | Digital Output |  | P11 | [10 empty] | °C | IS-10 | On/Off | [29 empty] | U | 2122 |  | USY-2122
S-02115 | USY-2123 | 281.04 | Digital Output |  | P11 | [10 empty] | °C | IS-11 | On/Off | [29 empty] | U | 2123 |  | USY-2123
S-02115 | USY-2157 | 281.04 | Digital Output |  | P12 | [10 empty] | °C | IS-12 | On/Off | [29 empty] | U | 2157 |  | USY-2157
S-02115 | USY-2158 | 281.04 | Digital Output |  | P12 | [10 empty] | °C | IS-13 | On/Off | [29 empty] | U | 2158 |  | USY-2158
S-02115 | US_O-2166 | 281.04 | Digital Output |  | P12 | [10 empty] | °C | IS-13 | On/Off | [29 empty] | U | 2166 |  | USY-2166
S-02115 | US_O-2381 | 281.04 | Digital Output |  | P18 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2381 |  | USY-2381
S-02115 | USY-2409 | 281.04 | Digital Output |  | P19 | [10 empty] | °C | IS-33 | [30 empty] | U | 2409 |  | USY-2409
S-02115 | USY-2413 | 281.04 | Digital Output |  | P19 | [10 empty] | °C | IS-33 | [30 empty] | U | 2413 |  | USY-2413
S-02115 | USY-2446 | 281.04 | Digital Output |  | P20 | [10 empty] | °C | IS-34 | On/Off | [29 empty] | U | 2446 |  | USY-2446
S-02115 | USY-2450 | 281.04 | Digital Output |  | P20 | [10 empty] | °C | IS-34 | On/Off | [29 empty] | U | 2450 |  | USY-2450
S-02115 | US_O-2482 | 281.04 | Digital Output |  | P21 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2482 |  | USY-2482
S-02115 | USY-2486 | 281.04 | Digital Output |  | P21 | [10 empty] | °C | IS-35 | On/Off | [29 empty] | U | 2486 |  | USY-2486
S-02115 | USY-2490 | 281.04 | Digital Output |  | P21 | [10 empty] | °C | IS-35 | On/Off | [29 empty] | U | 2490 |  | USY-2490
S-02115 | US_O-2541 | 281.04 | Digital Output |  | U01 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2541 |  | USY-2541
S-02115 | US_O-2542 | 281.04 | Digital Output |  | U01 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2542 |  | USY-2542
S-02115 | US_O-2543 | 281.04 | Digital Output |  | U01 | [10 empty] | °C | IS-1 | On/Off | [29 empty] | U | 2543 |  | USY-2543
S-02115 | US_O-2544 | 281.04 | Digital Output |  | U01 | [10 empty] | °C | IS-14 | On/Off | [29 empty] | U | 2544 |  | USY-2544
S-02115 | US_O-2545 | 281.04 | Digital Output |  | U01 | [10 empty] | °C | IS-14 | On/Off | [29 empty] | U | 2545 |  | USY-2545
S-02115 | US_O-2547 | 281.04 | Digital Output |  | U01 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2547 |  | USY-2547
S-02115 | US_O-2548 | 281.04 | Digital Output |  | U01 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2548 |  | USY-2548
S-02115 | US_O-2549 | 281.04 | Digital Output |  | U01 | [10 empty] | °C |  | On/Off | [29 empty] | U | 2549 |  | USY-2549
S-02115 | US_O-3018 | 281.04 | Digital Output |  | P22 | [10 empty] | °C | IS-3 | On/Off | [29 empty] | U | 3018 |  | USY-3018
S-02115 | US_O-3052 | 281.04 | Digital Output |  | P23 | [10 empty] | °C | IS-3 | On/Off | [29 empty] | U | 3052 |  | USY-3052
S-02115 | US_O-3172 | 281.04 | Digital Output |  | P27 | [10 empty] | °C | IS-42 | On/Off | [29 empty] | U | 3172 |  | USY-3172
S-02115 | USY-5012 | 281.04 | Digital Output |  | P29 | [10 empty] | °C | IS-53 | [30 empty] | U | 5012 |  | USY-5012
S-02115 | USY-5016 | 281.04 | Digital Output |  | P29 | [10 empty] | °C | IS-53 | [30 empty] | U | 5016 |  | USY-5016
S-02115 | USY-5076 | 281.04 | Digital Output |  | P31 | [10 empty] | °C | IS-55 | [30 empty] | U | 5076 |  | USY-5076
S-02115 | USY-5080 | 281.04 | Digital Output |  | P31 | [10 empty] | °C | IS-55 | [30 empty] | U | 5080 |  | USY-5080
S-02115 | USY-5100 | 281.04 | Digital Output |  | P32 | [10 empty] | °C | IS-56 | On/Off | [29 empty] | U | 5100 |  | USY-5100
S-02115 | USY-5104 | 281.04 | Digital Output |  | P32 | [10 empty] | °C | IS-56 | On/Off | [29 empty] | U | 5104 |  | USY-5104
S-02115 | USY-5132 | 281.04 | Digital Output |  | P33 | [10 empty] | °C | IS-54 | On/Off | [29 empty] | U | 5132 |  | USY-5132
S-02115 | USY-5136 | 281.04 | Digital Output |  | P33 | [10 empty] | °C | IS-54 | [30 empty] | U | 5136 |  | USY-5136
S-02115 | USY-5211 | 281.04 | Digital Output |  | P36 | [10 empty] | °C | IS-58 | On/Off | [29 empty] | U | 5211 |  | USY-5211
S-02115 | USY-5215 | 281.04 | Digital Output |  | P36 | [10 empty] | °C | IS-58 | On/Off | [29 empty] | U | 5215 |  | USY-5215
S-02115 | USY-5232 | 281.04 | Digital Output |  | P37 | [10 empty] | °C | IS-57 | On/Off | [29 empty] | U | 5232 |  | USY-5232
S-02115 | USY-5236 | 281.04 | Digital Output |  | P37 | [10 empty] | °C | IS-57 | On/Off | [29 empty] | U | 5236 |  | USY-5236
S-02115 | US_O-5302 | 281.04 | Digital Output |  | P39 | [10 empty] | °C | IS-4 | On/Off | [29 empty] | U | 5302 |  | USY-5302
S-02115 | USY-5328 | 281.04 | Digital Output |  | P40 | [10 empty] | °C | IS-60 | On/Off | [29 empty] | U | 5328 |  | USY-5328
S-02115 | USY-5332 | 281.04 | Digital Output |  | P40 | [10 empty] | °C | IS-60 | On/Off | [29 empty] | U | 5332 |  | USY-5332
S-02115 | USY-5352 | 281.04 | Digital Output |  | P41 | [10 empty] | °C | IS-59 | On/Off | [29 empty] | U | 5352 |  | USY-5352
S-02115 | USY-5356 | 281.04 | Digital Output |  | P41 | [10 empty] | °C | IS-59 | On/Off | [29 empty] | U | 5356 |  | USY-5356
S-02115 | USY-5360 | 281.04 | Digital Output |  | P41 | [10 empty] | °C | IS-59 (IS-67 alt. option) | On/Off | [29 empty] | U | 5360 |  | USY-5360
S-02115 | USY-5364 | 281.04 | Digital Output |  | P41 | [10 empty] | °C | IS-59 (IS-67 alt. option) | On/Off | [29 empty] | U | 5364 |  | USY-5364
S-02115 | US_O-5391 | 281.04 | Digital Output |  | P43 | [10 empty] | °C | IS-62, IS-63 | On/Off | [29 empty] | U | 5391 |  | USY-5391
S-02115 | US_O-5392 | 281.04 | Digital Output |  | P43 | [10 empty] | °C | IS-62, IS-63 | On/Off | [29 empty] | U | 5392 |  | USY-5392
S-02115 | US_O-5393 | 281.04 | Digital Output |  | P43 | [10 empty] | °C | IS-62, IS-63 | On/Off | [29 empty] | U | 5393 |  | USY-5393
S-02115 | USY-5403 | 281.04 | Digital Output |  | P43 | [10 empty] | °C | IS-1, IS-66 | [30 empty] | U | 5403 |  | USY-5403
S-02115 | US_O-5420 | 281.04 | Digital Output |  | P44 | [10 empty] | °C | IS-64, IS-65 | On/Off | [29 empty] | U | 5420 |  | USY-5420
S-02115 | US_O-5421 | 281.04 | Digital Output |  | P44 | [10 empty] | °C | IS-62, IS-63 | On/Off | [29 empty] | U | 5421 |  | USY-5421
S-02115 | US_O-5422 | 281.04 | Digital Output |  | P44 | [10 empty] | °C | IS-64, IS-65 | On/Off | [29 empty] | U | 5422 |  | USY-5422
S-02115 | USY-5424 | 281.04 | Digital Output |  | P44 | [10 empty] | °C | IS-66 | On/Off | [29 empty] | U | 5424 |  | USY-5424
S-02115 | USY-5428 | 281.04 | Digital Output |  | P44 | [10 empty] | °C | IS-66 | On/Off | [29 empty] | U | 5428 |  | USY-5428
S-02115 | USY-5454 | 281.04 | Digital Output |  | P45 | [10 empty] | °C | IS-1, I-52 | On/Off | [29 empty] | U | 5454 |  | USY-5454
S-02115 | USY-5458 | 281.04 | Digital Output |  | P45 | [10 empty] | °C | IS-1, I-52 | [30 empty] | U | 5458 |  | USY-5458
S-02115 | USY-6003 | 281.04 | Digital Output |  | P05 | [10 empty] | °C | IS-30 | [30 empty] | U | 6003 |  | USY-6003
S-02115 | USY-6007 | 281.04 | Digital Output |  | P05 | [10 empty] | °C | IS-30 | [30 empty] | U | 6007 |  | USY-6007
S-02115 | USY-6061 | 281.04 | Digital Output |  | P07 | [10 empty] | °C | IS-31 | [30 empty] | U | 6061 |  | USY-6061
S-02115 | USY-6065 | 281.04 | Digital Output |  | P07 | [10 empty] | °C | IS-31 | [30 empty] | U | 6065 |  | USY-6065
S-02115 | US_O-6081 | 281.04 | Digital Output |  | P08 | [10 empty] | °C | IS-31, I-36 | On/Off | [29 empty] | U | 6081 |  | USY-6081
S-02115 | US_O-6082 | 281.04 | Digital Output |  | P08 | [10 empty] | °C | IS-31, I-36 | On/Off | [29 empty] | U | 6082 |  | USY-6082
S-02115 | US_O-7130 | 281.04 | Digital Output |  | U10 | [10 empty] | °C | IS-71 | On/Off | [29 empty] | U | 7130 |  | USY-7130
S-02115 | US_O-7135 | 281.04 | Digital Output |  | U10 | [10 empty] | °C | IS-72 | On/Off | [29 empty] | U | 7135 |  | USY-7135
S-02115 | AS_R/A-1001 | 281.09 | Repeater Isolator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | DCS | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AS_R/B-1001 | 281.09 | Repeater Isolator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | DCS | [30 empty] | A | 1001 |  | AI-1001
S-02115 | AS_R/C-1001 | 281.09 | Repeater Isolator |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | DCS | [30 empty] | A | 1001 |  | AI-1001
S-02115 | FS_R/A-2007 | 281.09 | Repeater Isolator |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | DCS | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FS_R/B-2007 | 281.09 | Repeater Isolator |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | DCS | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FS_R/C-2007 | 281.09 | Repeater Isolator |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | DCS | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FS_R/A-2040 | 281.09 | Repeater Isolator |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | DCS | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FS_R/B-2040 | 281.09 | Repeater Isolator |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | DCS | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FS_R/C-2040 | 281.09 | Repeater Isolator |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | DCS | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FS_R/A-2061 | 281.09 | Repeater Isolator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | DCS | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FS_R/B-2061 | 281.09 | Repeater Isolator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | DCS | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FS_R/C-2061 | 281.09 | Repeater Isolator |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | DCS | [30 empty] | F | 2061 |  | FIC-2061
S-02115 | FS_R/A-2072 | 281.09 | Repeater Isolator |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | DCS | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FS_R/B-2072 | 281.09 | Repeater Isolator |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | DCS | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FS_R/C-2072 | 281.09 | Repeater Isolator |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | DCS | [30 empty] | F | 2072 |  | FIC-2072
S-02115 | FS_R/A-2233 | 281.09 | Repeater Isolator |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | DCS | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FS_R/B-2233 | 281.09 | Repeater Isolator |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | DCS | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FS_R/C-2233 | 281.09 | Repeater Isolator |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | DCS | [30 empty] | F | 2233 |  | FIC-2233
S-02115 | FS_R/A-6070 | 281.09 | Repeater Isolator |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | DCS | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FS_R/B-6070 | 281.09 | Repeater Isolator |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | DCS | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | FS_R/C-6070 | 281.09 | Repeater Isolator |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | DCS | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | LS_R/A-2372 | 281.09 | Repeater Isolator |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | DCS | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LS_R/B-2372 | 281.09 | Repeater Isolator |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | DCS | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LS_R/C-2372 | 281.09 | Repeater Isolator |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | DCS | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LS_R/A-2474 | 281.09 | Repeater Isolator |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | DCS | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LS_R/B-2474 | 281.09 | Repeater Isolator |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | DCS | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LS_R/C-2474 | 281.09 | Repeater Isolator |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | DCS | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LS_R/A-3042 | 281.09 | Repeater Isolator |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | DCS | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LS_R/B-3042 | 281.09 | Repeater Isolator |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | DCS | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LS_R/C-3042 | 281.09 | Repeater Isolator |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | DCS | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LS_R/A-3161 | 281.09 | Repeater Isolator |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | DCS | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LS_R/B-3161 | 281.09 | Repeater Isolator |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | DCS | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LS_R/C-3161 | 281.09 | Repeater Isolator |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | DCS | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LS_R/A-3192 | 281.09 | Repeater Isolator |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | DCS | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LS_R/B-3192 | 281.09 | Repeater Isolator |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | DCS | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LS_R/C-3192 | 281.09 | Repeater Isolator |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | DCS | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LS_R/A-5501 | 281.09 | Repeater Isolator |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | DCS | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LS_R/B-5501 | 281.09 | Repeater Isolator |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | DCS | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LS_R/C-5501 | 281.09 | Repeater Isolator |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | DCS | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LS_R/A-6051 | 281.09 | Repeater Isolator |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | DCS | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LS_R/B-6051 | 281.09 | Repeater Isolator |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | DCS | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LS_R/C-6051 | 281.09 | Repeater Isolator |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | DCS | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LS_R/A-7091 | 281.09 | Repeater Isolator |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | DCS | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | LS_R/B-7091 | 281.09 | Repeater Isolator |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | DCS | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | LS_R/C-7091 | 281.09 | Repeater Isolator |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | DCS | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | PS_R/A-2163 | 281.09 | Repeater Isolator |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | DCS | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PS_R/B-2163 | 281.09 | Repeater Isolator |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | DCS | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PS_R/C-2163 | 281.09 | Repeater Isolator |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | DCS | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PS_R/A-2224 | 281.09 | Repeater Isolator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | DCS | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PS_R/B-2224 | 281.09 | Repeater Isolator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | DCS | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PS_R/C-2224 | 281.09 | Repeater Isolator |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | DCS | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PS_R/A-2372 | 281.09 | Repeater Isolator |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | DCS | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PS_R/B-2372 | 281.09 | Repeater Isolator |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | DCS | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PS_R/C-2372 | 281.09 | Repeater Isolator |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | DCS | [30 empty] | P | 2372 |  | PI-2372
S-02115 | PS_R/A-2554 | 281.09 | Repeater Isolator |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | DCS | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PS_R/B-2554 | 281.09 | Repeater Isolator |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | DCS | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PS_R/C-2554 | 281.09 | Repeater Isolator |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | DCS | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PS_R/A-3042 | 281.09 | Repeater Isolator |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | DCS | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PS_R/B-3042 | 281.09 | Repeater Isolator |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | DCS | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PS_R/C-3042 | 281.09 | Repeater Isolator |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | DCS | [30 empty] | P | 3042 |  | PIC-3042
S-02115 | PS_R/A-5207 | 281.09 | Repeater Isolator |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | DCS | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PS_R/B-5207 | 281.09 | Repeater Isolator |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | DCS | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | PS_R/C-5207 | 281.09 | Repeater Isolator |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | DCS | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | TS_R/A-2335 | 281.09 | Repeater Isolator |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | DCS | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TS_R/B-2335 | 281.09 | Repeater Isolator |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | DCS | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TS_R/C-2335 | 281.09 | Repeater Isolator |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | DCS | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TS_R/A-2336 | 281.09 | Repeater Isolator |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | DCS | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TS_R/B-2336 | 281.09 | Repeater Isolator |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | DCS | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TS_R/C-2336 | 281.09 | Repeater Isolator |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | DCS | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TS_R/A-2360 | 281.09 | Repeater Isolator |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | DCS | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TS_R/B-2360 | 281.09 | Repeater Isolator |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | DCS | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TS_R/C-2360 | 281.09 | Repeater Isolator |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | DCS | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TS_R/A-7071 | 281.09 | Repeater Isolator |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | DCS | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TS_R/B-7071 | 281.09 | Repeater Isolator |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | DCS | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | TS_R/C-7071 | 281.09 | Repeater Isolator |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | DCS | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | ASY-1001 | 281.6 | Calculation |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 2oo3 Voting | [30 empty] | A | 1001 |  | AI-1001
S-02115 | FSY-2007 | 281.6 | Calculation |  | P02 |  | 10"-PO-20-106-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 2oo3 Voting | [30 empty] | F | 2007 |  | FIC-2007
S-02115 | FFSY-2008 | 281.6 | Calculation |  | P02 | [10 empty] | °C |  | FSY-2063, FSY-2007 | [29 empty] | F | 2008 |  | FFSAH-2008
S-02115 | FSY-2040 | 281.6 | Calculation |  | P03 |  | 4"-HPS-20-108-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 2oo3 Voting | [30 empty] | F | 2040 |  | FIC-2040
S-02115 | FSY-2061 | 281.6 | Calculation |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 2oo3 Voting |  |  | FSY-2062 | [27 empty] | F | 2061 |  | FIC-2061
S-02115 | FSY-2062 | 281.6 | Calculation |  | P09 | [10 empty] | °C | Addition/Subtraction | FSY-6070, FSY-2061, FSY-2072 | FSY-2233 | FFSY-2064 | [27 empty] | F | 2062 |  | FSAL-2062
S-02115 | FSY-2063 | 281.6 | Calculation |  | P09 | [10 empty] | °C | Multiplier | HSIC-2063, FSY-6070 |  | FFSY-2008, FFSY-2064 | [27 empty] | F | 2063 |  | FSY-2063
S-02115 | FFSY-2064 | 281.6 | Calculation |  | P09 | [10 empty] | °C | Division | FSY-2062, FSY-2063 | [29 empty] | F | 2064 |  | FFSAL-2064
S-02115 | FSY-2072 | 281.6 | Calculation |  | P09 |  | 12"-HPS-70-125-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 2oo3 Voting |  |  | FSY-2062 | [27 empty] | F | 2072 |  | FIC-2072
S-02115 | FSY-2233 | 281.6 | Calculation |  | P13 |  | 3"-PRC-20-102-G40-N |  |  | 80 | 52 | bar g |  | 49 | 106 | °C | 2oo3 Voting |  |  | FSY-2062 | [27 empty] | F | 2233 |  | FIC-2233
S-02115 | FSY-2582 | 281.6 | Calculation |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | P comp | PST-2582 | [29 empty] | F | 2582 |  | FI-2582
S-02115 | FSY-6070 | 281.6 | Calculation |  | P07 |  | 16"-PRG-60-110-F24-H |  |  | 55 | 43.8 | bar g |  | 358 | 410 | °C | 2oo3 Voting | [30 empty] | F | 6070 |  | FIC-6070
S-02115 | LSY-1004 | 281.6 | Calculation |  | P01 |  | D 1001 |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 2oo3 Voting | [30 empty] | L | 1004 |  | LI-1004
S-02115 | LSY/1-2372 | 281.6 | Calculation |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 2oo3 Voting | [30 empty] | L | 2372 |  | LIC-2372
S-02115 | LSY/2-2372 | 281.6 | Calculation |  | P18 |  | D 2001 Bottom |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Density Compensation | PSY-2372 | [29 empty] | L | 2372 |  | LIC-2372
S-02115 | LSY-2474 | 281.6 | Calculation |  | P21 |  | D 2005 |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 2oo3 Voting | [30 empty] | L | 2474 |  | LIC-2474
S-02115 | LSY/1-3042 | 281.6 | Calculation |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 2oo3 Voting | [30 empty] | L | 3042 |  | LIC-3042
S-02115 | LSY/2-3042 | 281.6 | Calculation |  | P23 |  | D 3003 Bottom |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | Density Compensation | PSY-3042 | [29 empty] | L | 3042 |  | LIC-3042
S-02115 | LSY-3161 | 281.6 | Calculation |  | P27 |  | D 3001 |  |  | 99 | 83.7 | bar g |  | 48 | 100 | °C | 2oo3 Voting | [30 empty] | L | 3161 |  | LIC-3161
S-02115 | LSY-3192 | 281.6 | Calculation |  | P28 |  | D 3002 Bottom |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | 2oo3 Voting | [30 empty] | L | 3192 |  | LIC-3192
S-02115 | LSY-5501 | 281.6 | Calculation |  | U23B |  | D 5010 |  |  | 3.5 | 0 | bar g |  | 43 | 100 | °C | 2oo3 Voting | [30 empty] | L | 5501 |  | LIC-5501
S-02115 | LSY-6051 | 281.6 | Calculation |  | P07 |  | D 6001 |  |  | 55 | 49 | bar g |  | 226 | 290 | °C | 2oo3 Voting | [30 empty] | L | 6051 |  | LIC-6051
S-02115 | LSY-7091 | 281.6 | Calculation |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 2oo3 Voting | [30 empty] | L | 7091 |  | LIC-7091
S-02115 | PSY-2036 | 281.6 | Calculation |  | P03 |  | 4"-HPS-20-106-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 2oo3 Voting | [30 empty] | P | 2036 |  | PDI-2036
S-02115 | PSY-2163 | 281.6 | Calculation |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 2oo3 Voting | [30 empty] | P | 2163 |  | PIC-2163
S-02115 | PSY-2224 | 281.6 | Calculation |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 2oo3 Voting | [30 empty] | P | 2224 |  | PIC-2224
S-02115 | PSY-2372 | 281.6 | Calculation |  | P18 |  | D 2001 Top |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 2oo3 Voting |  |  | LSY-2372 2 | [27 empty] | P | 2372 |  | PI-2372
S-02115 | PSY-2554 | 281.6 | Calculation |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 2oo3 Voting | [30 empty] | P | 2554 |  | PIC-2554
S-02115 | PSY-2556 | 281.6 | Calculation |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 2oo3 Voting | [30 empty] | P | 2556 |  | PSAL-2556
S-02115 | PSY-3042 | 281.6 | Calculation |  | P23 |  | D 3003 Top |  |  | 45 | 33.7 | bar g |  | 242 | 290 | °C | 2oo3 Voting |  |  | LSY-3042/2 | [27 empty] | P | 3042 |  | PIC-3042
S-02115 | PSY-5207 | 281.6 | Calculation |  | P36 |  | D 5002 Top |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 2oo3 Voting | [30 empty] | P | 5207 |  | PIC-5207
S-02115 | TSY-2047 | 281.6 | Calculation |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 2oo3 Voting | [30 empty] | T | 2047 |  | TI-2047
S-02115 | TSY-2221 | 281.6 | Calculation |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 2oo3 Voting | [30 empty] | T | 2221 |  | TI-2221
S-02115 | TSY-2305 | 281.6 | Calculation |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 2oo3 Voting | [30 empty] | T | 2305 |  | TI-2305
S-02115 | TSY-2325 | 281.6 | Calculation |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C | 2oo3 Voting | [30 empty] | T | 2325 |  | TI-2325
S-02115 | TSY-2329 | 281.6 | Calculation |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 236 |  | °C | 2oo3 Voting | [30 empty] | T | 2329 |  | TI-2329
S-02115 | TSY-2333 | 281.6 | Calculation |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 2oo3 Voting | [30 empty] | T | 2333 |  | TI-2333
S-02115 | TSY-2334 | 281.6 | Calculation |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C | 2oo3 Voting | [30 empty] | T | 2334 |  | TI-2334
S-02115 | TSY-2335 | 281.6 | Calculation |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 2oo3 Voting | [30 empty] | T | 2335 |  | TIC-2335
S-02115 | TSY-2336 | 281.6 | Calculation |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C | 2oo3 Voting | [30 empty] | T | 2336 |  | TIC-2336
S-02115 | TSY-2360 | 281.6 | Calculation |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 2oo3 Voting | [30 empty] | T | 2360 |  | TIC-2360
S-02115 | TSY-3072 | 281.6 | Calculation |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 2oo3 Voting | [30 empty] | T | 3072 |  | TI-3072
S-02115 | TSY-3076 | 281.6 | Calculation |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 2oo3 Voting | [30 empty] | T | 3076 |  | TI-3076
S-02115 | TSY-3080 | 281.6 | Calculation |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C | 2oo3 Voting | [30 empty] | T | 3080 |  | TI-3080
S-02115 | TSY-7071 | 281.6 | Calculation |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 2oo3 Voting | [30 empty] | T | 7071 |  | TIC-7071
S-02115 | HSIC-2063 | 281.7 | Manual Input |  | P09 | [10 empty] | °C | 0.9-1.1 kmole/kmole | [30 empty] | H | 2063 |  | HSIC-2063
S-02115 | TW-1001 | 284 | Thermowell |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1001 |  | TI-1001
S-02115 | TW-1002 | 284 | Thermowell |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1002 |  | TG-1002
S-02115 | TW-1010 | 284 | Thermowell |  | P01 |  | 8"-NG-20-101-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1010 |  | TI-1010
S-02115 | TW-1012 | 284 | Thermowell |  | P01 |  | 24"-NG-20-102-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1012 |  | TI-1012
S-02115 | TW-1034 | 284 | Thermowell |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 600 mm |  | AISI 316 | [28 empty] | T | 1034 |  | TI-1034
S-02115 | TW-1035 | 284 | Thermowell |  | P04 |  | R 1001 |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 600 mm |  | AISI 316 | [28 empty] | T | 1035 |  | TI-1035
S-02115 | TW-1037 | 284 | Thermowell |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1037 |  | TI-1037
S-02115 | TW-1041 | 284 | Thermowell |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1041 |  | TI-1041
S-02115 | TW-1042 | 284 | Thermowell |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1042 |  | TI-1042
S-02115 | TW-1045 | 284 | Thermowell |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1045 |  | TI-1045
S-02115 | TW-1047 | 284 | Thermowell |  | P04 |  | 8"-FLG-10-113-B24-P |  |  | 5 |  | bar g |  |  | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 1047 |  | TI-1047
S-02115 | TW-2001 | 284 | Thermowell |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 125 mm |  | Monel | [28 empty] | T | 2001 |  | TI-2001
S-02115 | TW-2002 | 284 | Thermowell |  | P02 |  | 10"-PO-20-110-F50-N |  |  | 47 | 40 | bar g |  | 35 | 85 | °C | 125 mm |  | Monel | [28 empty] | T | 2002 |  | TG-2002
S-02115 | TW-2003 | 284 | Thermowell |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2003 |  | TI-2003
S-02115 | TW-2011 | 284 | Thermowell |  | P02 |  | 12"-PO-20-102-F70-N |  |  | 47 | 35 | bar g |  | 35 | 85 | °C | 125 mm |  | Monel | [28 empty] | T | 2011 |  | TG-2011
S-02115 | TW-2012 | 284 | Thermowell |  | P02 |  | 6"-HPS-20-102-F24-H |  |  | 52 | 43.5 | bar g |  | 272 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2012 |  | TG-2012
S-02115 | TW-2013 | 284 | Thermowell |  | P02 |  | 6"-HPC-20-101-F24-H |  |  | 53 | 43.5 | bar g |  | 257 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2013 |  | TG-2013
S-02115 | TW-2039 | 284 | Thermowell |  | P03 |  | 4"-HPS-20-109-F44-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2039 |  | TI-2039
S-02115 | TW-2044 | 284 | Thermowell |  | P03 |  | 6"-VA-20-104-F70-P |  |  | 45 |  | bar g |  |  | 255 | °C | 125 mm |  | Monel | [28 empty] | T | 2044 |  | TI-2044
S-02115 | TW-2046 | 284 | Thermowell |  | P03 |  | 18"-PO-20-116-F50-H |  |  | 47 | 34 | bar g |  | 236 | 270 | °C | 125 mm |  | Monel | [28 empty] | T | 2046 |  | TI-2046
S-02115 | TW/A-2047 | 284 | Thermowell |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 125 mm |  | Monel | [28 empty] | T | 2047 |  | TI-2047
S-02115 | TW/B-2047 | 284 | Thermowell |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 125 mm |  | Monel | [28 empty] | T | 2047 |  | TI-2047
S-02115 | TW/C-2047 | 284 | Thermowell |  | P03 |  | 16"-PO-20-114-F70-H |  |  | 47 | 34 | bar g |  | 230 | 255 | °C | 125 mm |  | Monel | [28 empty] | T | 2047 |  | TI-2047
S-02115 | TW-2050 | 284 | Thermowell |  | P03 |  | 2"-VA-20-101-F70-P |  |  | 4.5 |  | bar g |  |  | 255 | °C | 125 mm |  | Monel | [28 empty] | T | 2050 |  | TI-2050
S-02115 | TW-2061 | 284 | Thermowell |  | P09 |  | 24"-PRG-60-104-F24-H |  |  | 55 | 42.3 | bar g |  | 262 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2061 |  | TI-2061
S-02115 | TW-2074 | 284 | Thermowell |  | P09 |  | 24"-FLG-20-107-B24-P |  |  | 5 |  | bar g |  |  | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2074 |  | TI-2074
S-02115 | TW-2111 | 284 | Thermowell |  | P11 |  | CA |  |  |  | -3 | mbar g |  | 48 |  | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2111 |  | TI-2111
S-02115 | TW-2112 | 284 | Thermowell |  | P11 |  | Ducting |  |  |  | 21 | mbar g |  | 54 | 80 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2112 |  | TI-2112
S-02115 | TW-2116 | 284 | Thermowell |  | P11 |  | 8"-HPS-70-101-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2116 |  | TG-2116
S-02115 | TW-2120 | 284 | Thermowell |  | P11 |  | 16"-LPS-20-102-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2120 |  | TG-2120
S-02115 | TW-2148 | 284 | Thermowell |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2148 |  | TI-2148
S-02115 | TW-2149 | 284 | Thermowell |  | P12 |  | 16"-PRG-20-102-F24-P |  |  | 55 | 49.4 | bar g |  | 246 | 375 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2149 |  | TI-2149
S-02115 | TW-2150 | 284 | Thermowell |  | P12 |  | 3"-HG-20-112-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2150 |  | TI-2150
S-02115 | TW-2151 | 284 | Thermowell |  | P12 |  | 14"-NG-10-105-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2151 |  | TI-2151
S-02115 | TW-2161 | 284 | Thermowell |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2161 |  | TI-2161
S-02115 | TW-2162 | 284 | Thermowell |  | P12 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2162 |  | TI-2162
S-02115 | TW-2164 | 284 | Thermowell |  | P12 |  | 6"-HPS-70-111-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2164 |  | TG-2164
S-02115 | TW-2170 | 284 | Thermowell |  | P12 |  | 12"-LPS-20-106-D24-H |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2170 |  | TG-2170
S-02115 | TW-2220 | 284 | Thermowell |  | P13 |  | 16"-PRG-20-101-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2220 |  | TIC-2220
S-02115 | TW-2232 | 284 | Thermowell |  | P13 |  | 24"-PRG-20-112-F24-H |  |  | 46 | 42.1 | bar g |  | 267 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2232 |  | TIC-2232
S-02115 | TW-2234 | 284 | Thermowell |  | P13 |  | 34"-RFG-20-114-H44-H |  |  | 46 | 36.3 | bar g |  | 638 | 675 | °C | 125 mm |  | AISI 347H | [28 empty] | T | 2234 |  | TI-2234
S-02115 | TW-2253 | 284 | Thermowell |  | P14 |  | 30"-PRG-20-113-G36-H |  |  | 46 | 38.4 | bar g |  | 496 | 550 | °C | 125 mm |  | AISI 347H | [28 empty] | T | 2253 |  | TIC-2253
S-02115 | TW-2254 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2254 |  | TI-2254
S-02115 | TW-2255 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2255 |  | TI-2255
S-02115 | TW-2256 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2256 |  | TI-2256
S-02115 | TW-2257 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2257 |  | TI-2257
S-02115 | TW-2258 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2258 |  | TI-2258
S-02115 | TW-2259 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2259 |  | TI-2259
S-02115 | TW-2260 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2260 |  | TI-2260
S-02115 | TW-2261 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2261 |  | TI-2261
S-02115 | TW-2262 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2262 |  | TI-2262
S-02115 | TW-2263 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2263 |  | TI-2263
S-02115 | TW-2264 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2264 |  | TI-2264
S-02115 | TW-2265 | 284 | Thermowell |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C |  |  |  | Special | [27 empty] | T | 2265 |  | TI-2265
S-02115 | TW-2268 | 284 | Thermowell |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2268 |  | TI-2268
S-02115 | TW-2285 | 284 | Thermowell |  | P15 |  | CA |  |  |  | 20 | mbar g |  | 161 |  | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2285 |  | TI-2285
S-02115 | TW-2303 | 284 | Thermowell |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | [5 empty] | Part of reformer supply | [25 empty] | T | 2303 |  | TI-2303
S-02115 | TW-2304 | 284 | Thermowell |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | [5 empty] | Part of reformer supply | [25 empty] | T | 2304 |  | TI-2304
S-02115 | TW-2305 | 284 | Thermowell |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | [5 empty] | Part of reformer supply | [25 empty] | T | 2305 |  | TI-2305
S-02115 | TW/A-2325 | 284 | Thermowell |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2325 |  | TI-2325
S-02115 | TW/B-2325 | 284 | Thermowell |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2325 |  | TI-2325
S-02115 | TW/C-2325 | 284 | Thermowell |  | P16A |  | R 2004 |  |  | 34.7 | 31.4 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2325 |  | TI-2325
S-02115 | TW-2326 | 284 | Thermowell |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C |  |  |  | Special | [27 empty] | T | 2326 |  | TI-2326
S-02115 | TW-2327 | 284 | Thermowell |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C |  |  |  | Special | [27 empty] | T | 2327 |  | TI-2327
S-02115 | TW-2328 | 284 | Thermowell |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C |  |  |  | Special | [27 empty] | T | 2328 |  | TI-2328
S-02115 | TW-2330 | 284 | Thermowell |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C |  |  |  | Special | [27 empty] | T | 2330 |  | TI-2330
S-02115 | TW-2331 | 284 | Thermowell |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C |  |  |  | Special | [27 empty] | T | 2331 |  | TI-2331
S-02115 | TW-2332 | 284 | Thermowell |  | P16A |  | R 2004 |  |  |  |  | bar g |  |  |  | °C |  |  |  | Special | [27 empty] | T | 2332 |  | TI-2332
S-02115 | TW/A-2333 | 284 | Thermowell |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2333 |  | TI-2333
S-02115 | TW/B-2333 | 284 | Thermowell |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2333 |  | TI-2333
S-02115 | TW/C-2333 | 284 | Thermowell |  | P16A |  | R 2004 Outlet |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2333 |  | TI-2333
S-02115 | TW/A-2334 | 284 | Thermowell |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2334 |  | TI-2334
S-02115 | TW/B-2334 | 284 | Thermowell |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2334 |  | TI-2334
S-02115 | TW/C-2334 | 284 | Thermowell |  | P16A |  | R 2004 |  |  | 34.7 | 27.1 | bar g |  | 1020 |  | °C |  |  |  | Special | [27 empty] | T | 2334 |  | TI-2334
S-02115 | TW/A-2335 | 284 | Thermowell |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C |  |  |  | Special | [27 empty] | T | 2335 |  | TIC-2335
S-02115 | TW/B-2335 | 284 | Thermowell |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C |  |  |  | Special | [27 empty] | T | 2335 |  | TIC-2335
S-02115 | TW/C-2335 | 284 | Thermowell |  | P16B |  | E 2020 1 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C |  |  |  | Special | [27 empty] | T | 2335 |  | TIC-2335
S-02115 | TW/A-2336 | 284 | Thermowell |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C |  |  |  | Special | [27 empty] | T | 2336 |  | TIC-2336
S-02115 | TW/B-2336 | 284 | Thermowell |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C |  |  |  | Special | [27 empty] | T | 2336 |  | TIC-2336
S-02115 | TW/C-2336 | 284 | Thermowell |  | P16B |  | E 2020 2 |  |  | 31 | 26.7 | bar g |  | 544 | 575 | °C |  |  |  | Special | [27 empty] | T | 2336 |  | TIC-2336
S-02115 | TW-2351 | 284 | Thermowell |  | P17 |  | 24"-RFG-20-110-D34-H |  |  | 30 | 26.3 | bar g |  | 360 | 390 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2351 |  | TI-2351
S-02115 | TW-2352 | 284 | Thermowell |  | P17 |  | 42"-RFG-20-115-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2352 |  | TI-2352
S-02115 | TW-2353 | 284 | Thermowell |  | P17 |  | 24"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2353 |  | TI-2353
S-02115 | TW-2354 | 284 | Thermowell |  | P17 |  | 42"-RFG-20-110-H24-H |  |  | 31 | 26.7 | bar g |  | 409 | 450 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2354 |  | TI-2354
S-02115 | TW-2355 | 284 | Thermowell |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2355 |  | TI-2355
S-02115 | TW-2356 | 284 | Thermowell |  | P17 |  | 24"-HHPS-20-117-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2356 |  | TI-2356
S-02115 | TW-2359 | 284 | Thermowell |  | P17 |  | 20"-HHPS-20-103-H24-H |  |  | 112 | 101 | bar g |  | 338 | 370 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2359 |  | TI-2359
S-02115 | TW/A-2360 | 284 | Thermowell |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2360 |  | TIC-2360
S-02115 | TW/B-2360 | 284 | Thermowell |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2360 |  | TIC-2360
S-02115 | TW/C-2360 | 284 | Thermowell |  | P17 |  | 24"-HHPS-20-115-H34-H |  |  | 112 | 100 | bar g |  | 460 | 490 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2360 |  | TIC-2360
S-02115 | TW-2371 | 284 | Thermowell |  | P18 |  | 12"-BFW-20-102-G24-H |  |  | 113 | 103 | bar g |  | 276 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2371 |  | TI-2371
S-02115 | TW-2401 | 284 | Thermowell |  | P19 |  | 24"-RFG |  |  | 29 | 25.8 | bar g |  | 251 | 280 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2401 |  | TG-2401
S-02115 | TW-2402 | 284 | Thermowell |  | P19 |  | 34"-RFG-20-117-D40-H |  |  | 29 | 25.8 | bar g |  | 165 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2402 |  | TI-2402
S-02115 | TW-2403 | 284 | Thermowell |  | P19 |  | 24"-RFG |  |  | 29 | 25.8 | bar g |  | 208 | 280 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2403 |  | TG-2403
S-02115 | TW-2404 | 284 | Thermowell |  | P19 |  | 12"-BFW |  |  | 113 | 104 | bar g |  | 166 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2404 |  | TG-2404
S-02115 | TW-2405 | 284 | Thermowell |  | P19 |  | 12"-BFW |  |  | 113 | 104 | bar g |  | 210 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2405 |  | TG-2405
S-02115 | TW-2407 | 284 | Thermowell |  | P19 |  | 16"-FLG-20-120-B40-P |  |  | 5 |  | bar g |  |  | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2407 |  | TI-2407
S-02115 | TW-2418 | 284 | Thermowell |  | P19 |  | 12"-BFW-20-104-G24 |  |  | 113 | 104 | bar g |  | 122 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2418 |  | TI-2418
S-02115 | TW-2421 | 284 | Thermowell |  | P19 |  | 34"-RFG-20-122-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2421 |  | TI-2421
S-02115 | TW-2444 | 284 | Thermowell |  | P20 |  | 34"-RFG-20-124-D40-P |  |  | 29 | 24.4 | bar g |  | 132 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2444 |  | TI-2444
S-02115 | TW-2454 | 284 | Thermowell |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2454 |  | TG-2454
S-02115 | TW-2455 | 284 | Thermowell |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2455 |  | TI-2455
S-02115 | TW-2456 | 284 | Thermowell |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2456 |  | TG-2456
S-02115 | TW-2457 | 284 | Thermowell |  | P20 |  | 10"-DMW-20-104-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2457 |  | TIC-2457
S-02115 | TW-2472 | 284 | Thermowell |  | P21 |  | 34"-RFG-20-125-D40-P |  |  | 29 | 24.2 | bar g |  | 65 | 120 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2472 |  | TI-2472
S-02115 | TW-2476 | 284 | Thermowell |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2476 |  | TI-2476
S-02115 | TW-2484 | 284 | Thermowell |  | P21 |  | 12"-FLG-20-123-B24-N |  |  | 5 |  | bar g |  |  | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2484 |  | TI-2484
S-02115 | TW-2493 | 284 | Thermowell |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2493 |  | TI-2493
S-02115 | TW-2494 | 284 | Thermowell |  | P21 |  | 12"-CWR-20-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2494 |  | TG-2494
S-02115 | TW-2536 | 284 | Thermowell |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2536 |  | TI-2536
S-02115 | TW-2540 | 284 | Thermowell |  | U01 |  | 24"-NG-20-108-B24-N |  |  | 7 | 2 | bar g |  | 35 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2540 |  | TI-2540
S-02115 | TW-2553 | 284 | Thermowell |  | U01 |  | 28"-FG-20-101-B24-H |  |  | 7 | 2 | bar g |  | 45 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2553 |  | TI-2553
S-02115 | TW-2572 | 284 | Thermowell |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2572 |  | TI-2572
S-02115 | TW-2574 | 284 | Thermowell |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2574 |  | TG-2574
S-02115 | TW-2579 | 284 | Thermowell |  | U02 |  | 10"-N-20-104-B24-P |  |  | 10.5 | 8 | bar g |  | 84 | 110 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2579 |  | TI-2579
S-02115 | TW-2601 | 284 | Thermowell |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2601 |  | TI-2601
S-02115 | TW-2607 | 284 | Thermowell |  | U17 |  | 3"-SG-30-128-G24-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 2607 |  | TI-2607
S-02115 | TW-3025 | 284 | Thermowell |  | P22 |  | 20"-CWR-30-101-B24-N |  |  | 7 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3025 |  | TG-3025
S-02115 | TW-3045 | 284 | Thermowell |  | P23 |  | 4"-MPS-70-118-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3045 |  | TI-3045
S-02115 | TW-3051 | 284 | Thermowell |  | P23 |  | Downcomers |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3051 |  | TG-3051
S-02115 | TW-3072 | 284 | Thermowell |  | P24 |  | R 3001 1 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C |  |  |  | Special | [27 empty] | T | 3072 |  | TI-3072
S-02115 | TW-3073 | 284 | Thermowell |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3073 |  | TI-3073
S-02115 | TW-3074 | 284 | Thermowell |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3074 |  | TG-3074
S-02115 | TW-3076 | 284 | Thermowell |  | P24 |  | R 3001 2 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C |  |  |  | Special | [27 empty] | T | 3076 |  | TI-3076
S-02115 | TW-3077 | 284 | Thermowell |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3077 |  | TI-3077
S-02115 | TW-3078 | 284 | Thermowell |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3078 |  | TG-3078
S-02115 | TW-3080 | 284 | Thermowell |  | P24 |  | R 3001 3 |  |  | 99 | 89.1 | bar g |  | 230 | 300 | °C |  |  |  | Special | [27 empty] | T | 3080 |  | TI-3080
S-02115 | TW-3081 | 284 | Thermowell |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3081 |  | TI-3081
S-02115 | TW-3082 | 284 | Thermowell |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3082 |  | TG-3082
S-02115 | TW-3084 | 284 | Thermowell |  | P24 |  | 12"-MPS-70-120-F24-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3084 |  | TI-3084
S-02115 | TW-3085 | 284 | Thermowell |  | P24 |  | 16"-MPS-30-132-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3085 |  | TG-3085
S-02115 | TW-3086 | 284 | Thermowell |  | P24 |  | 16"-MPC-30-131-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3086 |  | TG-3086
S-02115 | TW-3088 | 284 | Thermowell |  | P24 |  | 16"-MPS-30-128-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3088 |  | TG-3088
S-02115 | TW-3089 | 284 | Thermowell |  | P24 |  | 16"-MPC-30-127-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3089 |  | TG-3089
S-02115 | TW-3091 | 284 | Thermowell |  | P24 |  | 16"-MPS-30-123-F24-H |  |  | 46.5 | 28 | bar g |  | 230 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3091 |  | TG-3091
S-02115 | TW-3092 | 284 | Thermowell |  | P24 |  | 16"-MPC-30-122-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 280 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3092 |  | TG-3092
S-02115 | TW-3111 | 284 | Thermowell |  | P25 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3111 |  | TI-3111
S-02115 | TW-3113 | 284 | Thermowell |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3113 |  | TIC-3113
S-02115 | TW-3116 | 284 | Thermowell |  | P25 |  | 24"-SG-30-107-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3116 |  | TIC-3116
S-02115 | TW-3118 | 284 | Thermowell |  | P25 |  | 24"-SG-30-119-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3118 |  | TIC-3118
S-02115 | TW-3119 | 284 | Thermowell |  | P25 |  | 20"-SG-30-110-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3119 |  | TI-3119
S-02115 | TW-3120 | 284 | Thermowell |  | P25 |  | 20"-SG-30-109-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3120 |  | TI-3120
S-02115 | TW-3121 | 284 | Thermowell |  | P25 |  | 20"-SG-30-121-H40-P |  |  | 99 | 77.3 | bar g |  | 125 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3121 |  | TI-3121
S-02115 | TW-3142 | 284 | Thermowell |  | P26 |  | 24"-SG-30-122-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3142 |  | TI-3142
S-02115 | TW-3143 | 284 | Thermowell |  | P26 |  | 24"-CWR-30-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3143 |  | TG-3143
S-02115 | TW-3145 | 284 | Thermowell |  | P26 |  | 24"-SG-30-123-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3145 |  | TI-3145
S-02115 | TW-3146 | 284 | Thermowell |  | P26 |  | 14"-CWR-30-106-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3146 |  | TG-3146
S-02115 | TW-3148 | 284 | Thermowell |  | P26 |  | 24"-SG-30-124-G40-P |  |  | 99 | 76.8 | bar g |  | 65 | 120 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3148 |  | TI-3148
S-02115 | TW-3149 | 284 | Thermowell |  | P26 |  | 14"-CWR-30-105-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3149 |  | TG-3149
S-02115 | TW-3164 | 284 | Thermowell |  | P27 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3164 |  | TI-3164
S-02115 | TW-3194 | 284 | Thermowell |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3194 |  | TI-3194
S-02115 | TW-3198 | 284 | Thermowell |  | P28 |  | 10"-PMC-30-111-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 3198 |  | TI-3198
S-02115 | TW-5008 | 284 | Thermowell |  | P29 |  | TK 5001 |  |  | -0.3 | 0 | mbar g |  | 46 | 100 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5008 |  | TG-5008
S-02115 | TW-5020 | 284 | Thermowell |  | P29 |  | 2"-PMW-50-101-B24-N |  |  | 7.5 | 4 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5020 |  | TI-5020
S-02115 | TW-5039 | 284 | Thermowell |  | P30 |  | RFG-50 |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5039 |  | TI-5039
S-02115 | TW-5040 | 284 | Thermowell |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5040 |  | TI-5040
S-02115 | TW-5045 | 284 | Thermowell |  | P30 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5045 |  | TI-5045
S-02115 | TW-5052 | 284 | Thermowell |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5052 |  | TI-5052
S-02115 | TW-5053 | 284 | Thermowell |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5053 |  | TI-5053
S-02115 | TW-5054 | 284 | Thermowell |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5054 |  | TI-5054
S-02115 | TW-5056 | 284 | Thermowell |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5056 |  | TI-5056
S-02115 | TW-5057 | 284 | Thermowell |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5057 |  | TI-5057
S-02115 | TW-5059 | 284 | Thermowell |  | P30 |  | 42"-PMV-50-110-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5059 |  | TI-5059
S-02115 | TW-5060 | 284 | Thermowell |  | P30 |  | 20"-PMC-50-110-B24-H |  |  | 5 | 1 | bar g |  | 87 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5060 |  | TI-5060
S-02115 | TW-5062 | 284 | Thermowell |  | P30 |  | 34"-PMV-50-120-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5062 |  | TI-5062
S-02115 | TW-5064 | 284 | Thermowell |  | P30 |  | 34"-RFG-50-101-D40-H |  |  | 29 | 24.8 | bar g |  | 138 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5064 |  | TIC-5064
S-02115 | TW-5067 | 284 | Thermowell |  | P30 |  | 34"-PMW-50-122-B24-H |  |  | 5 | 1 | bar g |  | 88 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5067 |  | TI-5067
S-02115 | TW-5074 | 284 | Thermowell |  | P31 |  | 8"-LPC-50-110-D24-H |  |  | 18 | 2.4 | bar g |  | 138 | 190 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5074 |  | TI-5074
S-02115 | TW-5097 | 284 | Thermowell |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5097 |  | TI-5097
S-02115 | TW-5108 | 284 | Thermowell |  | P32 |  | 3"-CWR-50-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5108 |  | TG-5108
S-02115 | TW-5110 | 284 | Thermowell |  | P32 |  | 6"-FLG-50-131-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5110 |  | TI-5110
S-02115 | TW-5111 | 284 | Thermowell |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5111 |  | TI-5111
S-02115 | TW-5165 | 284 | Thermowell |  | P34 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5165 |  | TI-5165
S-02115 | TW-5167 | 284 | Thermowell |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5167 |  | TI-5167
S-02115 | TW-5171 | 284 | Thermowell |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5171 |  | TI-5171
S-02115 | TW-5173 | 284 | Thermowell |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5173 |  | TI-5173
S-02115 | TW-5174 | 284 | Thermowell |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5174 |  | TI-5174
S-02115 | TW-5175 | 284 | Thermowell |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5175 |  | TI-5175
S-02115 | TW-5177 | 284 | Thermowell |  | P34 |  | 72"PMV-50-130-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5177 |  | TI-5177
S-02115 | TW-5180 | 284 | Thermowell |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5180 |  | TI-5180
S-02115 | TW-5181 | 284 | Thermowell |  | P34 |  | 24"-PMC-50-140-B24-H |  |  | 5 | 0.7 | bar g |  | 83 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5181 |  | TI-5181
S-02115 | TW-5184 | 284 | Thermowell |  | P34 |  | 16"-PMC-50-147-B24-H |  |  | 5 | 0.7 | bar g |  | 86 | 160 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5184 |  | TI-5184
S-02115 | TW-5208 | 284 | Thermowell |  | P36 |  | 24"-PMP-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5208 |  | TI-5208
S-02115 | TW-5209 | 284 | Thermowell |  | P36 |  | 20"-PMP-50-102-B24-H |  |  | 13 | 0 | bar g |  | 65 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5209 |  | TI-5209
S-02115 | TW-5219 | 284 | Thermowell |  | P36 |  | 6"-PMP-50-110-B24-P |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5219 |  | TI-5219
S-02115 | TW-5220 | 284 | Thermowell |  | P36 |  | 6"-CWR-50-104-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5220 |  | TG-5220
S-02115 | TW-5221 | 284 | Thermowell |  | P36 |  | 6"-PMP-50-111-D24-N |  |  | 19 | 3.5 | bar g |  | 48 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5221 |  | TI-5221
S-02115 | TW-5261 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5261 |  | TI-5261
S-02115 | TW-5262 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5262 |  | TI-5262
S-02115 | TW-5263 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5263 |  | TI-5263
S-02115 | TW-5264 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5264 |  | TI-5264
S-02115 | TW-5265 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5265 |  | TI-5265
S-02115 | TW-5266 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 600 mm |  | AISI 316 | [28 empty] | T | 5266 |  | TIC-5266
S-02115 | TW-5267 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 600 mm |  | AISI 316 | [28 empty] | T | 5267 |  | TIC-5267
S-02115 | TW-5268 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 600 mm |  | AISI 316 | [28 empty] | T | 5268 |  | TIC-5268
S-02115 | TW-5269 | 284 | Thermowell |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5269 |  | TI-5269
S-02115 | TW-5273 | 284 | Thermowell |  | P38 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5273 |  | TI-5273
S-02115 | TW-5276 | 284 | Thermowell |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5276 |  | TG-5276
S-02115 | TW-5277 | 284 | Thermowell |  | P38 |  | 34"-RFG-20-121-D40-H |  |  | 29 | 25.3 | bar g |  | 159 | 200 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5277 |  | TIC-5277
S-02115 | TW-5280 | 284 | Thermowell |  | P38 |  | 56"-PMV-50-150-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5280 |  | TI-5280
S-02115 | TW-5307 | 284 | Thermowell |  | P39 |  | 16"-LPC-50-115-B24-H |  |  | 10.5 | 6.5 | bar g |  | 168 | 190 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5307 |  | TI-5307
S-02115 | TW-5325 | 284 | Thermowell |  | P40 |  | 24"-PMP-50-130-B24-H |  |  | 7 | 2.6 | bar g |  | 101 | 165 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5325 |  | TI-5325
S-02115 | TW-5335 | 284 | Thermowell |  | P40 |  | 6"-PMP-50-140-D24-H |  |  | 19 | 6 | bar g |  | 101 | 165 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5335 |  | TI-5335
S-02115 | TW-5339 | 284 | Thermowell |  | P40 |  | 10"-CWR-50-103-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5339 |  | TG-5339
S-02115 | TW-5340 | 284 | Thermowell |  | P40 |  | 6"-PMP-50-141-D24-N |  |  | 19 | 5.7 | bar g |  | 48 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5340 |  | TI-5340
S-02115 | TW-5369 | 284 | Thermowell |  | P41 |  | 2"-PMW-50-125-B24-P |  |  | 7.5 | 4.3 | bar g |  | 65 | 120 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5369 |  | TI-5369
S-02115 | TW-5370 | 284 | Thermowell |  | P41 |  | 3"-CWR-50-112-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5370 |  | TG-5370
S-02115 | TW-5381 | 284 | Thermowell |  | P42 |  | 10"-PMP-50-142-B24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5381 |  | TI-5381
S-02115 | TW-5394 | 284 | Thermowell |  | P43 |  | TK 5002 1 |  |  | -0.03 | 0 | bar g |  | 48 | 85 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5394 |  | TG-5394
S-02115 | TW-5411 | 284 | Thermowell |  | P44 |  | TK 5002 2 |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5411 |  | TG-5411
S-02115 | TW-5441 | 284 | Thermowell |  | P45 |  | 2"-LOS-50-110-B24-P |  |  | 7.5 | 3.4 | bar g |  | 115 | 175 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5441 |  | TI-5441
S-02115 | TW-5442 | 284 | Thermowell |  | P45 |  | 2"-LOS-50-113-B24-P |  |  | 7.5 | 2.5 | bar g |  | 115 | 175 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5442 |  | TI-5442
S-02115 | TW-5443 | 284 | Thermowell |  | P45 |  | 2"-LOS-50-114-B24-N |  |  | 7.5 | 2 | bar g |  | 48 | 75 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5443 |  | TI-5443
S-02115 | TW-5444 | 284 | Thermowell |  | P45 |  | 3"-CWR-50-115-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5444 |  | TG-5444
S-02115 | TW-5445 | 284 | Thermowell |  | P45 |  | TK 5003 |  |  | -0.3 | 0 | bar g |  | 48 | 100 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 5445 |  | TG-5445
S-02115 | TW-5501 | 284 | Thermowell |  | U23A |  | 4"-CWR-50-118-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 5501 |  | TG-5501
S-02115 | TW-6001 | 284 | Thermowell |  | P05 |  | 18"-MPC-60-101-F24-H |  |  | 73 | 32.5 | bar g |  | 240 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6001 |  | TI-6001
S-02115 | TW-6024 | 284 | Thermowell |  | P06 |  | 12"-PRC-60-101-G40-H |  |  | 57 | 44 | bar g |  | 225 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6024 |  | TI-6024
S-02115 | TW-6026 | 284 | Thermowell |  | P06 |  | 24"-MPS-60-102-F24-H |  |  | 45 | 32.2 | MPa g |  | 240 | 300 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6026 |  | TI-6026
S-02115 | TW-6031 | 284 | Thermowell |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6031 |  | TI-6031
S-02115 | TW-6034 | 284 | Thermowell |  | P06 |  | 8"-PRC-60-102-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6034 |  | TI-6034
S-02115 | TW-6054 | 284 | Thermowell |  | P07 |  | 24"-PRG-60-103-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6054 |  | TI-6054
S-02115 | TW-6056 | 284 | Thermowell |  | P07 |  | 16"-PRG-60-102-F24-H |  |  | 55 | 43.3 | bar g |  | 265 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6056 |  | TI-6056
S-02115 | TW-6058 | 284 | Thermowell |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6058 |  | TI-6058
S-02115 | TW-6081 | 284 | Thermowell |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6081 |  | TI-6081
S-02115 | TW-6082 | 284 | Thermowell |  | P08 |  | 4"-PRC-60-108-G40-H |  |  | 63 | 45 | bar g |  | 63 | 150 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6082 |  | TG-6082
S-02115 | TW-6083 | 284 | Thermowell |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6083 |  | TG-6083
S-02115 | TW-6084 | 284 | Thermowell |  | P08 |  | 4"-BD-60-109-G40-P |  |  | 57 | 44 | bar g |  | 78 | 260 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6084 |  | TI-6084
S-02115 | TW-6085 | 284 | Thermowell |  | P08 |  | 3"-CWR-60-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 6085 |  | TG-6085
S-02115 | TW-6086 | 284 | Thermowell |  | P08 |  | D 6002 |  |  | 3.5 | 0 | bar g |  | 100 | 125 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 6086 |  | TG-6086
S-02115 | TW-7001 | 284 | Thermowell |  | U03 |  | 16"-HPS-30-129-F24-H |  |  | 52 | 45 | bar g |  | 355 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7001 |  | TI-7001
S-02115 | TW-7002 | 284 | Thermowell |  | U03 |  | 12"-HPS-70-105-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7002 |  | TIC-7002
S-02115 | TW-7003 | 284 | Thermowell |  | U03 |  | 28"-HPS-70-104-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7003 |  | TIC-7003
S-02115 | TW-7004 | 284 | Thermowell |  | U03 |  | 28"-HPS-70-106-H34-H |  |  | 112 | 44 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7004 |  | TIC-7004
S-02115 | TW-7007 | 284 | Thermowell |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7007 |  | TI-7007
S-02115 | TW-7008 | 284 | Thermowell |  | U03 |  | 28"-HPS-70-116-F24-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7008 |  | TG-7008
S-02115 | TW-7021 | 284 | Thermowell |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7021 |  | TI-7021
S-02115 | TW-7022 | 284 | Thermowell |  | U04 |  | 24"-HPS-70-107-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7022 |  | TG-7022
S-02115 | TW-7025 | 284 | Thermowell |  | U04 |  | 24"-HPS-70-133-F34-H |  |  | 52 | 42.5 | bar g |  | 345 | 470 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7025 |  | TIC-7025
S-02115 | TW-7026 | 284 | Thermowell |  | U04 |  | 24"-HPS-70-1873-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7026 |  | TIC-7026
S-02115 | TW-7027 | 284 | Thermowell |  | U04 |  | 24"-HPS-70-1862-H34-H |  |  | 112 | 43 | bar g |  | 410 | 470 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7027 |  | TIC-7027
S-02115 | TW-7031 | 284 | Thermowell |  | U05 |  | 24"-MPS-30-115-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7031 |  | TI-7031
S-02115 | TW-7032 | 284 | Thermowell |  | U05 |  | 18"-MPS-70-128-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7032 |  | TIC-7032
S-02115 | TW-7033 | 284 | Thermowell |  | U05 |  | 18"-MPS-70-129-D24-H |  |  | 45 | 34 | bar g |  | 280 | 300 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7033 |  | TIC-7033
S-02115 | TW-7052 | 284 | Thermowell |  | U06 |  | 24"-LPS-70-116-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7052 |  | TIC-7052
S-02115 | TW-7053 | 284 | Thermowell |  | U06 |  | 24"-LPS-70-117-F24-H |  |  | 52 | 7.5 | bar g |  | 200 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7053 |  | TIC-7053
S-02115 | TW-7056 | 284 | Thermowell |  | U06 |  | 32"-LPS-70-108-D24-H |  |  | 9.5 | 7 | bar g |  | 189 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7056 |  | TI-7056
S-02115 | TW/A-7071 | 284 | Thermowell |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7071 |  | TIC-7071
S-02115 | TW/B-7071 | 284 | Thermowell |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7071 |  | TIC-7071
S-02115 | TW/C-7071 | 284 | Thermowell |  | U07 |  | 6"-HPS-70-126-F24-H |  |  | 52 | 44 | bar g |  | 272 | 310 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7071 |  | TIC-7071
S-02115 | TW-7097 | 284 | Thermowell |  | U09 |  | D 7001 |  |  | 3.5 | 1 | bar g |  | 120 | 200 | °C | 300 mm |  | AISI 316 | [28 empty] | T | 7097 |  | TI-7097
S-02115 | TW-7098 | 284 | Thermowell |  | U09 |  | 24"-VA-70-161-B24-P |  |  | 3.5 | 0 | bar g |  | 120 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7098 |  | TI-7098
S-02115 | TW-7128 | 284 | Thermowell |  | U10 |  | 8"-HPS-70-117-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7128 |  | TG-7128
S-02115 | TW-7133 | 284 | Thermowell |  | U10 |  | 8"-HPS-70-118-F24-H |  |  | 52 | 43 | bar g |  | 345 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7133 |  | TG-7133
S-02115 | TW-7138 | 284 | Thermowell |  | U10 |  | 14"-LPS-70-121-D24-H |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7138 |  | TG-7138
S-02115 | TW-7139 | 284 | Thermowell |  | U10 |  | 14"-LPS-70-125-D24-H |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7139 |  | TG-7139
S-02115 | TW-7256 | 284 | Thermowell |  | U16 |  | 4"-CWR-70-101-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 7256 |  | TG-7256
S-02115 | TW-8001 | 284 | Thermowell |  | U21 |  | 72"-FLG-80-144-B24-P |  |  | 5 | 1.5 | bar g |  | 390 | 410 | °C | 125 mm |  | AISI 316 | [28 empty] | T | 8001 |  | TI-8001
S-02115 | FO-2483 | 287 | Restriction Orifice |  | P21 |  | 12"-SG-20-107-D40-N |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 58000 Nm3/h | Gas | Thick restriction orifice t=d | 24 bar g | 48 °C | 10.3 kg/m3 | 0.016 cP | 1.01 | 1.39 | 11.14 | Critical pressure drop | 303.2 (12" sch 40S) | 0.2 | AISI 316 | 12", class 300, RF | [16 empty] | F | 2483 |  | FO-2483
S-02115 | FO-2552 | 287 | Restriction Orifice |  | U01 |  | 2"-NG-20-113-B24-N |  |  | 7 | 3 | bar g |  | 35 | 85 | °C | 620 Nm3/h | Gas | Thick restriction orifice t=d | 3 bar g | 35 °C | 2.64 kg/m3 | 0.012 cP | 0.99 | 1.31 | 16.74 | Critical pressure drop | 52.5 (2", Sch.40) | app. 0.32 | AISI 316 | 2", class 150, RF | [16 empty] | F | 2552 |  | FO-2552
S-02115 | FO-3191 | 287 | Restriction Orifice |  | P28 |  | 12"-PMC-30-105-G40-N |  |  | 100 | 32 | bar g |  | 47 | 100 | °C | 246704 kg/h | Liquid and gas | Thick restriction orifice t=6d | 32 bar g | 47 °C | [5 empty] | 28 bar | 288.9 (12" sch 80S) mm | app. 0.17 | AISI 316, hard faced | 12", class 900, RTJ | [16 empty] | F | 3191 |  | FO-3191
S-02115 | FO-7096 | 287 | Restriction Orifice |  | U09 |  | 2"-LPS-70-130-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | 764 kg/h | Steam | Square edge orifice | 1 bar g | 120 °C | 1.12 kg/m3 | 0.013 cP | 0.98 | 1.27 | 18.02 kg/kmol | 1 bar | 82.8 (3", Sch.10) mm | 0.39 | AISI 316, hard faced | [17 empty] | F | 7096 |  | FO-7096
S-02115 | PSV1-1008 | 288.1 | Body |  | P01 |  | 1 1/2"-NG-10-108-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 1008 |  | PSV-1008
S-02115 | PSV1-1009 | 288.1 | Body |  | P01 |  | 1 1/2"-NG-10-109-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 1009 |  | PSV-1009
S-02115 | PSV1-1013 | 288.1 | Body |  | P01 |  | 8"-NG-10-110-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 1013 |  | PSV-1013
S-02115 | PSV1-1014 | 288.1 | Body |  | P01 |  | 8"-NG-10-111-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 1014 |  | PSV-1014
S-02115 | PSV1-1015 | 288.1 | Body |  | P01 |  | 1 1/2"-NG-10-112-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 1015 |  | PSV-1015
S-02115 | PSV1-1031 | 288.1 | Body |  | P04 |  | 1 1/2"-PRG-10-102-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 1031 |  | PSV-1031
S-02115 | PSV1-1038 | 288.1 | Body |  | P04 |  | 1 1/2"-PRG-10-103-F24-H |  |  | 60 | 48.3 | bar g |  | 375 | 410 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 1038 |  | PSV-1038
S-02115 | PSV1-1043 | 288.1 | Body |  | P04 |  | 1 1/2"-PRG-10-106-F24-H |  |  | 60 | 48.3 | bar g |  | 375 | 410 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 1043 |  | PSV-1043
S-02115 | PSV1-2019 | 288.1 | Body |  | P02 |  | 2"-HPC-20-104-F24-P |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 2019 |  | PSV-2019
S-02115 | PSV1-2078 | 288.1 | Body |  | P09 |  | 1 1/2"-HPS-20-103-F24-H |  |  | 52 | 41.1 | bar g |  | 343 | 410 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 2078 |  | PSV-2078
S-02115 | PSV1-2121 | 288.1 | Body |  | P11 |  | HOLD-LPS-20-104-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 2121 |  | PSV-2121
S-02115 | PSV1-2122 | 288.1 | Body |  | P11 |  | HOLD-LPS-20-105-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 2122 |  | PSV-2122
S-02115 | PSV1-2171 | 288.1 | Body |  | P12 |  | HOLD-LPS-20-107-D24-P |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 2171 |  | PSV-2171
S-02115 | PSV1-2172 | 288.1 | Body |  | P12 |  | HOLD-LPS-20-108-D24-P |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 2172 |  | PSV-2172
S-02115 | PSV1-2354 | 288.1 | Body |  | P17 |  | 10"-RFG-20-105-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 600, RF | 8", Class 150, RF | [25 empty] | P | 2354 |  | PSV-2354
S-02115 | PSV1-2355 | 288.1 | Body |  | P17 |  | 10"-RFG-20-107-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 300, RF | 8", Class 150, RF | [25 empty] | P | 2355 |  | PSV-2355
S-02115 | PSV1-2356 | 288.1 | Body |  | P17 |  | 10"-RFG-20-109-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 300, RF | 8", Class 150, RF | [25 empty] | P | 2356 |  | PSV-2356
S-02115 | PSV1-2357 | 288.1 | Body |  | P17 |  | 10"-RFG-20-111-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 300, RF | 8", Class 150, RF | [25 empty] | P | 2357 |  | PSV-2357
S-02115 | PSV1-2358 | 288.1 | Body |  | P17 |  | 10"-RFG-20-113-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 300, RF | 8", Class 150, RF | [25 empty] | P | 2358 |  | PSV-2358
S-02115 | PSV1-2359 | 288.1 | Body |  | P17 |  | 10"-RFG-20-129-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 300, RF | 8", Class 150, RF | [25 empty] | P | 2359 |  | PSV-2359
S-02115 | PSV1-2360 | 288.1 | Body |  | P17 |  | 10"-RFG-20-130-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Full Nozzle | API 526 | Closed | A 217 WC6 | 6", Class 300, RF | 8", Class 150, RF | [25 empty] | P | 2360 |  | PSV-2360
S-02115 | PSV1-2376 | 288.1 | Body |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 3", Class 900, RTJ | 6", Class 300, RF | [25 empty] | P | 2376 |  | PSV-2376
S-02115 | PSV1-2377 | 288.1 | Body |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 3", Class 900, RTJ | 6", Class 300, RF | [25 empty] | P | 2377 |  | PSV-2377
S-02115 | PSV1-2378 | 288.1 | Body |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 3", Class 900, RTJ | 6", Class 300, RF | [25 empty] | P | 2378 |  | PSV-2378
S-02115 | PSV1-2379 | 288.1 | Body |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 3", Class 900, RTJ | 6", Class 300, RF | [25 empty] | P | 2379 |  | PSV-2379
S-02115 | PSV1-2380 | 288.1 | Body |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 3", Class 900, RTJ | 6", Class 300, RF | [25 empty] | P | 2380 |  | PSV-2380
S-02115 | PSV1-2458 | 288.1 | Body |  | P20 |  | 3"-DMW-20-102-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 3", Class 150, RF | 4", Class 150, RF | [25 empty] | P | 2458 |  | PSV-2458
S-02115 | PSV1-2494 | 288.1 | Body |  | P21 |  | 3"-CWR-20-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 2", Class 150, RF | 3", Class 150, RF | [25 empty] | P | 2494 |  | PSV-2494
S-02115 | PSV1-2546 | 288.1 | Body |  | U01 |  | 1 1/2"-N-20-118-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 150, RF | 3", Class 150, RF | [25 empty] | P | 2546 |  | PSV-2546
S-02115 | PSV1-2555 | 288.1 | Body |  | U01 |  | 1 1/2"-N-20-119-B24-N |  |  | 7 | 6 | bar g |  | 40 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 150, RF | 3", Class 150, RF | [25 empty] | P | 2555 |  | PSV-2555
S-02115 | PSV1-2581 | 288.1 | Body |  | U02 |  | 6"-N-20-120-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 110 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 4", Class 150, RF | 6", Class 150, RF | [25 empty] | P | 2581 |  | PSV-2581
S-02115 | PSV1-2604 | 288.1 | Body |  | U17 |  | 1 1/2"-HG-20-104-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 2604 |  | PSV-2604
S-02115 | PSV1-2605 | 288.1 | Body |  | U17 |  | 1 1/2"-HG-20-106-G24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 2605 |  | PSV-2605
S-02115 | PSV1-3021 | 288.1 | Body |  | P22 |  | 1 1/2"-SG-30-132-G40-H |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1½", Class 900, RTJ | 2", Class 300, RF | [25 empty] | P | 3021 |  | PSV-3021
S-02115 | PSV1-3047 | 288.1 | Body |  | P23 |  | 8"-MPS-30-112-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 6", Class 600, RF | 8", Class 300, RF | [25 empty] | P | 3047 |  | PSV-3047
S-02115 | PSV1-3048 | 288.1 | Body |  | P23 |  | 8"-MPS-30-110-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 6", Class 600, RF | 8", Class 300, RF | [25 empty] | P | 3048 |  | PSV-3048
S-02115 | PSV1-3057 | 288.1 | Body |  | P23 |  | 8"-MPS-30-113-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Full Nozzle | ASME Section I | Open | A 216 WCB | 6", Class 600, RF | 8", Class 300, RF | [25 empty] | P | 3057 |  | PSV-3057
S-02115 | PSV1-3143 | 288.1 | Body |  | P26 |  | 6"-CWR-30-103-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 3143 |  | PSV-3143
S-02115 | PSV1-3146 | 288.1 | Body |  | P26 |  | 6"-CWR-30-107-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 3146 |  | PSV-3146
S-02115 | PSV1-3149 | 288.1 | Body |  | P26 |  | 6"-CWR-30-109-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 3149 |  | PSV-3149
S-02115 | PSV1-3163 | 288.1 | Body |  | P27 |  | 3"-SG-30-137-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 3", Class 900, RTJ | 4", Class 150, RF | [25 empty] | P | 3163 |  | PSV-3163
S-02115 | PSV1-3173 | 288.1 | Body |  | P27 |  | 10"-PG-30-105-B24-N |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 3173 |  | PSV-3173
S-02115 | PSV1-3174 | 288.1 | Body |  | P27 |  | 10"-PG-30-107-B24-N |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 3174 |  | PSV-3174
S-02115 | PSV1-3196 | 288.1 | Body |  | P28 |  | 10"-PG-30-103-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 6", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 3196 |  | PSV-3196
S-02115 | PSV1-3197 | 288.1 | Body |  | P28 |  | 10"-PG-30-109-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 6", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 3197 |  | PSV-3197
S-02115 | PSV1-3206 | 288.1 | Body |  | P28 |  | 10"-PG-30-108-B24-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 6", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 3206 |  | PSV-3206
S-02115 | PSV1-5006 | 288.1 | Body |  | P29 |  | HOLD-PMV-50-104-B40-N |  |  | -0.3 | 0 | bar g |  | 46 | 100 | °C | Weighted pallet type | API 2000, API 650 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5006 |  | PSV-5006
S-02115 | PSV1-5007 | 288.1 | Body |  | P29 |  | HOLD-PMV-50-102-B40-N |  |  | -0.3 | 0 | bar g |  | 46 | 100 | °C | Tank breather valve | API 2000 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5007 |  | PSV-5007
S-02115 | PSV1-5058 | 288.1 | Body |  | P30 |  | 10"-PMV-50-111-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 5058 |  | PSV-5058
S-02115 | PSV1-5059 | 288.1 | Body |  | P30 |  | 10"-PMV-50-112-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 5059 |  | PSV-5059
S-02115 | PSV1-5060 | 288.1 | Body |  | P30 |  | 10"-PMV-50-123-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 5060 |  | PSV-5060
S-02115 | PSV1-5061 | 288.1 | Body |  | P30 |  | 10"-PMV-50-124-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 5061 |  | PSV-5061
S-02115 | PSV1-5073 | 288.1 | Body |  | P31 |  | 1 1/2"-LPS-50-101-B24-P |  |  | 9.5 | 2.4 | bar g |  | 138 | 190 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1", Class 150, RF | 2", Class 150, RF | [25 empty] | P | 5073 |  | PSV-5073
S-02115 | PSV1-5085 | 288.1 | Body |  | P31 |  | 3/4"-CWR-70-125-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5085 |  | PSV-5085
S-02115 | PSV1-5108 | 288.1 | Body |  | P32 |  | 3/4"-CWR-50-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5108 |  | PSV-5108
S-02115 | PSV1-5179 | 288.1 | Body |  | P34 |  | 6"-PMV-50-131-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 3", Class 150, RF | 4", Class 150, RF | [25 empty] | P | 5179 |  | PSV-5179
S-02115 | PSV1-5180 | 288.1 | Body |  | P34 |  | 6"-PMV-50-132-N24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 3", Class 150, RF | 4", Class 150, RF | [25 empty] | P | 5180 |  | PSV-5180
S-02115 | PSV1-5220 | 288.1 | Body |  | P36 |  | 3/4"-CWR-50-105-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5220 |  | PSV-5220
S-02115 | PSV1-5236 | 288.1 | Body |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 5236 |  | PSV-5236
S-02115 | PSV1-5239 | 288.1 | Body |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 5239 |  | PSV-5239
S-02115 | PSV1-5250 | 288.1 | Body |  | P38 |  | 10"-PMV-50-151-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 5250 |  | PSV-5250
S-02115 | PSV1-5251 | 288.1 | Body |  | P38 |  | 10"-PMV-50-152-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 5251 |  | PSV-5251
S-02115 | PSV1-5261 | 288.1 | Body |  | P38 |  | 10"-PMV-50-193-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 6", Class 150, RF | 8", Class 150, RF | [25 empty] | P | 5261 |  | PSV-5261
S-02115 | PSV1-5308 | 288.1 | Body |  | P39 |  | 3/4"-CWR-50-128-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5308 |  | PSV-5308
S-02115 | PSV1-5339 | 288.1 | Body |  | P40 |  | 3/4"-CWR-50-108-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5339 |  | PSV-5339
S-02115 | PSV1-5370 | 288.1 | Body |  | P41 |  | 3/4"-CWR-50-110-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5370 |  | PSV-5370
S-02115 | PSV1-5384 | 288.1 | Body |  | P42 |  | 3"-PMP-50-180-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 300, RF | 3", Class 150, RF | [25 empty] | P | 5384 |  | PSV-5384
S-02115 | PSV1-5386 | 288.1 | Body |  | P42 |  | 3"-PMP-50-194-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 300, RF | 3", Class 150, RF | [25 empty] | P | 5386 |  | PSV-5386
S-02115 | PSV1-5400 | 288.1 | Body |  | P43 |  | HOLD-PMV-50-181-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | Weighted pallet type | API 2000, API 650 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5400 |  | PSV-5400
S-02115 | PSV1-5401 | 288.1 | Body |  | P43 |  | HOLD-PMV-50-182-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | Tank breather valve | API 2000 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5401 |  | PSV-5401
S-02115 | PSV1-5405 | 288.1 | Body |  | P43 |  | HOLD-PMP-50-162-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1)", Class 600, RF | 1)", Class 150, RF | [25 empty] | P | 5405 |  | PSV-5405
S-02115 | PSV1-5417 | 288.1 | Body |  | P44 |  | HOLD-PMV-50-183-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | Weighted pallet type | API 2000, API 650 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5417 |  | PSV-5417
S-02115 | PSV1-5418 | 288.1 | Body |  | P44 |  | HOLD-PMV-50-184-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | Tank breather valve | API 2000 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5418 |  | PSV-5418
S-02115 | PSV1-5444 | 288.1 | Body |  | P45 |  | 3/4"-CWR-50-114-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5444 |  | PSV-5444
S-02115 | PSV1-5450 | 288.1 | Body |  | P45 |  | HOLD-PMV-50-190-B24-H |  |  | -0.3 | 0.01 | bar g |  | 48 | 85 | °C | Weighted pallet type | API 2000, API 650 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5450 |  | PSV-5450
S-02115 | PSV1-5451 | 288.1 | Body |  | P45 |  | HOLD-PMV-50-191-B24-H |  |  | -0.3 | 0.01 | bar g |  | 48 | 85 | °C | Tank breather valve | API 2000 |  | A 216 WCB | By vendor", Class 150, RF | By vendor", Class 150, RF | [25 empty] | P | 5451 |  | PSV-5451
S-02115 | PSV1-5461 | 288.1 | Body |  | P45 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1)", Class 600, RF | 1)", Class 150, RF | [25 empty] | P | 5461 |  | PSV-5461
S-02115 | PSV1-5462 | 288.1 | Body |  | P45 |  | 2"-LOS-50-123-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1)", Class 600, RF | 1)", Class 150, RF | [25 empty] | P | 5462 |  | PSV-5462
S-02115 | PSV1-5501 | 288.1 | Body |  | U23A |  | 3/4"-CWR-50-119-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 5501 |  | PSV-5501
S-02115 | PSV1-5505 | 288.1 | Body |  | U23A |  | 6"-PMW-50-142-B24-N |  |  | 7.5 | 1.5 | bar g |  | 62 | 100 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1½", Class 150, RF | 3", Class 150, RF | [25 empty] | P | 5505 |  | PSV-5505
S-02115 | PSV1-5512 | 288.1 | Body |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 5512 |  | PSV-5512
S-02115 | PSV1-5514 | 288.1 | Body |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 5514 |  | PSV-5514
S-02115 | PSV1-6021 | 288.1 | Body |  | P06 |  | 1 1/2"-PRC-60-196-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1", Class 900, RTJ | 2", Class 150, RF | [25 empty] | P | 6021 |  | PSV-6021
S-02115 | PSV1-6022 | 288.1 | Body |  | P06 |  | 1 1/2"-PRC-60-195-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1", Class 900, RTJ | 2", Class 150, RF | [25 empty] | P | 6022 |  | PSV-6022
S-02115 | PSV1-6027 | 288.1 | Body |  | P06 |  | 1 1/2"-MPS-60-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 6027 |  | PSV-6027
S-02115 | PSV1-6053 | 288.1 | Body |  | P07 |  | 1 1/2"-PRG-60-124-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 6053 |  | PSV-6053
S-02115 | PSV1-6056 | 288.1 | Body |  | P07 |  | 1 1/2"-PRG-10-125-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 6056 |  | PSV-6056
S-02115 | PSV1-6085 | 288.1 | Body |  | P08 |  | 3/4"-CWR-60-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle | API 526 | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 6085 |  | PSV-6085
S-02115 | PSV1-7010 | 288.1 | Body |  | U03 |  | 10"-HPS-70-110-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Full Nozzle | Non API, ASME Section I | Open | A 216 WCB | 6", Class 600, RF | 10", Class 300, RF | [25 empty] | P | 7010 |  | PSV-7010
S-02115 | PSV1-7011 | 288.1 | Body |  | U03 |  | 10"-HPS-70-112-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Full Nozzle | Non API, ASME Section I | Open | A 216 WCB | 6", Class 600, RF | 10", Class 300, RF | [25 empty] | P | 7011 |  | PSV-7011
S-02115 | PSV1-7012 | 288.1 | Body |  | U03 |  | 10"-HPS-70-114-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Full Nozzle | Non API, ASME Section I | Open | A 216 WCB | 6", Class 600, RF | 10", Class 300, RF | [25 empty] | P | 7012 |  | PSV-7012
S-02115 | PSV1-7013 | 288.1 | Body |  | U03 |  | 2"-BFW-70-106-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | Base Nozzle |  | Closed | A 217 WC6 | 1", Class 1500, RTJ | 1 ", Class 300, RF | [25 empty] | P | 7013 |  | PSV-7013
S-02115 | PSV1-7014 | 288.1 | Body |  | U03 |  | 3"-BFW-70-144-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | Base Nozzle |  | Closed | A 217 WC6 | 1", Class 1500, RTJ | 1 ", Class 300, RF | [25 empty] | P | 7014 |  | PSV-7014
S-02115 | PSV1-7015 | 288.1 | Body |  | U03 |  | 3"-BFW-70-142-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | Base Nozzle |  | Closed | A 217 WC6 | 1", Class 1500, RTJ | 1 ", Class 300, RF | [25 empty] | P | 7015 |  | PSV-7015
S-02115 | PSV1-7016 | 288.1 | Body |  | U04 |  | 2"-BFW-70-158-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | Base Nozzle |  | Closed | A 217 WC6 | 1", Class 1500, RTJ | 1 ", Class 300, RF | [25 empty] | P | 7016 |  | PSV-7016
S-02115 | PSV1-7017 | 288.1 | Body |  | U04 |  | 2"-BFW-70-157-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | Base Nozzle |  | Closed | A 217 WC6 | 1", Class 1500, RTJ | 1 ", Class 300, RF | [25 empty] | P | 7017 |  | PSV-7017
S-02115 | PSV1-7023 | 288.1 | Body |  | U04 |  | 10"-HPS-70-134-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | Full Nozzle | API 526 | Open | A 217 WC6 | 6", Class 600, RF | 10", Class 300, RF | [25 empty] | P | 7023 |  | PSV-7023
S-02115 | PSV1-7024 | 288.1 | Body |  | U04 |  | 10"-HPS-70-135-F34-H |  |  | 52 | 44 | bar g |  | 410 | 470 | °C | Full Nozzle | API 526 | Open | A 217 WC6 | 6", Class 600, RF | 10", Class 300, RF | [25 empty] | P | 7024 |  | PSV-7024
S-02115 | PSV1-7032 | 288.1 | Body |  | U05 |  | 2"-BFW-70-109-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 600, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7032 |  | PSV-7032
S-02115 | PSV1-7033 | 288.1 | Body |  | U05 |  | 2"-BFW-70-111-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 600, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7033 |  | PSV-7033
S-02115 | PSV1-7036 | 288.1 | Body |  | U05 |  | 1 1/2"-MPS-70-122-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 7036 |  | PSV-7036
S-02115 | PSV1-7037 | 288.1 | Body |  | U05 |  | 1 1/2"-MPS-70-123-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1", Class 600, RF | 2", Class 150, RF | [25 empty] | P | 7037 |  | PSV-7037
S-02115 | PSV1-7052 | 288.1 | Body |  | U06 |  | 2"-BFW-70-122-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 600, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7052 |  | PSV-7052
S-02115 | PSV1-7053 | 288.1 | Body |  | U06 |  | 2"-BFW-70-123-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 600, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7053 |  | PSV-7053
S-02115 | PSV1-7057 | 288.1 | Body |  | U06 |  | 10"-LPS-70-111-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 7057 |  | PSV-7057
S-02115 | PSV1-7058 | 288.1 | Body |  | U06 |  | 10"-LPS-70-110-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 7058 |  | PSV-7058
S-02115 | PSV1-7059 | 288.1 | Body |  | U06 |  | 10"-LPS-70-113-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 7059 |  | PSV-7059
S-02115 | PSV1-7060 | 288.1 | Body |  | U06 |  | 10"-LPS-70-141-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 7060 |  | PSV-7060
S-02115 | PSV1-7061 | 288.1 | Body |  | U06 |  | 10"-LPS-70-140-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 8", Class 300, RF | 10", Class 150, RF | [25 empty] | P | 7061 |  | PSV-7061
S-02115 | PSV1-7072 | 288.1 | Body |  | U07 |  | 2"-BFW-70-124-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 600, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7072 |  | PSV-7072
S-02115 | PSV1-7073 | 288.1 | Body |  | U07 |  | 2"-BFW-70-145-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Base Nozzle |  | Closed | A 216 WCB | 3/4", Class 600, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7073 |  | PSV-7073
S-02115 | PSV1-7095 | 288.1 | Body |  | U09 |  | 10"-LPS-70-132-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 7095 |  | PSV-7095
S-02115 | PSV1-7096 | 288.1 | Body |  | U09 |  | 10"-LPS-70-133-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 7096 |  | PSV-7096
S-02115 | PSV1-7097 | 288.1 | Body |  | U09 |  | 10"-LPS-70-197-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 8", Class 150, RF | 10", Class 150, RF | [25 empty] | P | 7097 |  | PSV-7097
S-02115 | PSV1-7104 | 288.1 | Body |  | U22 |  | 1 1/2"-PRC-70-197-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 900, RTJ | 1)", Class 150, RF | [25 empty] | P | 7104 |  | PSV-7104
S-02115 | PSV1-7107 | 288.1 | Body |  | U22 |  | 1 1/2"-PRC-70-199-G40-N |  |  | 71 | 45 | bar g |  | 65 | 100 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 900, RTJ | 1)", Class 150, RF | [25 empty] | P | 7107 |  | PSV-7107
S-02115 | PSV1-7130 | 288.1 | Body |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7130 |  | PSV-7130
S-02115 | PSV1-7131 | 288.1 | Body |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7131 |  | PSV-7131
S-02115 | PSV1-7132 | 288.1 | Body |  | U10 |  | HOLD-LPS-70-120-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 7132 |  | PSV-7132
S-02115 | PSV1-7134 | 288.1 | Body |  | U10 |  | HOLD-LPS-70-122-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 7134 |  | PSV-7134
S-02115 | PSV1-7135 | 288.1 | Body |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7135 |  | PSV-7135
S-02115 | PSV1-7136 | 288.1 | Body |  | U10 |  | HOLD-LPS-70-124-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 7136 |  | PSV-7136
S-02115 | PSV1-7137 | 288.1 | Body |  | U10 |  | HOLD-LPS-70-123-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 1)", Class 300, RF | 1)", Class 150, RF | [25 empty] | P | 7137 |  | PSV-7137
S-02115 | PSV1-7142 | 288.1 | Body |  | U11 |  | BFW-70-165-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 3", Class 600, RF | 4", Class 150, RF | [25 empty] | P | 7142 |  | PSV-7142
S-02115 | PSV1-7143 | 288.1 | Body |  | U11 |  | BFW-70-167-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Full Nozzle | API 526 | Closed | A 216 WCB | 3", Class 600, RF | 4", Class 150, RF | [25 empty] | P | 7143 |  | PSV-7143
S-02115 | PSV1-7165 | 288.1 | Body |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 1500, RTJ | 1)", Class 300, RF | [25 empty] | P | 7165 |  | PSV-7165
S-02115 | PSV1-7168 | 288.1 | Body |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 1500, RTJ | 1)", Class 300, RF | [25 empty] | P | 7168 |  | PSV-7168
S-02115 | PSV1-7171 | 288.1 | Body |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 600, RF | 1)", Class 150, RF | [25 empty] | P | 7171 |  | PSV-7171
S-02115 | PSV1-7174 | 288.1 | Body |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 600, RF | 1)", Class 150, RF | [25 empty] | P | 7174 |  | PSV-7174
S-02115 | PSV1-7195 | 288.1 | Body |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7195 |  | PSV-7195
S-02115 | PSV1-7198 | 288.1 | Body |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7198 |  | PSV-7198
S-02115 | PSV1-7215 | 288.1 | Body |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7215 |  | PSV-7215
S-02115 | PSV1-7218 | 288.1 | Body |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | Full Nozzle | API 526 | Closed | A 351 CF8 | 1)", Class 150, RF | 1)", Class 150, RF | [25 empty] | P | 7218 |  | PSV-7218
S-02115 | PSV1-7253 | 288.1 | Body |  | U16 |  | 4"-LPS-70-134-D24-P |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 2", Class 300, RF | 3", Class 150, RF | [25 empty] | P | 7253 |  | PSV-7253
S-02115 | PSV1-7254 | 288.1 | Body |  | U16 |  | 4"-LPS-70-135-D24-P |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | Full Nozzle | API 526 | Open | A 216 WCB | 2", Class 300, RF | 3", Class 150, RF | [25 empty] | P | 7254 |  | PSV-7254
S-02115 | PSV1-7256 | 288.1 | Body |  | U16 |  | 3/4"-CWR-70-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Base Nozzle | API 526 | Closed | A 216 WCB | 3/4", Class 150, NPT | 1 ", Class 150, NPT | [25 empty] | P | 7256 |  | PSV-7256
S-02115 | PSV2-1008 | 288.2 | Internals |  | P01 |  | 1 1/2"-NG-10-108-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 1008 |  | PSV-1008
S-02115 | PSV2-1009 | 288.2 | Internals |  | P01 |  | 1 1/2"-NG-10-109-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 1009 |  | PSV-1009
S-02115 | PSV2-1013 | 288.2 | Internals |  | P01 |  | 8"-NG-10-110-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Q, 71.3 cm² | SS 316 |  | Yes | [27 empty] | P | 1013 |  | PSV-1013
S-02115 | PSV2-1014 | 288.2 | Internals |  | P01 |  | 8"-NG-10-111-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Q, 71.3 cm² | SS 316 |  | Yes | [27 empty] | P | 1014 |  | PSV-1014
S-02115 | PSV2-1015 | 288.2 | Internals |  | P01 |  | 1 1/2"-NG-10-112-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 1015 |  | PSV-1015
S-02115 | PSV2-1031 | 288.2 | Internals |  | P04 |  | 1 1/2"-PRG-10-102-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 1031 |  | PSV-1031
S-02115 | PSV2-1038 | 288.2 | Internals |  | P04 |  | 1 1/2"-PRG-10-103-F24-H |  |  | 60 | 48.3 | bar g |  | 375 | 410 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 1038 |  | PSV-1038
S-02115 | PSV2-1043 | 288.2 | Internals |  | P04 |  | 1 1/2"-PRG-10-106-F24-H |  |  | 60 | 48.3 | bar g |  | 375 | 410 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 1043 |  | PSV-1043
S-02115 | PSV2-2019 | 288.2 | Internals |  | P02 |  | 2"-HPC-20-104-F24-P |  |  | 52 | 43.5 | bar g |  | 257 | 290 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 2019 |  | PSV-2019
S-02115 | PSV2-2078 | 288.2 | Internals |  | P09 |  | 1 1/2"-HPS-20-103-F24-H |  |  | 52 | 41.1 | bar g |  | 343 | 410 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 2078 |  | PSV-2078
S-02115 | PSV2-2121 | 288.2 | Internals |  | P11 |  | HOLD-LPS-20-104-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 2121 |  | PSV-2121
S-02115 | PSV2-2122 | 288.2 | Internals |  | P11 |  | HOLD-LPS-20-105-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 2122 |  | PSV-2122
S-02115 | PSV2-2171 | 288.2 | Internals |  | P12 |  | HOLD-LPS-20-107-D24-P |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 2171 |  | PSV-2171
S-02115 | PSV2-2172 | 288.2 | Internals |  | P12 |  | HOLD-LPS-20-108-D24-P |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 2172 |  | PSV-2172
S-02115 | PSV2-2354 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-105-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2354 |  | PSV-2354
S-02115 | PSV2-2355 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-107-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2355 |  | PSV-2355
S-02115 | PSV2-2356 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-109-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2356 |  | PSV-2356
S-02115 | PSV2-2357 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-111-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2357 |  | PSV-2357
S-02115 | PSV2-2358 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-113-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2358 |  | PSV-2358
S-02115 | PSV2-2359 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-129-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2359 |  | PSV-2359
S-02115 | PSV2-2360 | 288.2 | Internals |  | P17 |  | 10"-RFG-20-130-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 2360 |  | PSV-2360
S-02115 | PSV2-2376 | 288.2 | Internals |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 21.55 cm² | SS 316 | [29 empty] | P | 2376 |  | PSV-2376
S-02115 | PSV2-2377 | 288.2 | Internals |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 21.55 cm² | SS 316 | [29 empty] | P | 2377 |  | PSV-2377
S-02115 | PSV2-2378 | 288.2 | Internals |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 21.55 cm² | SS 316 | [29 empty] | P | 2378 |  | PSV-2378
S-02115 | PSV2-2379 | 288.2 | Internals |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 21.55 cm² | SS 316 | [29 empty] | P | 2379 |  | PSV-2379
S-02115 | PSV2-2380 | 288.2 | Internals |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 21.55 cm² | SS 316 | [29 empty] | P | 2380 |  | PSV-2380
S-02115 | PSV2-2458 | 288.2 | Internals |  | P20 |  | 3"-DMW-20-102-B50-H |  |  | 14 | 4.5 | bar g |  | 72 | 110 | °C | K, 11.86 cm² | SS 316 | [29 empty] | P | 2458 |  | PSV-2458
S-02115 | PSV2-2494 | 288.2 | Internals |  | P21 |  | 3"-CWR-20-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | J, 8.30 cm² | SS 316 | [29 empty] | P | 2494 |  | PSV-2494
S-02115 | PSV2-2546 | 288.2 | Internals |  | U01 |  | 1 1/2"-N-20-118-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | G, 3.24 cm² | SS 316 | [29 empty] | P | 2546 |  | PSV-2546
S-02115 | PSV2-2555 | 288.2 | Internals |  | U01 |  | 1 1/2"-N-20-119-B24-N |  |  | 7 | 6 | bar g |  | 40 | 75 | °C | G, 3.24 cm² | SS 316 | [29 empty] | P | 2555 |  | PSV-2555
S-02115 | PSV2-2581 | 288.2 | Internals |  | U02 |  | 6"-N-20-120-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 110 | °C | P, 41.2 cm² | SS 316 | [29 empty] | P | 2581 |  | PSV-2581
S-02115 | PSV2-2604 | 288.2 | Internals |  | U17 |  | 1 1/2"-HG-20-104-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | F, 1.98 cm² | SS 316 | [29 empty] | P | 2604 |  | PSV-2604
S-02115 | PSV2-2605 | 288.2 | Internals |  | U17 |  | 1 1/2"-HG-20-106-G24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | F, 1.98 cm² | SS 316 | [29 empty] | P | 2605 |  | PSV-2605
S-02115 | PSV2-3021 | 288.2 | Internals |  | P22 |  | 1 1/2"-SG-30-132-G40-H |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | E, 1.26 cm² | SS 316 | [29 empty] | P | 3021 |  | PSV-3021
S-02115 | PSV2-3047 | 288.2 | Internals |  | P23 |  | 8"-MPS-30-112-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 79.0 cm² | SS 316 | [29 empty] | P | 3047 |  | PSV-3047
S-02115 | PSV2-3048 | 288.2 | Internals |  | P23 |  | 8"-MPS-30-110-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 79.0 cm² | SS 316 | [29 empty] | P | 3048 |  | PSV-3048
S-02115 | PSV2-3057 | 288.2 | Internals |  | P23 |  | 8"-MPS-30-113-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 79.0 cm² | SS 316 | [29 empty] | P | 3057 |  | PSV-3057
S-02115 | PSV2-3143 | 288.2 | Internals |  | P26 |  | 6"-CWR-30-103-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 3143 |  | PSV-3143
S-02115 | PSV2-3146 | 288.2 | Internals |  | P26 |  | 6"-CWR-30-107-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 3146 |  | PSV-3146
S-02115 | PSV2-3149 | 288.2 | Internals |  | P26 |  | 6"-CWR-30-109-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | Q, 71.3 cm² | SS 316 | [29 empty] | P | 3149 |  | PSV-3149
S-02115 | PSV2-3163 | 288.2 | Internals |  | P27 |  | 3"-SG-30-137-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | J, 8.30 cm² | SS 316 | [29 empty] | P | 3163 |  | PSV-3163
S-02115 | PSV2-3173 | 288.2 | Internals |  | P27 |  | 10"-PG-30-105-B24-N |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | T,167.7 cm² | SS 316 |  | Yes | [27 empty] | P | 3173 |  | PSV-3173
S-02115 | PSV2-3174 | 288.2 | Internals |  | P27 |  | 10"-PG-30-107-B24-N |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | T,167.7 cm² | SS 316 |  | Yes | [27 empty] | P | 3174 |  | PSV-3174
S-02115 | PSV2-3196 | 288.2 | Internals |  | P28 |  | 10"-PG-30-103-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | R, 103.2 cm² | SS 316 |  | Yes | [27 empty] | P | 3196 |  | PSV-3196
S-02115 | PSV2-3197 | 288.2 | Internals |  | P28 |  | 10"-PG-30-109-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | R, 103.2 cm² | SS 316 |  | Yes | [27 empty] | P | 3197 |  | PSV-3197
S-02115 | PSV2-3206 | 288.2 | Internals |  | P28 |  | 10"-PG-30-108-B24-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | R, 103.2 cm² | SS 316 |  | Yes | [27 empty] | P | 3206 |  | PSV-3206
S-02115 | PSV2-5006 | 288.2 | Internals |  | P29 |  | HOLD-PMV-50-104-B40-N |  |  | -0.3 | 0 | bar g |  | 46 | 100 | °C | By vendor cm² | By vendor | [29 empty] | P | 5006 |  | PSV-5006
S-02115 | PSV2-5007 | 288.2 | Internals |  | P29 |  | HOLD-PMV-50-102-B40-N |  |  | -0.3 | 0 | bar g |  | 46 | 100 | °C | By vendor cm² | By vendor | [29 empty] | P | 5007 |  | PSV-5007
S-02115 | PSV2-5058 | 288.2 | Internals |  | P30 |  | 10"-PMV-50-111-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | T,167.7 cm² | SS 316 |  | Yes | [27 empty] | P | 5058 |  | PSV-5058
S-02115 | PSV2-5059 | 288.2 | Internals |  | P30 |  | 10"-PMV-50-112-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | T,167.7 cm² | SS 316 |  | Yes | [27 empty] | P | 5059 |  | PSV-5059
S-02115 | PSV2-5060 | 288.2 | Internals |  | P30 |  | 10"-PMV-50-123-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | T,167.7 cm² | SS 316 |  | Yes | [27 empty] | P | 5060 |  | PSV-5060
S-02115 | PSV2-5061 | 288.2 | Internals |  | P30 |  | 10"-PMV-50-124-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | T,167.7 cm² | SS 316 |  | Yes | [27 empty] | P | 5061 |  | PSV-5061
S-02115 | PSV2-5073 | 288.2 | Internals |  | P31 |  | 1 1/2"-LPS-50-101-B24-P |  |  | 9.5 | 2.4 | bar g |  | 138 | 190 | °C | E, 1.26 cm² | SS 316 | [29 empty] | P | 5073 |  | PSV-5073
S-02115 | PSV2-5085 | 288.2 | Internals |  | P31 |  | 3/4"-CWR-70-125-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5085 |  | PSV-5085
S-02115 | PSV2-5108 | 288.2 | Internals |  | P32 |  | 3/4"-CWR-50-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5108 |  | PSV-5108
S-02115 | PSV2-5179 | 288.2 | Internals |  | P34 |  | 6"-PMV-50-131-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | L, 18.41 cm² | SS 316 |  | Yes | [27 empty] | P | 5179 |  | PSV-5179
S-02115 | PSV2-5180 | 288.2 | Internals |  | P34 |  | 6"-PMV-50-132-N24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | L, 18.41 cm² | SS 316 |  | Yes | [27 empty] | P | 5180 |  | PSV-5180
S-02115 | PSV2-5220 | 288.2 | Internals |  | P36 |  | 3/4"-CWR-50-105-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5220 |  | PSV-5220
S-02115 | PSV2-5236 | 288.2 | Internals |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | 1) cm² | SS 316 | [29 empty] | P | 5236 |  | PSV-5236
S-02115 | PSV2-5239 | 288.2 | Internals |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | 1) cm² | SS 316 | [29 empty] | P | 5239 |  | PSV-5239
S-02115 | PSV2-5250 | 288.2 | Internals |  | P38 |  | 10"-PMV-50-151-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | R, 103.2 cm² | SS 316 | [29 empty] | P | 5250 |  | PSV-5250
S-02115 | PSV2-5251 | 288.2 | Internals |  | P38 |  | 10"-PMV-50-152-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | R, 103.2 cm² | SS 316 | [29 empty] | P | 5251 |  | PSV-5251
S-02115 | PSV2-5261 | 288.2 | Internals |  | P38 |  | 10"-PMV-50-193-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | R, 103.2 cm² | SS 316 | [29 empty] | P | 5261 |  | PSV-5261
S-02115 | PSV2-5308 | 288.2 | Internals |  | P39 |  | 3/4"-CWR-50-128-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5308 |  | PSV-5308
S-02115 | PSV2-5339 | 288.2 | Internals |  | P40 |  | 3/4"-CWR-50-108-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5339 |  | PSV-5339
S-02115 | PSV2-5370 | 288.2 | Internals |  | P41 |  | 3/4"-CWR-50-110-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5370 |  | PSV-5370
S-02115 | PSV2-5384 | 288.2 | Internals |  | P42 |  | 3"-PMP-50-180-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | H, 5.06 cm² | SS 316 | [29 empty] | P | 5384 |  | PSV-5384
S-02115 | PSV2-5386 | 288.2 | Internals |  | P42 |  | 3"-PMP-50-194-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | H, 5.06 cm² | SS 316 | [29 empty] | P | 5386 |  | PSV-5386
S-02115 | PSV2-5400 | 288.2 | Internals |  | P43 |  | HOLD-PMV-50-181-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | By vendor cm² | By vendor | [29 empty] | P | 5400 |  | PSV-5400
S-02115 | PSV2-5401 | 288.2 | Internals |  | P43 |  | HOLD-PMV-50-182-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | By vendor cm² | By vendor | [29 empty] | P | 5401 |  | PSV-5401
S-02115 | PSV2-5405 | 288.2 | Internals |  | P43 |  | HOLD-PMP-50-162-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 5405 |  | PSV-5405
S-02115 | PSV2-5417 | 288.2 | Internals |  | P44 |  | HOLD-PMV-50-183-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | By vendor cm² | By vendor | [29 empty] | P | 5417 |  | PSV-5417
S-02115 | PSV2-5418 | 288.2 | Internals |  | P44 |  | HOLD-PMV-50-184-B24-H |  |  | -0.3 | 0 | bar g |  | 48 | 85 | °C | By vendor cm² | By vendor | [29 empty] | P | 5418 |  | PSV-5418
S-02115 | PSV2-5444 | 288.2 | Internals |  | P45 |  | 3/4"-CWR-50-114-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5444 |  | PSV-5444
S-02115 | PSV2-5450 | 288.2 | Internals |  | P45 |  | HOLD-PMV-50-190-B24-H |  |  | -0.3 | 0.01 | bar g |  | 48 | 85 | °C | By vendor cm² | By vendor | [29 empty] | P | 5450 |  | PSV-5450
S-02115 | PSV2-5451 | 288.2 | Internals |  | P45 |  | HOLD-PMV-50-191-B24-H |  |  | -0.3 | 0.01 | bar g |  | 48 | 85 | °C | By vendor cm² | By vendor | [29 empty] | P | 5451 |  | PSV-5451
S-02115 | PSV2-5461 | 288.2 | Internals |  | P45 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 5461 |  | PSV-5461
S-02115 | PSV2-5462 | 288.2 | Internals |  | P45 |  | 2"-LOS-50-123-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 5462 |  | PSV-5462
S-02115 | PSV2-5501 | 288.2 | Internals |  | U23A |  | 3/4"-CWR-50-119-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 5501 |  | PSV-5501
S-02115 | PSV2-5505 | 288.2 | Internals |  | U23A |  | 6"-PMW-50-142-B24-N |  |  | 7.5 | 1.5 | bar g |  | 62 | 100 | °C | H, 5.06 cm² | SS 316 | [29 empty] | P | 5505 |  | PSV-5505
S-02115 | PSV2-5512 | 288.2 | Internals |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 5512 |  | PSV-5512
S-02115 | PSV2-5514 | 288.2 | Internals |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 5514 |  | PSV-5514
S-02115 | PSV2-6021 | 288.2 | Internals |  | P06 |  | 1 1/2"-PRC-60-196-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 6021 |  | PSV-6021
S-02115 | PSV2-6022 | 288.2 | Internals |  | P06 |  | 1 1/2"-PRC-60-195-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 6022 |  | PSV-6022
S-02115 | PSV2-6027 | 288.2 | Internals |  | P06 |  | 1 1/2"-MPS-60-103-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | E, 1.26 cm² | SS 316 | [29 empty] | P | 6027 |  | PSV-6027
S-02115 | PSV2-6053 | 288.2 | Internals |  | P07 |  | 1 1/2"-PRG-60-124-F24-H |  |  | 55 | 42.8 | bar g |  | 226 | 290 | °C | E, 1.26 cm² | SS 316 | [29 empty] | P | 6053 |  | PSV-6053
S-02115 | PSV2-6056 | 288.2 | Internals |  | P07 |  | 1 1/2"-PRG-10-125-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 6056 |  | PSV-6056
S-02115 | PSV2-6085 | 288.2 | Internals |  | P08 |  | 3/4"-CWR-60-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 6085 |  | PSV-6085
S-02115 | PSV2-7010 | 288.2 | Internals |  | U03 |  | 10"-HPS-70-110-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | 103.2 cm² | SS 316 | [29 empty] | P | 7010 |  | PSV-7010
S-02115 | PSV2-7011 | 288.2 | Internals |  | U03 |  | 10"-HPS-70-112-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | 103.2 cm² | SS 316 | [29 empty] | P | 7011 |  | PSV-7011
S-02115 | PSV2-7012 | 288.2 | Internals |  | U03 |  | 10"-HPS-70-114-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | 124.4 cm² | SS 316 | [29 empty] | P | 7012 |  | PSV-7012
S-02115 | PSV2-7013 | 288.2 | Internals |  | U03 |  | 2"-BFW-70-106-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7013 |  | PSV-7013
S-02115 | PSV2-7014 | 288.2 | Internals |  | U03 |  | 3"-BFW-70-144-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7014 |  | PSV-7014
S-02115 | PSV2-7015 | 288.2 | Internals |  | U03 |  | 3"-BFW-70-142-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7015 |  | PSV-7015
S-02115 | PSV2-7016 | 288.2 | Internals |  | U04 |  | 2"-BFW-70-158-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7016 |  | PSV-7016
S-02115 | PSV2-7017 | 288.2 | Internals |  | U04 |  | 2"-BFW-70-157-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7017 |  | PSV-7017
S-02115 | PSV2-7023 | 288.2 | Internals |  | U04 |  | 10"-HPS-70-134-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | 124.4 cm² | SS 316 | [29 empty] | P | 7023 |  | PSV-7023
S-02115 | PSV2-7024 | 288.2 | Internals |  | U04 |  | 10"-HPS-70-135-F34-H |  |  | 52 | 44 | bar g |  | 410 | 470 | °C | 124.4 cm² | SS 316 | [29 empty] | P | 7024 |  | PSV-7024
S-02115 | PSV2-7032 | 288.2 | Internals |  | U05 |  | 2"-BFW-70-109-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7032 |  | PSV-7032
S-02115 | PSV2-7033 | 288.2 | Internals |  | U05 |  | 2"-BFW-70-111-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7033 |  | PSV-7033
S-02115 | PSV2-7036 | 288.2 | Internals |  | U05 |  | 1 1/2"-MPS-70-122-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7036 |  | PSV-7036
S-02115 | PSV2-7037 | 288.2 | Internals |  | U05 |  | 1 1/2"-MPS-70-123-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7037 |  | PSV-7037
S-02115 | PSV2-7052 | 288.2 | Internals |  | U06 |  | 2"-BFW-70-122-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7052 |  | PSV-7052
S-02115 | PSV2-7053 | 288.2 | Internals |  | U06 |  | 2"-BFW-70-123-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7053 |  | PSV-7053
S-02115 | PSV2-7057 | 288.2 | Internals |  | U06 |  | 10"-LPS-70-111-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7057 |  | PSV-7057
S-02115 | PSV2-7058 | 288.2 | Internals |  | U06 |  | 10"-LPS-70-110-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7058 |  | PSV-7058
S-02115 | PSV2-7059 | 288.2 | Internals |  | U06 |  | 10"-LPS-70-113-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7059 |  | PSV-7059
S-02115 | PSV2-7060 | 288.2 | Internals |  | U06 |  | 10"-LPS-70-141-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7060 |  | PSV-7060
S-02115 | PSV2-7061 | 288.2 | Internals |  | U06 |  | 10"-LPS-70-140-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7061 |  | PSV-7061
S-02115 | PSV2-7072 | 288.2 | Internals |  | U07 |  | 2"-BFW-70-124-F24-H |  |  | 80 | 50 | bar g |  | 122 | 160 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7072 |  | PSV-7072
S-02115 | PSV2-7073 | 288.2 | Internals |  | U07 |  | 2"-BFW-70-145-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7073 |  | PSV-7073
S-02115 | PSV2-7095 | 288.2 | Internals |  | U09 |  | 10"-LPS-70-132-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7095 |  | PSV-7095
S-02115 | PSV2-7096 | 288.2 | Internals |  | U09 |  | 10"-LPS-70-133-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7096 |  | PSV-7096
S-02115 | PSV2-7097 | 288.2 | Internals |  | U09 |  | 10"-LPS-70-197-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | T,167.7 cm² | SS 316 | [29 empty] | P | 7097 |  | PSV-7097
S-02115 | PSV2-7104 | 288.2 | Internals |  | U22 |  | 1 1/2"-PRC-70-197-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | 1) cm² | SS 316 | [29 empty] | P | 7104 |  | PSV-7104
S-02115 | PSV2-7107 | 288.2 | Internals |  | U22 |  | 1 1/2"-PRC-70-199-G40-N |  |  | 71 | 45 | bar g |  | 65 | 100 | °C | 1) cm² | SS 316 | [29 empty] | P | 7107 |  | PSV-7107
S-02115 | PSV2-7130 | 288.2 | Internals |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 1) cm² | SS 316 | [29 empty] | P | 7130 |  | PSV-7130
S-02115 | PSV2-7131 | 288.2 | Internals |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 1) cm² | SS 316 | [29 empty] | P | 7131 |  | PSV-7131
S-02115 | PSV2-7132 | 288.2 | Internals |  | U10 |  | HOLD-LPS-70-120-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 7132 |  | PSV-7132
S-02115 | PSV2-7134 | 288.2 | Internals |  | U10 |  | HOLD-LPS-70-122-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 7134 |  | PSV-7134
S-02115 | PSV2-7135 | 288.2 | Internals |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 1) cm² | SS 316 | [29 empty] | P | 7135 |  | PSV-7135
S-02115 | PSV2-7136 | 288.2 | Internals |  | U10 |  | HOLD-LPS-70-124-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 7136 |  | PSV-7136
S-02115 | PSV2-7137 | 288.2 | Internals |  | U10 |  | HOLD-LPS-70-123-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) cm² | SS 316 | [29 empty] | P | 7137 |  | PSV-7137
S-02115 | PSV2-7142 | 288.2 | Internals |  | U11 |  | BFW-70-165-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | K, 11.86 cm² | SS 316 | [29 empty] | P | 7142 |  | PSV-7142
S-02115 | PSV2-7143 | 288.2 | Internals |  | U11 |  | BFW-70-167-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | K, 11.86 cm² | SS 316 | [29 empty] | P | 7143 |  | PSV-7143
S-02115 | PSV2-7165 | 288.2 | Internals |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7165 |  | PSV-7165
S-02115 | PSV2-7168 | 288.2 | Internals |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7168 |  | PSV-7168
S-02115 | PSV2-7171 | 288.2 | Internals |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7171 |  | PSV-7171
S-02115 | PSV2-7174 | 288.2 | Internals |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7174 |  | PSV-7174
S-02115 | PSV2-7195 | 288.2 | Internals |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7195 |  | PSV-7195
S-02115 | PSV2-7198 | 288.2 | Internals |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7198 |  | PSV-7198
S-02115 | PSV2-7215 | 288.2 | Internals |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7215 |  | PSV-7215
S-02115 | PSV2-7218 | 288.2 | Internals |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) cm² | SS 316 | [29 empty] | P | 7218 |  | PSV-7218
S-02115 | PSV2-7253 | 288.2 | Internals |  | U16 |  | 4"-LPS-70-134-D24-P |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | J, 8.30 cm² | SS 316 | [29 empty] | P | 7253 |  | PSV-7253
S-02115 | PSV2-7254 | 288.2 | Internals |  | U16 |  | 4"-LPS-70-135-D24-P |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | J, 8.30 cm² | SS 316 | [29 empty] | P | 7254 |  | PSV-7254
S-02115 | PSV2-7256 | 288.2 | Internals |  | U16 |  | 3/4"-CWR-70-102-B24-N |  |  | 7.5 | 1.5 | bar g |  | 48 | 100 | °C | D, 0.71 cm² | SS 316 | [29 empty] | P | 7256 |  | PSV-7256
S-02115 | PSV3-1008 | 288.99 | Remark: |  | P01 |  | 1 1/2"-NG-10-108-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 1) | At relieving conditions there | is no flow so minimum size PSV | is choosen | [27 empty] | P | 1008 |  | PSV-1008
S-02115 | PSV3-1009 | 288.99 | Remark: |  | P01 |  | 1 1/2"-NG-10-109-F24-N |  |  | 55 | 50 | bar g |  | 40 | 85 | °C | 1) | At relieving conditions there | is no flow so minimum size PSV | is choosen | PSV-1009 is spare | [26 empty] | P | 1009 |  | PSV-1009
S-02115 | PSV3-1013 | 288.99 | Remark: |  | P01 |  | 8"-NG-10-110-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | [28 empty] | P | 1013 |  | PSV-1013
S-02115 | PSV3-1014 | 288.99 | Remark: |  | P01 |  | 8"-NG-10-111-B24-N |  |  | 7 | 4 | bar g |  | 35 | 85 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | PSV-1014 is spare | [27 empty] | P | 1014 |  | PSV-1014
S-02115 | PSV3-1015 | 288.99 | Remark: |  | P01 |  | 1 1/2"-NG-10-112-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 1) | Exposed area = 9 m2 | F'= 0.01 | [28 empty] | P | 1015 |  | PSV-1015
S-02115 | PSV3-1031 | 288.99 | Remark: |  | P04 |  | 1 1/2"-PRG-10-102-F24-H |  |  | 55 | 48.8 | bar g |  | 380 | 410 | °C | 1) | Exposed area = 20 m2 | F'= 0.01 | [28 empty] | P | 1031 |  | PSV-1031
S-02115 | PSV3-1038 | 288.99 | Remark: |  | P04 |  | 1 1/2"-PRG-10-103-F24-H |  |  | 60 | 48.3 | bar g |  | 375 | 410 | °C | 1) | Exposed area = 20 m2 | F'= 0.01 | [28 empty] | P | 1038 |  | PSV-1038
S-02115 | PSV3-1043 | 288.99 | Remark: |  | P04 |  | 1 1/2"-PRG-10-106-F24-H |  |  | 60 | 48.3 | bar g |  | 375 | 410 | °C | 1) | Exposed area = 20 m2 | F'= 0.01 | [28 empty] | P | 1043 |  | PSV-1043
S-02115 | PSV3-2078 | 288.99 | Remark: |  | P09 |  | 1 1/2"-HPS-20-103-F24-H |  |  | 52 | 41.1 | bar g |  | 343 | 410 | °C | 1) | At relieving conditions there | is no flow so minimum size PSV | is choosen | [27 empty] | P | 2078 |  | PSV-2078
S-02115 | PSV3-2121 | 288.99 | Remark: |  | P11 |  | HOLD-LPS-20-104-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 1) Capacity and sizing by | FT 2002 vendor | [29 empty] | P | 2121 |  | PSV-2121
S-02115 | PSV3-2122 | 288.99 | Remark: |  | P11 |  | HOLD-LPS-20-105-D24-H |  |  | 9.5 | 7.5 | bar g |  | 194 | 340 | °C | 1) Capacity and sizing by | FT 2002 vendor | PSV-2122 is spare | [28 empty] | P | 2122 |  | PSV-2122
S-02115 | PSV3-2171 | 288.99 | Remark: |  | P12 |  | HOLD-LPS-20-107-D24-P |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 1) Capacity and sizing by | FT 2001 vendor | [29 empty] | P | 2171 |  | PSV-2171
S-02115 | PSV3-2172 | 288.99 | Remark: |  | P12 |  | HOLD-LPS-20-108-D24-P |  |  | 9.5 | 7.5 | bar g |  | 204 | 340 | °C | 1) Capacity and sizing by | FT 2001 vendor | PSV-2172 is spare | [28 empty] | P | 2172 |  | PSV-2172
S-02115 | PSV3-2354 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-105-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | Contingencies considered: | Tube rupture E 2020 | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2354 |  | PSV-2354
S-02115 | PSV3-2355 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-107-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | Contingencies considered: | Tube rupture E 2020 | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2355 |  | PSV-2355
S-02115 | PSV3-2356 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-109-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | Contingencies considered: | Tube rupture E 2020 | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2356 |  | PSV-2356
S-02115 | PSV3-2357 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-111-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | Contingencies considered: | Tube rupture E 2020 | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2357 |  | PSV-2357
S-02115 | PSV3-2358 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-113-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | Contingencies considered: | Tube rupture E 2020 | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2358 |  | PSV-2358
S-02115 | PSV3-2359 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-129-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | Contingencies considered: | Tube rupture E 2020 | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2359 |  | PSV-2359
S-02115 | PSV3-2360 | 288.99 | Remark: |  | P17 |  | 10"-RFG-20-130-D34-H |  |  | 29 | 26.3 | bar g |  | 360 | 390 | °C | The total relieving capacity | 870000 Nm3/h is shared by | PSV-2354, -2355, -2356, -2357, | -2358-2359 | PSV-2360 is spare |  | Note that inlet flange rating | Class 600 differs from piping | [23 empty] | P | 2360 |  | PSV-2360
S-02115 | PSV3-2376 | 288.99 | Remark: |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Two ring blowdown adjustment | the total relieving capacity | 430000 kg/h is shared by | PSV-2376, -2377, -2378 & -2379 | Vendor to confirm inlet/outlet | sizes, area and ratings | [25 empty] | P | 2376 |  | PSV-2376
S-02115 | PSV3-2377 | 288.99 | Remark: |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Two ring blowdown adjustment | the total relieving capacity | 430000 kg/h is shared by | PSV-2376, -2377, -2378 & -2379 | Vendor to confirm inlet/outlet | sizes, area and ratings | [25 empty] | P | 2377 |  | PSV-2377
S-02115 | PSV3-2378 | 288.99 | Remark: |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Two ring blowdown adjustment | the total relieving capacity | 430000 kg/h is shared by | PSV-2376, -2377, -2378 & -2379 | Vendor to confirm inlet/outlet | sizes, area and ratings | [25 empty] | P | 2378 |  | PSV-2378
S-02115 | PSV3-2379 | 288.99 | Remark: |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Two ring blowdown adjustment | the total relieving capacity | 430000 kg/h is shared by | PSV-2376, -2377, -2378 & -2379 | Vendor to confirm inlet/outlet | sizes, area and ratings | [25 empty] | P | 2379 |  | PSV-2379
S-02115 | PSV3-2380 | 288.99 | Remark: |  | P18 |  | D 2001 |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | Two ring blowdown adjustment | the total relieving capacity | 430000 kg/h is shared by | PSV-2376, -2377, -2378 & -2379 | Vendor to confirm inlet/outlet | sizes, area and ratings | PSV-2380 is spare | [24 empty] | P | 2380 |  | PSV-2380
S-02115 | PSV3-2546 | 288.99 | Remark: |  | U01 |  | 1 1/2"-N-20-118-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | Capacity to be checked against | actual selected Cv of control | valve | [28 empty] | P | 2546 |  | PSV-2546
S-02115 | PSV3-2555 | 288.99 | Remark: |  | U01 |  | 1 1/2"-N-20-119-B24-N |  |  | 7 | 6 | bar g |  | 40 | 75 | °C | Capacity to be checked against | actual selected Cv of control | valve | PSV-2555 is spare | [27 empty] | P | 2555 |  | PSV-2555
S-02115 | PSV3-2581 | 288.99 | Remark: |  | U02 |  | 6"-N-20-120-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 110 | °C | 1) Capacity to be confirmed by | C 2001 vendor | [29 empty] | P | 2581 |  | PSV-2581
S-02115 | PSV3-2604 | 288.99 | Remark: |  | U17 |  | 1 1/2"-HG-20-104-F24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Capacity to be checked against | actual selected Cv of control | valve | [28 empty] | P | 2604 |  | PSV-2604
S-02115 | PSV3-2605 | 288.99 | Remark: |  | U17 |  | 1 1/2"-HG-20-106-G24-N |  |  | 60 | 50.4 | bar g |  | 48 | 200 | °C | Capacity to be checked against | actual selected Cv of control | valve | PSV-2605 is spare | [27 empty] | P | 2605 |  | PSV-2605
S-02115 | PSV3-3021 | 288.99 | Remark: |  | P22 |  | 1 1/2"-SG-30-132-G40-H |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 1) | Exposed area = 20 m2 | F'= 0.03 | [28 empty] | P | 3021 |  | PSV-3021
S-02115 | PSV3-3047 | 288.99 | Remark: |  | P23 |  | 8"-MPS-30-112-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Two ring blowdown adjustment | the total relieving capacity | 310000 kg/h is shared by | PSV-3047 & -3048 | Vendor to confirm inlet/outlet | sizes, area and ratings | Contingiencies considered: | Tube rupture R 3001 | [23 empty] | P | 3047 |  | PSV-3047
S-02115 | PSV3-3048 | 288.99 | Remark: |  | P23 |  | 8"-MPS-30-110-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Two ring blowdown adjustment | the total relieving capacity | 310000 kg/h is shared by | PSV-3047 & -3048 | Vendor to confirm inlet/outlet | sizes, area and ratings | Contingiencies considered: | Tube rupture R 3001 | [23 empty] | P | 3048 |  | PSV-3048
S-02115 | PSV3-3057 | 288.99 | Remark: |  | P23 |  | 8"-MPS-30-113-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | Two ring blowdown adjustment | the total relieving capacity | 310000 kg/h is shared by | PSV-3047 & -3048 | Vendor to confirm inlet/outlet | sizes, area and ratings | PSV-3057 is spare | [24 empty] | P | 3057 |  | PSV-3057
S-02115 | PSV3-3163 | 288.99 | Remark: |  | P27 |  | 3"-SG-30-137-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 1) | Exposed area = 113 m2 | F'= 0.03 | [28 empty] | P | 3163 |  | PSV-3163
S-02115 | PSV3-3173 | 288.99 | Remark: |  | P27 |  | 10"-PG-30-105-B24-N |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | Note that inlet flange rating | Class 300 differs from piping | [26 empty] | P | 3173 |  | PSV-3173
S-02115 | PSV3-3174 | 288.99 | Remark: |  | P27 |  | 10"-PG-30-107-B24-N |  |  | 7 | 4 | bar g |  | 47 | 100 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | Note that inlet flange rating | Class 300 differs from piping | PSV-3174 is spare | [25 empty] | P | 3174 |  | PSV-3174
S-02115 | PSV3-3196 | 288.99 | Remark: |  | P28 |  | 10"-PG-30-103-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Max. gas breakthrough FO-3191 | The total relieving capacity | 160000 Nm3/h is shared by | PSV-3196 & -3197 | Capacity to be confirmed | Note that inlet flange rating | Class 300 differs from piping | [24 empty] | P | 3196 |  | PSV-3196
S-02115 | PSV3-3197 | 288.99 | Remark: |  | P28 |  | 10"-PG-30-109-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Max. gas breakthrough FO-3191 | The total relieving capacity | 160000 Nm3/h is shared by | PSV-3196 & -3197 | Capacity to be confirmed | Note that inlet flange rating | Class 300 differs from piping | [24 empty] | P | 3197 |  | PSV-3197
S-02115 | PSV3-3206 | 288.99 | Remark: |  | P28 |  | 10"-PG-30-108-B24-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | Max. gas breakthrough FO-3191 | The total relieving capacity | 160000 Nm3/h is shared by | PSV-3196 & -3197 | Capacity to be confirmed | Note that inlet flange rating | Class 300 differs from piping | PSV-3206 is spare | [23 empty] | P | 3206 |  | PSV-3206
S-02115 | PSV3-5006 | 288.99 | Remark: |  | P29 |  | HOLD-PMV-50-104-B40-N |  |  | -0.3 | 0 | bar g |  | 46 | 100 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | Contingencies considered: | Fire- wetted (12000 Nm3/h) | [26 empty] | P | 5006 |  | PSV-5006
S-02115 | PSV3-5058 | 288.99 | Remark: |  | P30 |  | 10"-PMV-50-111-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | The total relieving capacity | 89000 Nm3/h is shared by | PSV-5058, -5059 & -5060 | Kb=0.9 | Contingencies considered: | Tube rupture E 2024, E 5001 | Fire - wetted | [24 empty] | P | 5058 |  | PSV-5058
S-02115 | PSV3-5059 | 288.99 | Remark: |  | P30 |  | 10"-PMV-50-112-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | The total relieving capacity | 89000 Nm3/h is shared by | PSV-5058, -5059 & -5060 | Kb=0.9 | Contingencies considered: | Tube rupture E 2024, E 5001 | Fire - wetted | [24 empty] | P | 5059 |  | PSV-5059
S-02115 | PSV3-5060 | 288.99 | Remark: |  | P30 |  | 10"-PMV-50-123-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | The total relieving capacity | 89000 Nm3/h is shared by | PSV-5058, -5059 & -5060 | Kb=0.9 | Contingencies considered: | Tube rupture E 2024, E 5001 | Fire - wetted | [24 empty] | P | 5060 |  | PSV-5060
S-02115 | PSV3-5061 | 288.99 | Remark: |  | P30 |  | 10"-PMV-50-124-B24-P |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | The total relieving capacity | 89000 Nm3/h is shared by | PSV-5058, -5059 & -5060 | Kb=0.9 | PSV-5061 is spare | [26 empty] | P | 5061 |  | PSV-5061
S-02115 | PSV3-5179 | 288.99 | Remark: |  | P34 |  | 6"-PMV-50-131-B24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | Contingencies considered: | Reflux failure | Tube rupture E 5002 | [28 empty] | P | 5179 |  | PSV-5179
S-02115 | PSV3-5180 | 288.99 | Remark: |  | P34 |  | 6"-PMV-50-132-N24-P |  |  | 3.5 | 0.1 | bar g |  | 67 | 150 | °C | Contingencies considered: | Reflux failure | Tube rupture E 5002 |  | PSV-5180 is spare | [26 empty] | P | 5180 |  | PSV-5180
S-02115 | PSV3-5236 | 288.99 | Remark: |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | 1) Capacity and sizing by | P 5080 A vendor | [29 empty] | P | 5236 |  | PSV-5236
S-02115 | PSV3-5239 | 288.99 | Remark: |  | U15 |  | 1 1/2"-MOR-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 65 | °C | 1) Capacity and sizing by | P 5080 B vendor | [29 empty] | P | 5239 |  | PSV-5239
S-02115 | PSV3-5250 | 288.99 | Remark: |  | P38 |  | 10"-PMV-50-151-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | The total relieving capacity | 82805 Nm3/h is shared by | PSV-5250 & -5251 |  | Contingencies considered: | Fire - wetted | Tube rupture E 2023, E 5003 | [24 empty] | P | 5250 |  | PSV-5250
S-02115 | PSV3-5251 | 288.99 | Remark: |  | P38 |  | 10"-PMV-50-152-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | The total relieving capacity | 82805 Nm3/h is shared by | PSV-5250 & -5251 |  | Contingencies considered: | Fire - wetted | Tube rupture E 2023, E 5003 | [24 empty] | P | 5251 |  | PSV-5251
S-02115 | PSV3-5261 | 288.99 | Remark: |  | P38 |  | 10"-PMV-50-193-B24-H |  |  | 6 | 2.7 | bar g |  | 102 | 165 | °C | The total relieving capacity | 82805 Nm3/h is shared by | PSV-5250 & -5251 | PSV-5261 is spare | [27 empty] | P | 5261 |  | PSV-5261
S-02115 | PSV3-5405 | 288.99 | Remark: |  | P43 |  | HOLD-PMP-50-162-F24-N |  |  | 52 | 47 | bar g |  | 48 | 75 | °C | 1) Capacity and sizing by | P 5012 vendor | [29 empty] | P | 5405 |  | PSV-5405
S-02115 | PSV3-5450 | 288.99 | Remark: |  | P45 |  | HOLD-PMV-50-190-B24-H |  |  | -0.3 | 0.01 | bar g |  | 48 | 85 | °C | Contingiencies considered: | Gasbreakthrough from 1" hand- | valve outlet D 1001 (P01) | (10000Nm3/h MW=16.74, Z=0.93, | Cp/Cv=1.28 assuming Cv= 11 to | be confirmed) | [25 empty] | P | 5450 |  | PSV-5450
S-02115 | PSV3-5461 | 288.99 | Remark: |  | P45 |  | 2"-LOS-50-122-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 1) Capacity and sizing by | P 5009 A vendor | [29 empty] | P | 5461 |  | PSV-5461
S-02115 | PSV3-5462 | 288.99 | Remark: |  | P45 |  | 2"-LOS-50-123-F24-N |  |  | 60 | 53 | bar g |  | 50 | 75 | °C | 1) Capacity and sizing by | P 5009 A vendor | [29 empty] | P | 5462 |  | PSV-5462
S-02115 | PSV3-5512 | 288.99 | Remark: |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 5070 A vendor |  | Alternative option | [27 empty] | P | 5512 |  | PSV-5512
S-02115 | PSV3-5514 | 288.99 | Remark: |  | U24 |  | 1 1/2"-NS-50-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 5070 A vendor |  | Alternative option | [27 empty] | P | 5514 |  | PSV-5514
S-02115 | PSV3-6021 | 288.99 | Remark: |  | P06 |  | 1 1/2"-PRC-60-196-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 1) | At relieving conditions there | is no flow so minimum size PSV | is choosen | [27 empty] | P | 6021 |  | PSV-6021
S-02115 | PSV3-6022 | 288.99 | Remark: |  | P06 |  | 1 1/2"-PRC-60-195-G40-H |  |  | 71 | 44 | bar g |  | 119 | 180 | °C | 1) | At relieving conditions there | is no flow so minimum size PSV | is choosen | [27 empty] | P | 6022 |  | PSV-6022
S-02115 | PSV3-6056 | 288.99 | Remark: |  | P07 |  | 1 1/2"-PRG-10-125-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 1) | At relieving conditions there | is no flow so minimum size PSV | is choosen | [27 empty] | P | 6056 |  | PSV-6056
S-02115 | PSV3-7010 | 288.99 | Remark: |  | U03 |  | 10"-HPS-70-110-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=587 | Total required capacity | 509000 kg/h to be split | between PSV-7010 & -7011 | [25 empty] | P | 7010 |  | PSV-7010
S-02115 | PSV3-7011 | 288.99 | Remark: |  | U03 |  | 10"-HPS-70-112-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=587 | Total required capacity | 509000 kg/h to be split | between PSV-7010 & -7011 | [25 empty] | P | 7011 |  | PSV-7011
S-02115 | PSV3-7012 | 288.99 | Remark: |  | U03 |  | 10"-HPS-70-114-F24-H |  |  | 52 | 44 | bar g |  | 345 | 470 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=587 | Total required capacity | 509000 kg/h to be split | between PSV-7010 & -7011 | PSV-7012 is spare | [24 empty] | P | 7012 |  | PSV-7012
S-02115 | PSV3-7013 | 288.99 | Remark: |  | U03 |  | 2"-BFW-70-106-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | PSV may not be required | depending on design of | PV-7002 A | [28 empty] | P | 7013 |  | PSV-7013
S-02115 | PSV3-7014 | 288.99 | Remark: |  | U03 |  | 3"-BFW-70-144-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | PSV may not be required | depending on design of | PV-7002 B | [28 empty] | P | 7014 |  | PSV-7014
S-02115 | PSV3-7015 | 288.99 | Remark: |  | U03 |  | 3"-BFW-70-142-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | PSV may not be required | depending on design of | PV-7002 C | [28 empty] | P | 7015 |  | PSV-7015
S-02115 | PSV3-7016 | 288.99 | Remark: |  | U04 |  | 2"-BFW-70-158-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | PSV may not be required | depending on design of | PV-7025 A | [28 empty] | P | 7016 |  | PSV-7016
S-02115 | PSV3-7017 | 288.99 | Remark: |  | U04 |  | 2"-BFW-70-157-H34-H |  |  | 170 |  | bar g |  | 122 | 353 | °C | PSV may not be required | depending on design of | PV-7025 B | [28 empty] | P | 7017 |  | PSV-7017
S-02115 | PSV3-7023 | 288.99 | Remark: |  | U04 |  | 10"-HPS-70-134-F34-H |  |  | 52 | 43 | bar g |  | 410 | 470 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=316 | [28 empty] | P | 7023 |  | PSV-7023
S-02115 | PSV3-7024 | 288.99 | Remark: |  | U04 |  | 10"-HPS-70-135-F34-H |  |  | 52 | 44 | bar g |  | 410 | 470 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=316 | [28 empty] | P | 7024 |  | PSV-7024
S-02115 | PSV3-7032 | 288.99 | Remark: |  | U05 |  | 2"-BFW-70-109-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | PSV may not be required | depending on design of | PV-7031 A | [28 empty] | P | 7032 |  | PSV-7032
S-02115 | PSV3-7033 | 288.99 | Remark: |  | U05 |  | 2"-BFW-70-111-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | PSV may not be required | depending on design of | PV-7031 B | [28 empty] | P | 7033 |  | PSV-7033
S-02115 | PSV3-7036 | 288.99 | Remark: |  | U05 |  | 1 1/2"-MPS-70-122-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 1) | No flow at relieving condition | so min. size PSV choosen | [28 empty] | P | 7036 |  | PSV-7036
S-02115 | PSV3-7037 | 288.99 | Remark: |  | U05 |  | 1 1/2"-MPS-70-123-F24-H |  |  | 45 | 32.7 | bar g |  | 240 | 300 | °C | 1) | No flow at relieving condition | so min. size PSV choosen | PSV-7037 is spare | [27 empty] | P | 7037 |  | PSV-7037
S-02115 | PSV3-7052 | 288.99 | Remark: |  | U06 |  | 2"-BFW-70-122-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | PSV may not be required | depending on design of | PV-7051 A | [28 empty] | P | 7052 |  | PSV-7052
S-02115 | PSV3-7053 | 288.99 | Remark: |  | U06 |  | 2"-BFW-70-123-F24-H |  |  | 80 |  | bar g |  | 122 | 296 | °C | PSV may not be required | depending on design of | PV-7051 B | [28 empty] | P | 7053 |  | PSV-7053
S-02115 | PSV3-7057 | 288.99 | Remark: |  | U06 |  | 10"-LPS-70-111-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=720 | Total required capacity | 320250 kg/h to be split | between PSV-7057, -7058, | -7059-7060 | [24 empty] | P | 7057 |  | PSV-7057
S-02115 | PSV3-7058 | 288.99 | Remark: |  | U06 |  | 10"-LPS-70-110-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=720 | Total required capacity | 320250 kg/h to be split | between PSV-7057, -7058, | -7059-7060 | [24 empty] | P | 7058 |  | PSV-7058
S-02115 | PSV3-7059 | 288.99 | Remark: |  | U06 |  | 10"-LPS-70-113-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=720 | Total required capacity | 320250 kg/h to be split | between PSV-7057, -7058, | -7059-7060 | [24 empty] | P | 7059 |  | PSV-7059
S-02115 | PSV3-7060 | 288.99 | Remark: |  | U06 |  | 10"-LPS-70-141-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=720 | Total required capacity | 320250 kg/h to be split | between PSV-7057, -7058, | -7059-7060 | [24 empty] | P | 7060 |  | PSV-7060
S-02115 | PSV3-7061 | 288.99 | Remark: |  | U06 |  | 10"-LPS-70-140-D24-P |  |  | 9.5 | 7 | bar g |  | 230 | 340 | °C | Capacity to be checked against | actual selected Cv of control | valves. Total Cv=720 | Total required capacity | 320250 kg/h to be split | between PSV-7057, -7058, | -7059-7060 | PSV-7061 is spare | [23 empty] | P | 7061 |  | PSV-7061
S-02115 | PSV3-7095 | 288.99 | Remark: |  | U09 |  | 10"-LPS-70-132-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | The total relieving capacity | 64000 kg/h is shared by | PSV-7095 & -7096 |  | Contingencies considered: | Blocked outlet, fire, | inadvertent opening of inlet | valves | [23 empty] | P | 7095 |  | PSV-7095
S-02115 | PSV3-7096 | 288.99 | Remark: |  | U09 |  | 10"-LPS-70-133-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | The total relieving capacity | 64000 kg/h is shared by | PSV-7095 & -7096 |  | Contingencies considered: | Blocked outlet, fire, | inadvertent opening of inlet | valves | [23 empty] | P | 7096 |  | PSV-7096
S-02115 | PSV3-7097 | 288.99 | Remark: |  | U09 |  | 10"-LPS-70-197-B24-H |  |  | 3.5 | 1 | bar g |  | 120 | 340 | °C | The total relieving capacity | 64000 kg/h is shared by | PSV-7095 & -7096 |  | PSV-7097 is spare | [26 empty] | P | 7097 |  | PSV-7097
S-02115 | PSV3-7104 | 288.99 | Remark: |  | U22 |  | 1 1/2"-PRC-70-197-G40-N |  |  | 71 | 46 | bar g |  | 65 | 100 | °C | 1) Capacity and sizing by | P 7004 A vendor | [29 empty] | P | 7104 |  | PSV-7104
S-02115 | PSV3-7107 | 288.99 | Remark: |  | U22 |  | 1 1/2"-PRC-70-199-G40-N |  |  | 71 | 45 | bar g |  | 65 | 100 | °C | 1) Capacity and sizing by | P 7004 A vendor | [29 empty] | P | 7107 |  | PSV-7107
S-02115 | PSV3-7130 | 288.99 | Remark: |  | U10 |  | 14"-BFW-70-151-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 1) Capacity and sizing by | P 7001 A vendor | [29 empty] | P | 7130 |  | PSV-7130
S-02115 | PSV3-7131 | 288.99 | Remark: |  | U10 |  | 14"-BFW-70-135-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 1) Capacity and sizing by | P 7001 B vendor | [29 empty] | P | 7131 |  | PSV-7131
S-02115 | PSV3-7132 | 288.99 | Remark: |  | U10 |  | HOLD-LPS-70-120-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) Capacity and sizing by | FP 7001 A vendor | [29 empty] | P | 7132 |  | PSV-7132
S-02115 | PSV3-7134 | 288.99 | Remark: |  | U10 |  | HOLD-LPS-70-122-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) Capacity and sizing by | FP 7001 A vendor | PSV-7134 is spare | [28 empty] | P | 7134 |  | PSV-7134
S-02115 | PSV3-7135 | 288.99 | Remark: |  | U10 |  | 14"-BFW-70-136-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 1) Capacity and sizing by | P 7001 B vendor | [29 empty] | P | 7135 |  | PSV-7135
S-02115 | PSV3-7136 | 288.99 | Remark: |  | U10 |  | HOLD-LPS-70-124-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) Capacity and sizing by | FP 7001 B vendor | [29 empty] | P | 7136 |  | PSV-7136
S-02115 | PSV3-7137 | 288.99 | Remark: |  | U10 |  | HOLD-LPS-70-123-D24-P |  |  | 9.5 | 7.5 | bar g |  | 191 | 340 | °C | 1) Capacity and sizing by | FP 7001 B vendor | PSV-7137 is spare | [28 empty] | P | 7137 |  | PSV-7137
S-02115 | PSV3-7142 | 288.99 | Remark: |  | U11 |  | BFW-70-165-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | [28 empty] | P | 7142 |  | PSV-7142
S-02115 | PSV3-7143 | 288.99 | Remark: |  | U11 |  | BFW-70-167-F24-H |  |  | 80 | 50 | bar g |  | 121 | 160 | °C | Capacity to be checked against | actual selected Cv of control | valve and bypass valve | PSV-7143 is spare | [27 empty] | P | 7143 |  | PSV-7143
S-02115 | PSV3-7165 | 288.99 | Remark: |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7051 A vendor | [29 empty] | P | 7165 |  | PSV-7165
S-02115 | PSV3-7168 | 288.99 | Remark: |  | U12 |  | 1 1/2"-PH-70-101-H40-N |  |  | 114 | 103 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7051 B vendor | [29 empty] | P | 7168 |  | PSV-7168
S-02115 | PSV3-7171 | 288.99 | Remark: |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7052 A vendor | [29 empty] | P | 7171 |  | PSV-7171
S-02115 | PSV3-7174 | 288.99 | Remark: |  | U12 |  | 1 1/2"-PH-70-102-F40-H |  |  | 47 | 35 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7052 B vendor | [29 empty] | P | 7174 |  | PSV-7174
S-02115 | PSV3-7195 | 288.99 | Remark: |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7060 A vendor | [29 empty] | P | 7195 |  | PSV-7195
S-02115 | PSV3-7198 | 288.99 | Remark: |  | U13 |  | 1 1/2"-AM-70-101-B40-H |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7060 B vendor | [29 empty] | P | 7198 |  | PSV-7198
S-02115 | PSV3-7215 | 288.99 | Remark: |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7070 A vendor | [29 empty] | P | 7215 |  | PSV-7215
S-02115 | PSV3-7218 | 288.99 | Remark: |  | U14 |  | 1 1/2"-HZ-70-101-B40-N |  |  | 7 | 2 | bar g |  | 35 | 75 | °C | 1) Capacity and sizing by | P 7070 B vendor | [29 empty] | P | 7218 |  | PSV-7218
S-02115 | PSV3-7254 | 288.99 | Remark: |  | U16 |  | 4"-LPS-70-135-D24-P |  |  | 9.5 | 7.5 | bar g |  | 173 | 340 | °C | PSV-7254 is spare | [30 empty] | P | 7254 |  | PSV-7254
S-02115 | AP-1002 | 298 | Sample Point |  | P01 |  | 14"-NG-10-101-F24-N |  |  | 60 | 52 | bar g |  | 40 | 85 | °C | 4 | [30 empty] | A | 1002 |  | AP-1002
S-02115 | AP-1036 | 298 | Sample Point |  | P04 |  | 16"-PRG-10-101-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 5 | [30 empty] | A | 1036 |  | AP-1036
S-02115 | AP-1039 | 298 | Sample Point |  | P04 |  | R 1002 1 |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 5 | [30 empty] | A | 1039 |  | AP-1039
S-02115 | AP-1040 | 298 | Sample Point |  | P04 |  | 16"-PRG-10-105-F24-H |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 5 | [30 empty] | A | 1040 |  | AP-1040
S-02115 | AP-1044 | 298 | Sample Point |  | P04 |  | R 1002 2 |  |  | 55 | 48.3 | bar g |  | 375 | 410 | °C | 5 | [30 empty] | A | 1044 |  | AP-1044
S-02115 | AP-1046 | 298 | Sample Point |  | P04 |  | 16"-PRG-10-107-F24-H |  |  | 55 | 47.3 | bar g |  | 365 | 410 | °C | 5 | [30 empty] | A | 1046 |  | AP-1046
S-02115 | AP-2031 | 298 | Sample Point |  | P03 |  | 4"-HPS-70-103-F34-H |  |  | 52 | 44 | bar g |  | 345 | 410 | °C | 2 | [30 empty] | A | 2031 |  | AP-2031
S-02115 | AP-2160 | 298 | Sample Point |  | P12 |  | Flue Gas Stack |  |  |  | 0 | bar g |  | 161 |  | °C | 9 | [30 empty] | A | 2160 |  | AP-2160
S-02115 | AP-2222 | 298 | Sample Point |  | P13 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 9 | [30 empty] | A | 2222 |  | AP-2222
S-02115 | AP-2266 | 298 | Sample Point |  | P14 |  | R 2003 |  |  | 46 | 38.4 | bar g |  | 500 | 550 | °C | 7 | [30 empty] | A | 2266 |  | AP-2266
S-02115 | AP-2267 | 298 | Sample Point |  | P14 |  | 30"-RFG-20-101-F34-H |  |  | 46 | 37.7 | bar g |  | 441 | 500 | °C | 5 | [30 empty] | A | 2267 |  | AP-2267
S-02115 | AP-2294 | 298 | Sample Point |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 9 | [30 empty] | A | 2294 |  | AP-2294
S-02115 | AP-2296 | 298 | Sample Point |  | P15 |  | WHS |  |  |  | 0 | bar g |  | 1095 |  | °C | 9 | [30 empty] | A | 2296 |  | AP-2296
S-02115 | AP-2306 | 298 | Sample Point |  | P15 |  | Cold Collector |  |  | 34.7 | 32 | bar g |  | 742 | 800 | °C | 7 | [30 empty] | A | 2306 |  | AP-2306
S-02115 | AP-2380 | 298 | Sample Point |  | P18 |  | 18"-HHPS-20-102-G24-H |  |  | 112 | 102 | bar g |  | 313 | 330 | °C | 2 | [30 empty] | A | 2380 |  | AP-2380
S-02115 | AP-2383 | 298 | Sample Point |  | P18 |  | 2"-CBD-20-102-G24-P |  |  | 113 | 103 | bar g |  | 313 | 330 | °C | 2 | [30 empty] | A | 2383 |  | AP-2383
S-02115 | AP-2454 | 298 | Sample Point |  | P20 |  | 10"-DMW-20-101-B50-N |  |  | 14 | 5 | bar g |  | 35 | 65 | °C | 1 | [30 empty] | A | 2454 |  | AP-2454
S-02115 | AP-2480 | 298 | Sample Point |  | P21 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4 | [30 empty] | A | 2480 |  | AP-2480
S-02115 | AP-2539 | 298 | Sample Point |  | U01 |  | 24"-PG-30-104-B24-N |  |  | 7 | 3.6 | bar g |  | 47 | 100 | °C | 4 | [30 empty] | A | 2539 |  | AP-2539
S-02115 | AP-2571 | 298 | Sample Point |  | U02 |  | 10"-N-20-110-B24-N |  |  | 10.5 | 6 | bar g |  | 40 | 75 | °C | 4 | [30 empty] | A | 2571 |  | AP-2571
S-02115 | AP-2602 | 298 | Sample Point |  | U17 |  | 3"-HG-20-102-D24-N |  |  | 28 | 25 | bar g |  | 40 | 85 | °C | 4 | [30 empty] | A | 2602 |  | AP-2602
S-02115 | AP-3005 | 298 | Sample Point |  | P22 |  | 28"-SG-20-109-D40-TR |  |  | 29 | 24 | bar g |  | 48 | 100 | °C | 4 | [30 empty] | A | 3005 |  | AP-3005
S-02115 | AP-3019 | 298 | Sample Point |  | P22 |  | 30"-SG-30-118-G40-N |  |  | 99 | 76.2 | bar g |  | 48 | 100 | °C | 4 | [30 empty] | A | 3019 |  | AP-3019
S-02115 | AP-3022 | 298 | Sample Point |  | P22 |  | 32"-SG-30-103-G40-N |  |  | 99 | 80 | bar g |  | 74 | 120 | °C | 6 | [30 empty] | A | 3022 |  | AP-3022
S-02115 | AP-3049 | 298 | Sample Point |  | P23 |  | 24"-MPS-30-114-F24-H |  |  | 45 | 33.7 | bar g |  | 242 | 300 | °C | 2 | [30 empty] | A | 3049 |  | AP-3049
S-02115 | AP-3054 | 298 | Sample Point |  | P23 |  | 2"-CBD-30-101-F24-P |  |  | 47 | 35 | bar g |  | 242 | 265 | °C | 2 | [30 empty] | A | 3054 |  | AP-3054
S-02115 | AP-3074 | 298 | Sample Point |  | P24 |  | 24"-SG-30-111-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 7 | [30 empty] | A | 3074 |  | AP-3074
S-02115 | AP-3078 | 298 | Sample Point |  | P24 |  | 24"-SG-30-108-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 7 | [30 empty] | A | 3078 |  | AP-3078
S-02115 | AP-3082 | 298 | Sample Point |  | P24 |  | 24"-SG-30-120-H40-H |  |  | 99 | 77.8 | bar g |  | 246 | 290 | °C | 7 | [30 empty] | A | 3082 |  | AP-3082
S-02115 | AP-3114 | 298 | Sample Point |  | P25 |  | 24"-SG-30-135-H40-H |  |  | 99 | 79.5 | bar g |  | 210 | 260 | °C | 7 | [30 empty] | A | 3114 |  | AP-3114
S-02115 | AP-3195 | 298 | Sample Point |  | P28 |  | 8"-PG-30-102-B40-N |  |  | 7 | 4 | bar g |  | 48 | 100 | °C | 4 | [30 empty] | A | 3195 |  | AP-3195
S-02115 | AP-3197 | 298 | Sample Point |  | P28 |  | 10"-PMC-30-111-B40-N |  |  | 8 | 4 | bar g |  | 48 | 100 | °C | 1 | [30 empty] | A | 3197 |  | AP-3197
S-02115 | AP-5010 | 298 | Sample Point |  | P29 |  | 16"-PMC-50-101-B40-N |  |  | 4.5 | 1 | bar g |  | 47 | 100 | °C | 1 | [30 empty] | A | 5010 |  | AP-5010
S-02115 | AP-5019 | 298 | Sample Point |  | P29 |  | 10"-PMC-50-103-B40-N |  |  | 13 | 5 | bar g |  | 47 | 100 | °C | 1 | [30 empty] | A | 5019 |  | AP-5019
S-02115 | AP-5021 | 298 | Sample Point |  | P29 |  | 24"-VG-50-101-B40-N |  |  | 3.5 | 0 | bar g |  | 59 | 100 | °C | 3 | [30 empty] | A | 5021 |  | AP-5021
S-02115 | AP-5044 | 298 | Sample Point |  | P30 |  | 16"-PMC-50-130-B24-H |  |  | 10 | 1 | bar g |  | 88 | 160 | °C | 2 | [30 empty] | A | 5044 |  | AP-5044
S-02115 | AP-5052 | 298 | Sample Point |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 2 | [30 empty] | A | 5052 |  | AP-5052
S-02115 | AP-5053 | 298 | Sample Point |  | P30 |  | T 5001 Top |  |  | 3.5 | 0.7 | bar g |  | 78 | 150 | °C | 2 | [30 empty] | A | 5053 |  | AP-5053
S-02115 | AP-5055 | 298 | Sample Point |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 2 | [30 empty] | A | 5055 |  | AP-5055
S-02115 | AP-5056 | 298 | Sample Point |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 2 | [30 empty] | A | 5056 |  | AP-5056
S-02115 | AP-5057 | 298 | Sample Point |  | P30 |  | T 5001 Middle |  |  | 3.5 | 0.7 | bar g |  | 84-86 | 150 | °C | 2 | [30 empty] | A | 5057 |  | AP-5057
S-02115 | AP-5098 | 298 | Sample Point |  | P32 |  | 10"-PMC-50-121-B24 |  |  | 13 | 0.6 | bar g |  | 65 | 150 | °C | 2 | [30 empty] | A | 5098 |  | AP-5098
S-02115 | AP-5112 | 298 | Sample Point |  | P32 |  | 6"-PG-50-101-B24-N |  |  | 3.5 | 0.6 | bar g |  | 48 | 75 | °C | 4 | [30 empty] | A | 5112 |  | AP-5112
S-02115 | AP-5164 | 298 | Sample Point |  | P34 |  | 10"-PMC-50-150-D24-H |  |  | 16 | 0.7 | bar g |  | 86 | 160 | °C | 2 | [30 empty] | A | 5164 |  | AP-5164
S-02115 | AP-5167 | 298 | Sample Point |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 2 | [30 empty] | A | 5167 |  | AP-5167
S-02115 | AP-5171 | 298 | Sample Point |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 2 | [30 empty] | A | 5171 |  | AP-5171
S-02115 | AP-5173 | 298 | Sample Point |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 2 | [30 empty] | A | 5173 |  | AP-5173
S-02115 | AP-5174 | 298 | Sample Point |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 2 | [30 empty] | A | 5174 |  | AP-5174
S-02115 | AP-5175 | 298 | Sample Point |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 2 | [30 empty] | A | 5175 |  | AP-5175
S-02115 | AP-5180 | 298 | Sample Point |  | P34 |  | T 5002 |  |  | 3.5 | 0.1-0.7 | bar g |  | 67-88 | 150 | °C | 2 | [30 empty] | A | 5180 |  | AP-5180
S-02115 | AP-5208 | 298 | Sample Point |  | P36 |  | 2"-VA-50-101-B24-P |  |  | 3.5 | 0 | bar g |  | 65 | 150 | °C | 6 | [30 empty] | A | 5208 |  | AP-5208
S-02115 | AP-5218 | 298 | Sample Point |  | P36 |  | 12"-PMP-50-104-B24-H |  |  | 13 | 4 | bar g |  | 65 | 150 | °C | 2 | [30 empty] | A | 5218 |  | AP-5218
S-02115 | AP-5261 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5261 |  | AP-5261
S-02115 | AP-5262 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5262 |  | AP-5262
S-02115 | AP-5264 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5264 |  | AP-5264
S-02115 | AP-5265 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5265 |  | AP-5265
S-02115 | AP-5266 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5266 |  | AP-5266
S-02115 | AP-5267 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5267 |  | AP-5267
S-02115 | AP-5268 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5268 |  | AP-5268
S-02115 | AP-5269 | 298 | Sample Point |  | P38 |  | T 5003 |  |  | 6 | 2.7-3.6 | bar g |  | 102-149 | 165 | °C | 2 | [30 empty] | A | 5269 |  | AP-5269
S-02115 | AP-5274 | 298 | Sample Point |  | P38 |  | 10"-PMW-50-120-D24-H |  |  | 15 | 3.6 | bar g |  | 149 | 175 | °C | 2 | [30 empty] | A | 5274 |  | AP-5274
S-02115 | AP-5326 | 298 | Sample Point |  | P40 |  | 24"-PMP-50-130-B24-H |  |  | 7 | 2.6 | bar g |  | 101 | 165 | °C | 2 | [30 empty] | A | 5326 |  | AP-5326
S-02115 | AP-5382 | 298 | Sample Point |  | P42 |  | 10"-PMP-50-143-D24-N |  |  | 19 | 3 | bar g |  | 48 | 75 | °C | 1 | [30 empty] | A | 5382 |  | AP-5382
S-02115 | AP-5431 | 298 | Sample Point |  | P44 |  | 8"-PMP-50-153-B24-N |  |  | 14 | 5 | bar g |  | 48 | 75 | °C | 1 | [30 empty] | A | 5431 |  | AP-5431
S-02115 | AP-5452 | 298 | Sample Point |  | P45 |  | 2"-LOS-50-120-B24-N |  |  | 4.5 | 0 | bar g |  | 48 | 75 | °C | 1 | [30 empty] | A | 5452 |  | AP-5452
S-02115 | AP-6059 | 298 | Sample Point |  | P07 |  | 16"-PRC-60-110-G40-H |  |  | 56 | 43 | bar g |  | 225 | 290 | °C | 2 | [30 empty] | A | 6059 |  | AP-6059
S-02115 | AP-7001 | 298 | Sample Point |  | U18 |  | 12"-DMW-70-107-B50-N |  |  | 4.5 | 0 | bar g |  | 35 | 65 | °C | 1 | [30 empty] | A | 7001 |  | AP-7001
S-02115 | AP-7002 | 298 | Sample Point |  | U18 |  | 12"-DMW-70-113-B50-N |  |  | 4.5 | 0 | bar g |  | 35 | 65 | °C | 1 | [30 empty] | A | 7002 |  | AP-7002
S-02115 | AP-7100 | 298 | Sample Point |  | U09 |  | 18"-BFW-70-129-B24-H |  |  | 4.5 | 1 | bar g |  | 120 | 160 | °C | 2 | [30 empty] | A | 7100 |  | AP-7100
S-02115 | AP-7101 | 298 | Sample Point |  | U22 |  | 2"-PRC-70-139-B40-N |  |  | 7 | 1 | bar g |  | 65 | 100 | °C | 2 | [30 empty] | A | 7101 |  | AP-7101
S-02115 | AP-7126 | 298 | Sample Point |  | U10 |  | 12"-BFW-70-140-H24-H |  |  | 170 | 120 | bar g |  | 122 | 160 | °C | 2 | [30 empty] | A | 7126 |  | AP-7126

## Remarks_d
Job_No | Tag No. | Rem. No. | Remark | Loop No.
S-02115 | ASY-1001 | 10 | Result to be used for Carbon Number calculation | AI-1001
S-02115 | AY-1001 | 10 | Result to be used for Carbon Number calculation | AI-1001
S-02115 | AT-2223 | 10 | Note 1: Zirconium oxide/Dual hotwire catalytic detectors | AI-2223
S-02115 | AT-2223 | 20 | Close-coupled aspirated technique | AI-2223
S-02115 | AT-2379 | 10 | With cationic exchanger | AI-2379
S-02115 | AT-3001 | 10 | Automatic manifold for automatic switching between sample | AI-3001
S-02115 | AT-3001 | 20 | points. Stream 1 & 2 are normally continously measured in | AI-3001
S-02115 | AT-3001 | 30 | sequence | AI-3001
S-02115 | AT-3001 | 40 |  | AI-3001
S-02115 | AT-3001 | 50 | Note 2: 1/Synthesis gas to C 3001 & 2/Makeup- recycle gas to | AI-3001
S-02115 | AT-3001 | 60 | R 3001 1 | AI-3001
S-02115 | AT-3001 | 70 |  | AI-3001
S-02115 | AT-3001 | 80 | Design conditions for 1 given above | AI-3001
S-02115 | AT-3001 | 90 | Design conditions for 2 op/design pressure/ temperature: | AI-3001
S-02115 | AT-3001 | 100 | 76.2/99 bar g; 48/100°C | AI-3001
S-02115 | AT-3002 | 10 | Automatic manifold for automatic switching between sample | AI-3002
S-02115 | AT-3002 | 20 | points. Stream 1 & 2 are normally continously measured in | AI-3002
S-02115 | AT-3002 | 30 | sequence | AI-3002
S-02115 | AT-3002 | 40 |  | AI-3002
S-02115 | AT-3002 | 50 | Note 2: 1/Synthesis gas to C 3001 & 2/Makeup- recycle gas to | AI-3002
S-02115 | AT-3002 | 60 | R 3001 1 | AI-3002
S-02115 | AT-3002 | 70 |  | AI-3002
S-02115 | AT-3002 | 80 | Design conditions for 1 given above | AI-3002
S-02115 | AT-3002 | 90 | Design conditions for 2 op/design pressure/ temperature: | AI-3002
S-02115 | AT-3002 | 100 | 76.2/99 bar g; 48/100°C | AI-3002
S-02115 | AT-3003 | 10 | Automatic manifold for automatic switching between sample | AI-3003
S-02115 | AT-3003 | 20 | points. Stream 1 & 2 are normally continously measured in | AI-3003
S-02115 | AT-3003 | 30 | sequence | AI-3003
S-02115 | AT-3003 | 40 |  | AI-3003
S-02115 | AT-3003 | 50 | Note 2: 1/Synthesis gas to C 3001 & 2/Makeup- recycle gas to | AI-3003
S-02115 | AT-3003 | 60 | R 3001 1 | AI-3003
S-02115 | AT-3003 | 70 |  | AI-3003
S-02115 | AT-3003 | 80 | Design conditions for 1 given above | AI-3003
S-02115 | AT-3003 | 90 | Design conditions for 2 op/design pressure/ temperature: | AI-3003
S-02115 | AT-3003 | 100 | 76.2/99 bar g; 48/100°C | AI-3003
S-02115 | FIC-2417 | 10 | Signal from LY-2372/3 | FIC-2417
S-02115 | FT/1-2531 | 10 | Located in 10" pipe | FIC-2531
S-02115 | FIC-2536 | 10 | Signal from QIC-2535 | FIC-2536
S-02115 | FIC-3041 | 10 | Signal from LY-3042/3 | FIC-3041
S-02115 | FI-3167 | 10 | Signal from HIC-3167 | FI-3167
S-02115 | FIC-3169 | 10 | Signal from PIC-3166 A | FIC-3169
S-02115 | FO-3191 | 10 | To be calculated as a thick restriction orifice (t=6d) with | FO-3191
S-02115 | FO-3191 | 20 | sharp edge according to "Flow Measurement Handbook", by | FO-3191
S-02115 | FO-3191 | 30 | Richard Miller. | FO-3191
S-02115 | FO-3191 | 40 |  | FO-3191
S-02115 | FO-3191 | 50 | Release of dissolved gas before orifice: | FO-3191
S-02115 | FO-3191 | 60 | 1246 kg/h, MW 17.46, density 21.2 kg/m3 | FO-3191
S-02115 | FO-3191 | 70 | Liquid flow: | FO-3191
S-02115 | FO-3191 | 80 | 245458 kg/h, density 757 kg/m3 | FO-3191
S-02115 | FO-3191 | 90 |  | FO-3191
S-02115 | FO-3191 | 100 | The average density of the mixture to be used for the | FO-3191
S-02115 | FO-3191 | 110 | calculation of the restriction orifice ie. 644 kg/m3. | FO-3191
S-02115 | FO-3191 | 120 |  | FO-3191
S-02115 | FO-3191 | 130 | The orifice calculated above also restricts the flow of gas | FO-3191
S-02115 | FO-3191 | 140 | in case of gas breakthrough, see PSV-3196 and PSV-3206. | FO-3191
S-02115 | FY-5301 | 10 | Steam flow corresponding to MeOH production | FIC-5301
S-02115 | FV-5501 | 10 |  | FIC-5501
S-02115 | FV4-5501 | 10 |  | FV-5501
S-02115 | FV-5501 | 20 | Alternative option | FIC-5501
S-02115 | FV4-5501 | 20 | Alternative option | FV-5501
S-02115 | FIC-6031 | 10 | Signal from LY-6051 | FIC-6031
S-02115 | FI-6057 | 10 | Signal to be averaged over time due to pulsations in flow. | FI-6057
S-02115 | FHIC-7001 | 10 | Signal to PY-7002 3 | FI-7001
S-02115 | FI-7101 | 10 | Signal to be averaged over time due to pulsations in flow. | FI-7101
S-02115 | HV4-2031 | 10 |  | HV-2031
S-02115 | HV4-2031 | 20 | Valve and silencer to be supplied together | HV-2031
S-02115 | HSIC-2063 | 10 | Restricted input | HSIC-2063
S-02115 | H_O-2471 | 10 |  | HS-2471
S-02115 | H_O-2471 | 20 | Number of motors by AE 2026 vendor | HS-2471
S-02115 | H_O-2472 | 10 |  | HIC-2472
S-02115 | H_O-2472 | 20 | Number of motors and type of output by AE 2026 vendor | HIC-2472
S-02115 | H_O-3142 | 10 |  | HIC-3142
S-02115 | H_O-3142 | 20 | Number of motors and type of output by AE 3002 1 vendor | HIC-3142
S-02115 | H_O-3145 | 10 |  | HIC-3145
S-02115 | H_O-3145 | 20 | Number of motors and type of output by AE 3002 2 vendor | HIC-3145
S-02115 | H_O-3148 | 10 |  | HIC-3148
S-02115 | H_O-3148 | 20 | Number of motors and type of output by AE 3002 3 vendor | HIC-3148
S-02115 | H_O-5092 | 10 |  | HS-5092
S-02115 | H_O-5092 | 20 | Number of motors by AE 5004 vendor | HS-5092
S-02115 | H_O-5093 | 10 |  | HIC-5093
S-02115 | H_O-5093 | 20 | Number of motors and type of output by AE 5004 vendor | HIC-5093
S-02115 | H_O-5201 | 10 |  | HS-5201
S-02115 | H_O-5201 | 20 | Number of motors by AE 5005 vendor | HS-5201
S-02115 | H_O-5202 | 10 |  | HIC-5202
S-02115 | H_O-5202 | 20 | Number of motors and type of output by AE 5005 vendor | HIC-5202
S-02115 | H_O-5361 | 10 |  | HS-5361
S-02115 | H_O-5361 | 20 | Optional U23B | HS-5361
S-02115 | H_O-5365 | 10 |  | HS-5365
S-02115 | H_O-5365 | 20 | Optional U23B | HS-5365
S-02115 | H_O-5369 | 10 |  | HIC-5369
S-02115 | H_O-5369 | 20 | Number of motors and type of output by AE 5006 vendor | HIC-5369
S-02115 | H_0-5403 | 10 | C.t. stroke control of P 5012 | HIC-5403
S-02115 | H_0-5403 | 20 | Type of signal to be confirmed | HIC-5403
S-02115 | H_O-5454 | 10 | C.t. stroke control of P 5009 A | HIC-5454
S-02115 | H_O-5454 | 20 | Type of signal to be confirmed | HIC-5454
S-02115 | H_O-5458 | 10 | C.t. stroke control of P 5009 B | HIC-5458
S-02115 | H_O-5458 | 20 | Type of signal to be confirmed | HIC-5458
S-02115 | H_O-7102 | 10 | C.t. stroke control of P 7004 A | HIC-7102
S-02115 | H_O-7102 | 20 | Type of signal to be confirmed | HIC-7102
S-02115 | H_O-7104 | 10 | C.t. stroke control of P 7004 B | HIC-7104
S-02115 | H_O-7104 | 20 | Type of signal to be confirmed | HIC-7104
S-02115 | HIC-7131 | 10 | C.t. PDIC-2417 | HIC-7131
S-02115 | H_O-7131 | 10 | Type of signal to be confirmed | HIC-7131
S-02115 | HIC-7136 | 10 | C.t. PDIC-2417 | HIC-7136
S-02115 | H_O-7136 | 10 | Type of signal to be confirmed | HIC-7136
S-02115 | LST/A-2372 | 10 | For calibration range see HTAS Document J-751 | LIC-2372
S-02115 | LST/C-2372 | 10 | For calibration range see HTAS Document J-751 | LIC-2372
S-02115 | LST/B-2372 | 10 | For calibration range see HTAS Document J-751 | LIC-2372
S-02115 | LG/LI-2373 | 10 | Additional local indicator for installation at ground | LI-2373
S-02115 | LG/LI-2373 | 20 | level is required. | LI-2373
S-02115 | LST/A-3042 | 10 | For calibration range see HTAS Document J-751 | LIC-3042
S-02115 | LST/C-3042 | 10 | For calibration range see HTAS Document J-751 | LIC-3042
S-02115 | LST/B-3042 | 10 | For calibration range see HTAS Document J-751 | LIC-3042
S-02115 | LG/LI-3043 | 10 | Additional local indicator for installation at ground | LI-3043
S-02115 | LG/LI-3043 | 20 | level is required. | LI-3043
S-02115 | LV2-3161/A | 10 | Multistage, single path to avoid blockage | LV-3161/A
S-02115 | LV2-3161/B | 10 | Multistage, single path to avoid blockage | LV-3161/B
S-02115 | LZLL-5501 | 10 |  | LIC-5501
S-02115 | LV7-5501 | 10 |  | LV-5501
S-02115 | LZLL-5501 | 20 | Alternative option | LIC-5501
S-02115 | LV7-5501 | 20 | Alternative option | LV-5501
S-02115 | LG-5502 | 10 |  | LG-5502
S-02115 | LG-5502 | 20 | Alternative option | LG-5502
S-02115 | LT-7060 | 5 | Range to correspond to liquid height | LI-7060
S-02115 | LT-7060 | 10 | Liquid Density: 994 kg/m3 | LI-7060
S-02115 | LT-7061 | 5 | Range to correspond to liquid height | LI-7061
S-02115 | LT-7061 | 10 | Liquid Density: 994 kg/m3 | LI-7061
S-02115 | ML-2471 | 10 |  | ML-2471
S-02115 | ML-2471 | 20 | Number of motors by AE 2026 vendor | ML-2471
S-02115 | ML-5092 | 10 |  | ML-5092
S-02115 | ML-5092 | 20 | Number of motors by AE 5004 vendor | ML-5092
S-02115 | ML-5201 | 10 |  | ML-5201
S-02115 | ML-5201 | 20 | Number of motors by AE 5005 vendor | ML-5201
S-02115 | ML-5361 | 10 |  | ML-5361
S-02115 | ML-5361 | 20 | Optional U23B | ML-5361
S-02115 | ML-5365 | 10 |  | ML-5365
S-02115 | ML-5365 | 20 | Optional U23B | ML-5365
S-02115 | ML-5368 | 10 |  | ML-5368
S-02115 | ML-5368 | 20 | Number of motors by AE 5006 vendor | ML-5368
S-02115 | PZI_I-2073 | 10 | Connected to I-20 | PIC-2073
S-02115 | PSY-2372 | 10 | Signal to LY-2372 2 | PI-2372
S-02115 | PY-2372 | 10 | Signal to LY-2373 2 | PI-2372
S-02115 | PV3-2551 | 10 | Spring setting 3.5-2.5 bar g | PCV-2551
S-02115 | PSAL-2554 | 10 | Purge gas fuel | PIC-2554
S-02115 | PSAL-2556 | 10 | Natural gas fuel | PSAL-2556
S-02115 | PST/C-2556 | 10 | 1) Range to be decided together with burner vendor | PSAL-2556
S-02115 | PST/A-2556 | 10 | 1) Range to be decided together with burner vendor | PSAL-2556
S-02115 | PST/B-2556 | 10 | 1) Range to be decided together with burner vendor | PSAL-2556
S-02115 | PSV3-5006 | 10 | Set pressure to be provided by PSV vendor to ensure that | PSV-5006
S-02115 | PSV3-5006 | 20 | set point + overpressure does not exceed tank MAWP | PSV-5006
S-02115 | PSV3-5006 | 60 | Required capacity to be verified against actual design. | PSV-5006
S-02115 | PSV3-5007 | 10 | Inbreathing set pressure/capacity: By vendor g / 3220 Nm3/h | PSV-5007
S-02115 | PSV3-5007 | 11 | (Product movement:350 Nm3/h; Thermal inbreathing:2870 Nm3/h) | PSV-5007
S-02115 | PSV3-5007 | 20 | Outbreathing set pressure/capacity:By vendor barg/5455 Nm3/h | PSV-5007
S-02115 | PSV3-5007 | 21 | (Product movement:765 Nm3/h; Flash gas vol.:1820 Nm3/h | PSV-5007
S-02115 | PSV3-5007 | 22 | Thermal outbreathing:2870 Nm3/h) | PSV-5007
S-02115 | PSV3-5007 | 30 | Outbreathing set pressure to be at least 20% less than set | PSV-5007
S-02115 | PSV3-5007 | 40 | of PSV-5006. Backpressure to be assumed to be operating | PSV-5007
S-02115 | PSV3-5007 | 50 | dp over T 5004 ( max. 0.010 bar g) | PSV-5007
S-02115 | PSV3-5007 | 60 | In & out-breathing requirements to be verified against | PSV-5007
S-02115 | PSV3-5007 | 70 | actual design. | PSV-5007
S-02115 | PSV3-5007 | 80 | Inbreathing is air, outbreathing is nitrogen/methanol | PSV-5007
S-02115 | PV3-5009 | 10 | External pressure registration SP approx 25-125 mm WG | PCV-5009
S-02115 | PT-5047 | 10 | High accuracy <= 0.075%, low drift | PI-5047
S-02115 | PT-5049 | 10 | High accuracy <= 0.075%, low drift | PI-5049
S-02115 | PT-5051 | 10 | High accuracy <= 0.075%, low drift | PI-5051
S-02115 | PT-5166 | 10 | High accuracy <= 0.075%, low drift | PI-5166
S-02115 | PT-5168 | 10 | High accuracy <= 0.075%, low drift | PI-5168
S-02115 | PT-5170 | 10 | High accuracy <= 0.075%, low drift | PI-5170
S-02115 | PT-5172 | 10 | High accuracy <= 0.075%, low drift | PI-5172
S-02115 | PT-5176 | 10 | High accuracy <= 0.075%, low drift | PI-5176
S-02115 | PT-5252 | 10 | High accuracy <= 0.075%, low drift | PI-5252
S-02115 | PT-5254 | 10 | High accuracy <= 0.075%, low drift | PI-5254
S-02115 | PT-5256 | 10 | High accuracy <= 0.075%, low drift | PI-5256
S-02115 | PT-5258 | 10 | High accuracy <= 0.075%, low drift | PI-5258
S-02115 | PT-5260 | 10 | High accuracy <= 0.075%, low drift | PI-5260
S-02115 | PV3-5395 | 10 | External pressure registration SP approx 25-125 mm WG | PCV-5395
S-02115 | PSV3-5400 | 10 | Set pressure to be provided by PSV vendor to ensure that | PSV-5400
S-02115 | PSV3-5400 | 20 | set point + overpressure does not exceed tank MAWP | PSV-5400
S-02115 | PSV3-5400 | 60 | Required capacity to be verified against design. | PSV-5400
S-02115 | PSV3-5401 | 10 | Inbreathing design press/capacity: -0.006 bar g/1430 Nm3/h | PSV-5401
S-02115 | PSV3-5401 | 20 | (Product movement:310 Nm3/h; Thermal inbreathing:1120 Nm3/h) | PSV-5401
S-02115 | PSV3-5401 | 30 | Outbreathing set pressure/capacity:By vendor barg/4090 Nm3/h | PSV-5401
S-02115 | PSV3-5401 | 40 | (Product movement:2970Nm3/h | PSV-5401
S-02115 | PSV3-5401 | 50 | Outbreathing set pressure to be at least 20% less than set | PSV-5401
S-02115 | PSV3-5401 | 51 | of PSV-5400. Backpressure to be assumed to be operating | PSV-5401
S-02115 | PSV3-5401 | 52 | dp over T 5004 ( max. 0.010 bar g) | PSV-5401
S-02115 | PSV3-5401 | 60 | In & out-breathing requirements to be verified against | PSV-5401
S-02115 | PSV3-5401 | 70 | actual design. | PSV-5401
S-02115 | PV3-5412 | 10 | External pressure registration SP approx 25-125 mm WG | PCV-5412
S-02115 | PSV3-5417 | 10 | Set pressure to be provided by PSV vendor to ensure that | PSV-5417
S-02115 | PSV3-5417 | 20 | set point + overpressure does not exceed tank MAWP | PSV-5417
S-02115 | PSV3-5417 | 60 | Required capacity to be verified against design. | PSV-5417
S-02115 | PSV3-5418 | 10 | Inbreathing design press/capacity: -0.006 bar g/1430 Nm3/h | PSV-5418
S-02115 | PSV3-5418 | 20 | (Product movement:310 Nm3/h; Thermal inbreathing:1120 Nm3/h) | PSV-5418
S-02115 | PSV3-5418 | 30 | Outbreathing set pressure/capacity:By vendor barg/4090 Nm3/h | PSV-5418
S-02115 | PSV3-5418 | 40 | (Product movement:2970Nm3/h | PSV-5418
S-02115 | PSV3-5418 | 50 | Outbreathing set pressure to be at least 20% less than set | PSV-5418
S-02115 | PSV3-5418 | 51 | of PSV-5417. Backpressure to be assumed to be operating | PSV-5418
S-02115 | PSV3-5418 | 52 | dp over T 5004 ( max. 0.010 bar g) | PSV-5418
S-02115 | PSV3-5418 | 60 | In & out-breathing requirements to be verified against | PSV-5418
S-02115 | PSV3-5418 | 70 | actual design. | PSV-5418
S-02115 | PV3-5445 | 10 | External pressure registration SP approx 25-125 mm WG | PCV-5445
S-02115 | PSV3-5450 | 10 | Set pressure to be provided by PSV vendor to ensure that | PSV-5450
S-02115 | PSV3-5450 | 20 | set point + overpressure does not exceed tank MAWP | PSV-5450
S-02115 | PSV3-5450 | 60 | Required capacity to be verified against design. | PSV-5450
S-02115 | PSV3-5451 | 10 | Inbreathing design press/capacity: By vendor g / 19 Nm3/h | PSV-5451
S-02115 | PSV3-5451 | 11 | (Product movement:5 Nm3/h; Thermal inbreathing:14 Nm3/h) | PSV-5451
S-02115 | PSV3-5451 | 20 | Outbreathing set pressure/capacity: By vendor bar g/29 Nm3/h | PSV-5451
S-02115 | PSV3-5451 | 21 | (Product movement:15 Nm3/h; Thermal outbreathing:14 Nm3/h) | PSV-5451
S-02115 | PSV3-5451 | 30 | Outbreathing set pressure to be at least 20% less than set | PSV-5451
S-02115 | PSV3-5451 | 40 | of PSV-5450. Backpressure to be assumed to be operating | PSV-5451
S-02115 | PSV3-5451 | 50 | dp over T 5004 ( max. 0.010 bar g) | PSV-5451
S-02115 | PSV3-5451 | 60 | In & out-breathing requirements to be verified against | PSV-5451
S-02115 | PSV3-5451 | 70 | actual design. | PSV-5451
S-02115 | PG-5501 | 10 |  | PG-5501
S-02115 | PSV2-5501 | 10 |  | PSV-5501
S-02115 | PG-5501 | 20 | Alternative option | PG-5501
S-02115 | PSV2-5501 | 20 | Alternative option | PSV-5501
S-02115 | PG-5502 | 10 |  | PG-5502
S-02115 | PG-5502 | 20 | Alternative option | PG-5502
S-02115 | PG-5503 | 10 |  | PG-5503
S-02115 | PG-5503 | 20 | Alternative option | PG-5503
S-02115 | PG-5504 | 10 |  | PG-5504
S-02115 | PG-5504 | 20 | Alternative option | PG-5504
S-02115 | PSV2-5505 | 10 |  | PSV-5505
S-02115 | PSV2-5505 | 20 | Alternative option | PSV-5505
S-02115 | PSV3-7010 | 10 | Non API 526 valve, outlet flange is class 300 | PSV-7010
S-02115 | PSV3-7010 | 20 | Size and outlet rating to be confirmed by vendor | PSV-7010
S-02115 | PSV3-7011 | 10 | Non API 526 valve, outlet flange is class 300 | PSV-7011
S-02115 | PSV3-7011 | 20 | Size and outlet rating to be confirmed by vendor | PSV-7011
S-02115 | PSV3-7012 | 10 | Non API 526 valve, outlet flange is class 300 | PSV-7012
S-02115 | PSV3-7012 | 20 | Size and outlet rating to be confirmed by vendor | PSV-7012
S-02115 | PSV3-7023 | 10 | Non API 526 valve, outlet flange is class 300 | PSV-7023
S-02115 | PSV3-7023 | 20 | Size and outlet rating to be confirmed by vendor | PSV-7023
S-02115 | PSV3-7024 | 10 | Non API 526 valve, outlet flange is class 300 | PSV-7024
S-02115 | PSV3-7024 | 20 | Size and outlet rating to be confirmed by vendor | PSV-7024
S-02115 | PSV3-7024 | 30 | PSV-7024 is spare | PSV-7024
S-02115 | SC-2119 | 10 | Signal from HIC-2119 | SIC-2119
S-02115 | SC-2167 | 10 | Signal from HIC-2167 | SIC-2167
S-02115 | SC-7131 | 10 | Signal from HIC-7131 | SC-7131
S-02115 | SC-7136 | 10 | Signal from HIC-7136 | SC-7136
S-02115 | SC-7193 | 10 | Signal from AIC-7099 | SC-7193
S-02115 | SC-7196 | 10 | Signal from AIC-7099 | SC-7196
S-02115 | TW-2254 | 10 | Part of R 2003 Prereformer | TI-2254
S-02115 | TW-2254 | 20 | Common well for assembly of the following thermocouples | TI-2254
S-02115 | TW-2254 | 30 | TE-2254, TE-2255, TE-2256, TE-2257, TE-2258, TE-2259 | TI-2254
S-02115 | TW-2255 | 10 | Part of R 2003 Prereformer | TI-2255
S-02115 | TW-2255 | 20 | Common well for assembly of the following thermocouples | TI-2255
S-02115 | TW-2255 | 30 | TE-2254, TE-2255, TE-2256, TE-2257, TE-2258, TE-2259 | TI-2255
S-02115 | TW-2256 | 10 | Part of R 2003 Prereformer | TI-2256
S-02115 | TW-2256 | 20 | Common well for assembly of the following thermocouples | TI-2256
S-02115 | TW-2256 | 30 | TE-2254, TE-2255, TE-2256, TE-2257, TE-2258, TE-2259 | TI-2256
S-02115 | TW-2257 | 10 | Part of R 2003 Prereformer | TI-2257
S-02115 | TW-2257 | 20 | Common well for assembly of the following thermocouples | TI-2257
S-02115 | TW-2257 | 30 | TE-2254, TE-2255, TE-2256, TE-2257, TE-2258, TE-2259 | TI-2257
S-02115 | TW-2258 | 10 | Part of R 2003 Prereformer | TI-2258
S-02115 | TW-2258 | 20 | Common well for assembly of the following thermocouples | TI-2258
S-02115 | TW-2258 | 30 | TE-2254, TE-2255, TE-2256, TE-2257, TE-2258, TE-2259 | TI-2258
S-02115 | TW-2259 | 10 | Part of R 2003 Prereformer | TI-2259
S-02115 | TW-2259 | 20 | Common well for assembly of the following thermocouples | TI-2259
S-02115 | TW-2259 | 30 | TE-2254, TE-2255, TE-2256, TE-2257, TE-2258, TE-2259 | TI-2259
S-02115 | TW-2260 | 10 | Part of R 2003 Prereformer | TI-2260
S-02115 | TW-2260 | 20 | Common well for assembly of the following thermocouples | TI-2260
S-02115 | TW-2260 | 30 | TE-2260, TE-2261, TE-2262, TE-2263, TE-2264, TE-2265 | TI-2260
S-02115 | TW-2261 | 10 | Part of R 2003 Prereformer | TI-2261
S-02115 | TW-2261 | 20 | Common well for assembly of the following thermocouples | TI-2261
S-02115 | TW-2261 | 30 | TE-2260, TE-2261, TE-2262, TE-2263, TE-2264, TE-2265 | TI-2261
S-02115 | TW-2262 | 10 | Part of R 2003 Prereformer | TI-2262
S-02115 | TW-2262 | 20 | Common well for assembly of the following thermocouples | TI-2262
S-02115 | TW-2262 | 30 | TE-2260, TE-2261, TE-2262, TE-2263, TE-2264, TE-2265 | TI-2262
S-02115 | TW-2263 | 10 | Part of R 2003 Prereformer | TI-2263
S-02115 | TW-2263 | 20 | Common well for assembly of the following thermocouples | TI-2263
S-02115 | TW-2263 | 30 | TE-2260, TE-2261, TE-2262, TE-2263, TE-2264, TE-2265 | TI-2263
S-02115 | TW-2264 | 10 | Part of R 2003 Prereformer | TI-2264
S-02115 | TW-2264 | 20 | Common well for assembly of the following thermocouples | TI-2264
S-02115 | TW-2264 | 30 | TE-2260, TE-2261, TE-2262, TE-2263, TE-2264, TE-2265 | TI-2264
S-02115 | TW-2265 | 10 | Part of R 2003 Prereformer | TI-2265
S-02115 | TW-2265 | 20 | Common well for assembly of the following thermocouples | TI-2265
S-02115 | TW-2265 | 30 | TE-2260, TE-2261, TE-2262, TE-2263, TE-2264, TE-2265 | TI-2265
S-02115 | TW/A-2325 | 10 | Thermowell part of R 2004 supply | TI-2325
S-02115 | TW/C-2325 | 10 | Thermowell part of R 2004 supply | TI-2325
S-02115 | TW/B-2325 | 10 | Thermowell part of R 2004 supply | TI-2325
S-02115 | TW-2326 | 10 | Thermowell ½" NPT female connection, part of R 2004 supply | TI-2326
S-02115 | TW-2327 | 10 | Thermowell ½" NPT female connection, part of R 2004 supply | TI-2327
S-02115 | TW-2328 | 10 | Thermowell ½" NPT female connection, part of R 2004 supply | TI-2328
S-02115 | TW-2330 | 10 | Thermowell ½" NPT female connection, part of R 2004 supply | TI-2330
S-02115 | TW-2331 | 10 | Thermowell ½" NPT female connection, part of R 2004 supply | TI-2331
S-02115 | TW-2332 | 10 | Thermowell ½" NPT female connection, part of R 2004 supply | TI-2332
S-02115 | TW/A-2333 | 10 | Thermowell part of R 2004/E 2020 supply | TI-2333
S-02115 | TW/C-2333 | 10 | Thermowell part of R 2004/E 2020 supply | TI-2333
S-02115 | TW/B-2333 | 10 | Thermowell part of R 2004/E 2020 supply | TI-2333
S-02115 | TW/A-2334 | 10 | Thermowell part of R 2004 supply | TI-2334
S-02115 | TW/B-2334 | 10 | Thermowell part of R 2004 supply | TI-2334
S-02115 | TW/C-2334 | 10 | Thermowell part of R 2004 supply | TI-2334
S-02115 | TW/A-2335 | 10 | Thermowell part of E 2020 supply | TIC-2335
S-02115 | TW/C-2335 | 10 | Thermowell part of R 2004/E 2020 supply | TIC-2335
S-02115 | TW/B-2335 | 10 | Thermowell part of R 2004/E 2020 supply | TIC-2335
S-02115 | TW/A-2336 | 10 | Thermowell part of E 2020 supply | TIC-2336
S-02115 | TW/B-2336 | 10 | Thermowell part of R 2004/E 2020 supply | TIC-2336
S-02115 | TW/C-2336 | 10 | Thermowell part of R 2004/E 2020 supply | TIC-2336
S-02115 | TW-3072 | 10 | Part of R 3001 1 Methanol Reactor | TI-3072
S-02115 | TW-3076 | 10 | Part of R 3001 2 Methanol Reactor | TI-3076
S-02115 | TW-3080 | 10 | Part of R 3001 3 Methanol Reactor | TI-3080
S-02115 | TG-5501 | 10 |  | TG-5501
S-02115 | TG-5501 | 20 | Alternative option | TG-5501
S-02115 | TZ-7025 | 10 | to be sized and supplied together with TV-7025/A & /B | TZ-7025
S-02115 | TV4-7071/A | 10 |  | TV-7071/A
S-02115 | TV4-7071/A | 20 | Steam pipe no.: 6"-HPS-70-126-F24-H | TV-7071/A
S-02115 | TV4-7071/A | 30 | Operating / design pressure: 44/52 bar g | TV-7071/A
S-02115 | TV4-7071/A | 40 | Operating / design temperature: 272/310 °C | TV-7071/A
S-02115 | TV4-7071/B | 10 |  | TV-7071/B
S-02115 | TV4-7071/B | 20 | Steam pipe no.: 6"-HPS-70-126-F24-H | TV-7071/B
S-02115 | TV4-7071/B | 30 | Operating / design pressure: 44/52 bar g | TV-7071/B
S-02115 | TV4-7071/B | 40 | Operating / design temperature: 272/310 °C | TV-7071/B
S-02115 | US_O-2547 | 10 | Signal from: Burner leak test | USY-2547
S-02115 | US_O-2548 | 10 | Signal from: Burner leak test | USY-2548
S-02115 | US_O-2549 | 10 | Signal from: Burner leak test | USY-2549
S-02115 | XA-5092 | 10 |  | XA-5092
S-02115 | XA-5092 | 20 | Number of motors by AE 5004 vendor | XA-5092
S-02115 | XA-5201 | 10 |  | XA-5201
S-02115 | XA-5201 | 20 | Number of motors by AE 5005 vendor | XA-5201
S-02115 | XA-5361 | 10 |  | XA-5361
S-02115 | XA-5361 | 20 | Optional U23B | XA-5361
S-02115 | XA-5365 | 10 |  | XA-5365
S-02115 | XA-5365 | 20 | Optional U23B | XA-5365
S-02115 | XA-5368 | 10 |  | XA-5368
S-02115 | XA-5368 | 20 | Number of motors by AE 5006 vendor | XA-5368
S-02115 | YL-2471 | 10 |  | YL-2471
S-02115 | YL-2471 | 20 | Number of motors by AE 2026 vendor | YL-2471
S-02115 | YL-5361 | 10 |  | YL-5361
S-02115 | YL-5361 | 20 | Optional U23B | YL-5361
S-02115 | YL-5365 | 10 |  | YL-5365
S-02115 | YL-5365 | 20 | Optional U23B | YL-5365

## Control Valve Calc._d
Job No. | Tag No. | Fluid Phase | Viscosity | Viscosity Unit | Compressibility | Cp/Cv | Mole Weight | Vapour Pressure | Vapour Pressure Unit | Outlet Valve Diameter | Outlet Valve Diameter Unit | Minimum Flow | Minimum Upstream Pressure | Minimum Downstream Pressure | Minimum Temperature | Minimum Inlet Density | Minimum Flash % | Minimum Cv Valve | Minimum Outlet Velocity | Normal Flow | Normal Upstream Pressure | Normal Downstream Pressure | Normal Temperature | Normal Inlet Density | Normal Flash % | Normal Cv Valve | Normal Outlet Velosity | Maximum Flow | Maximum Upstream Pressure | Maximum Downstream Pressure | Maximum Temperature | Maximum Inlet Density | Maximum Flash % | Maximum Cv Valve | Maximum Outlet Velosity | Special Flow | Special Upstream Pressure | Special Downstream Pressure | Special Temperature | Special Inlet Density | Special Flash % | Special Cv Valve | Special Outlet Velosity | Flow Unit | Upstream Pressure Unit | Downstream Pressure Unit | Inlet Density Unit | Outlet Velosity Unit | Temperature Unit | Fp | Ff | Fl | Flp | Fr | Fd | Xt | Xtp | Calcrem
S-02115 | FV-2007 | G | 0.022 | cP | 0.98 | 1.39 | 32.01 |  |  | 8 | inch | [8 empty] | 65769 | 39 | 37 | 35 |  |  | 347.7145 | 17.6739 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | FV-2009 | G | 0.022 | cP | 0.98 | 1.39 | 32.01 |  |  | 4 | inch | [8 empty] | 19700 | 39 | 37 | 35 |  |  | 104.152 | 21.1756 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: Start-up
S-02115 | FV-2040 | S | 0.022 | cP |  |  | 18.02 |  |  | 3 | inch | [8 empty] | 4588 | 43 | 36 | 345 | 17.2 |  | 16.5334 | 19.3206 | 9176 | 43 | 36 | 345 | 17.2 |  | 33.0669 | 38.6411 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | FV-2061 | G | 0.019 | cP | 0.94 | 1.19 | 17.47 |  |  | 24 | inch | [8 empty] | 423949 | 42.5 | 42.1 | 262 |  |  | 4498.217 | 19.3829 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | FV-2072 | S | 0.022 | cP |  |  | 18.02 |  |  | 8 | inch | [8 empty] | 32826 | 44 | 42.1 | 345 | 17.3 |  | 213.9076 | 16.9692 | 75000 | 44 | 42.1 | 345 | 17.3 |  | 488.7307 | 38.7709 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-2079 | G |  | cP | 1.02 | 1.37 | 11.6 |  |  | 1.5 | inch | [8 empty] | 0 | 50.4 | 41.5 | 48 |  |  | 0 | 0 | [8 empty] | 5063 | 45.4 | 41.5 | 48 |  |  | 11.35 | 36.0638 | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: Emergency shut-down
S-02115 | FV-2091 | G | 0.019 | cP | 0.94 | 1.19 | 17.47 |  |  | 10 | inch | [8 empty] | 127000 | 43.1 | 42.1 | 262 |  |  | 852.7121 | 33.445 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Start-up
S-02115 | FV-2150 | G |  | cP | 1.02 | 1.39 | 11.4 |  |  | 2 | inch | [8 empty] | 5101 | 50.4 | 49.5 | 48 |  |  | 21.7071 | 17.2013 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-2233/1 | L | 0.56 | cP |  |  | 18.02 |  |  | 1.5 | inch | [8 empty] | 0 | 52 | 42.1 | 49 | 991 |  | 0 | 0 | 15000 | 52 | 42.1 | 49 | 991 |  | 5.5472 | 3.6879 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0 | Downstream pressure is gas/steam pressure. The stated Cv is the combination of valve and nozzle FZ-2233.
S-02115 | FV-2233/2 | L | 0.23 | cP |  |  | 18.02 |  |  | 1.5 | inch | [8 empty] | 0 | 50 | 42.1 | 122 | 944 |  | 0 | 0 | 15000 | 50 | 42.1 | 122 | 944 |  | 6.3625 | 3.8715 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure is gas/steam pressure. The stated Cv is the combination of valve and nozzle FZ-2233.
S-02115 | FV-2417 | L | 0.23 | cP |  |  | 18.02 |  |  | 10 | inch | [8 empty] | 393709 | 109 | 104 | 122 | 947 |  | 209.5813 | 2.2791 | 393709 | 122 | 120.7 | 122 | 947 |  | 411.0229 | 2.2791 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas. Max case: PSV's blowing.
S-02115 | FV-2531/1 | G | 0.013 | cP | 0.99 | 1.3 | 16.74 |  |  | 6 | inch | [8 empty] | 8400 | 4 | 2 | 35 |  |  | 111.186 | 50.6291 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: 25% of max. case 100% NG firing
S-02115 | FV-2531/2 | G | 0.013 | cP | 0.99 | 1.3 | 16.74 |  |  | 10 | inch | [8 empty] | 5000 | 4 | 2 | 35 |  |  | 66.1822 | 10.8491 | 25072 | 4 | 2 | 35 |  |  | 331.8639 | 54.4017 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal/max. case: C1 EOR - Lean Gas. Max. case 100% NG firing
S-02115 | FV-2536 | G | 0.016 | cP | 1 | 1.37 | 13.03 |  |  | 16 | inch | [8 empty] | 67806 | 3.6 | 2 | 47 |  |  | 906.0365 | 59.7094 | 87680 | 3.6 | 2 | 47 |  |  | 1171.596 | 77.2103 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal/max.case: C3 EOR - Rich Gas; Max. 75% firing
S-02115 | FV-3041 | L | 0.23 | cP |  |  | 18.02 |  |  | 6 | inch | [8 empty] | 27405 | 50 | 41.8 | 121 | 945 |  | 11.4037 | 0.44161 | 150000 | 50 | 41.8 | 121 | 945 |  | 62.4174 | 2.4171 | 310000 | 50 | 48.7 | 121 | 945 |  | 323.9749 | 4.9954 | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas. Max case: Start-up. Specíal case: PSV's blowing.
S-02115 | FV-3169 | G | 0.016 | cP | 1.03 | 1.37 | 11.4 |  |  | 4 | inch | [8 empty] | 0 | 83.7 | 3.6 | 48 |  |  | 0 | 0 | 62273 | 83.7 | 3.6 | 48 |  |  | 37.8983 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-3171 | G | 0.016 | cP | 1.03 | 1.37 | 11.4 |  |  | 4 | inch | [8 empty] | 62273 | 83.7 | 83.2 | 48 |  |  | 276.8327 | 31.4897 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-5020 | L | 0.57 | cP |  |  | 18.02 |  |  | 1 | inch | [8 empty] | 8197 | 4 | 1 | 48 | 989 |  | 5.5123 | 4.5436 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | FV-5041 | L | 0.45 | cP |  |  | 28.92 |  |  | 8 | inch | [8 empty] | 245964 | 4.8 | 3.8 | 47 | 792 |  | 320.1446 | 2.6602 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-5093 | L | 0.33 | cP |  |  | 32.48 |  |  | 6 | inch | [8 empty] | 111377 | 3.8 | 3.3 | 65 | 752 |  | 210.3967 | 2.2554 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Lean Gas.
S-02115 | FV-5107 | L | 0.33 | cP |  |  | 32.48 |  |  | 1 | inch | [8 empty] | 1000 | 3.8 | 2.5 | 65 | 752 |  | 1.1715 | 0.72899 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Lean Gas.
S-02115 | FV-5161 | L | 0.27 | cP |  |  | 28.84 |  |  | 8 | inch | [8 empty] | 245177 | 2.2 | 1.8 | 88 | 753 |  | 517.4752 | 2.789 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-5203 | L | 0.33 | cP |  |  | 32.04 |  |  | 8 | inch | [8 empty] | 292596 | 3.5 | 2.5 | 65 | 750 |  | 391.3588 | 3.3417 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | FV-5239 | L | 0.29 | cP |  |  | 26.08 |  |  | 6 | inch | [8 empty] | 119214 | 6.5 | 5.5 | 86 | 786 |  | 155.759 | 2.3096 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Lean Gas.
S-02115 | FV-5301 | L | 0.16 | cP |  |  | 18.02 | 7.5 | bar a | 12 | inch | [8 empty] | 196357 | 6.5 | 1 | 168 | 899 | 9.4 | 319.1 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.91 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Lean Gas.
S-02115 | FV-5321 | L | 0.23 | cP |  |  | 32.04 |  |  | 10 | inch | [8 empty] | 358377 | 6 | 5.5 | 101 | 711 |  | 696.2379 | 2.7632 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | FV-5336 | L | 0.4 | cP |  |  | 32.04 |  |  | 4 | inch | [8 empty] | 82374 | 4.7 | 3 | 48 | 766 |  | 83.6159 | 3.6845 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | FV-5337 | L | 0.4 | cP |  |  | 32.04 |  |  | 6 | inch | [8 empty] | 126013 | 3.3 | 3 | 48 | 766 |  | 304.4932 | 2.5051 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-5367 | L | 0.19 | cP |  |  | 18.02 |  |  | 2 | inch | [8 empty] | 27742 | 49 | 46 | 150 | 920 |  | 19.3428 | 4.1327 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C2 SOR - Lean Gas
S-02115 | FV-5383 | L | 0.72 | cP |  |  | 18.02 |  |  | 1 | inch | [8 empty] | 0 | 4 | 3 | 35 | 994 |  | 0 | 0 | 7000 | 4 | 3 | 35 | 994 |  | 8.3844 | 3.8606 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 0.97 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | FV-5441 | L | 0.22 | cP |  |  | 18.02 |  |  | 1 | inch | [8 empty] | 2489 | 3.4 | 2.5 | 115 | 746 |  | 3.5186 | 1.8291 | 4525 | 3.4 | 2.5 | 115 | 746 |  | 6.3968 | 3.3252 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | FV-5501 | L | 0.19 | cP |  |  | 18.02 |  |  | 3 | inch | [8 empty] | 27742 | 3.6 | 2.6 | 149 | 918 |  | 33.5393 | 1.8407 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C2 SOR - Lean Gas
S-02115 | FV-6031 | L | 0.23 | cP |  |  | 18.02 |  |  | 3 | inch | [8 empty] | 0 | 50 | 44 | 122 | 944 |  | 0 | 0 | 60000 | 50 | 44 | 122 | 944 |  | 29.203 | 3.8715 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | FZ-6058 | L | 0.46 | cP | [15 empty] | 2465 | 53 | 47.3 | 50 | 813 |  |  |  | 5500 | 53 | 47.3 | 50 | 813 | [11 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | [8 empty] | Sizing by vendor
S-02115 | FV-6070 | G | 0.021 | cP | 1.01 | 1.19 | 16.66 |  |  | 14 | inch | [8 empty] | 171646 | 47.3 | 44.8 | 365 |  |  | 782.43 | 25.8804 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | FV-6081 | L | 0.36 | cP |  |  | 18.02 |  |  | 1 | inch | [8 empty] | 6179 | 44 | 0 | 78 | 975 | 0 | 1.0928 | 3.4742 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Norm case: C1 EOR.
S-02115 | FV-6082 | L | 0.43 | cP | [5 empty] | 1 | inch | [8 empty] | 6200 | 2.5 | 1.5 | 65 | 980 |  | 7.2546 | 3.4682 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 |  | 0.9 |  | 1 | 1 | 0.72
S-02115 | FV-6086 | L | 0.12 | cP |  |  | 18.02 | 25.5 | bar a |  | inch | [8 empty] | 0 | 43 | 0 | 225 | 834 | [11 empty] | 54000 | 28 | 0 | 225 | 834 | 23.3 | 29.7 |  | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.86 | 0.9 |  | 1 | 1 | 0.72
S-02115 | FV-7091 | L | 0.39 | cP | [5 empty] | 8 | inch | [8 empty] | 218326 | 3 | 2 | 69 | 977 |  | 255.8559 | 1.9141 | 372000 | 3 | 2 | 69 | 977 |  | 435.9463 | 3.2614 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0.72
S-02115 | FV-7141 | L | 0.23 | cP |  |  | 18.02 |  |  | 6 | inch | [8 empty] | 0 | 120 | 50 | 122 | 947 |  | 0 | 0 | 279000 | 120 | 50 | 122 | 947 |  | 39.6933 | 4.4863 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-1003 | G | 0.013 | cP | 0.93 | 1.28 | 16.74 |  |  | 14 | inch | [8 empty] | 178361 | 52 | 52 | 40 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | [8 empty] | Normal case: C1 EOR - Lean Gas
S-02115 | HV-2003 | G | 0.022 | cP | 0.98 | 1.39 | 32.01 |  |  | 10 | inch | [8 empty] | 65769 | 40 | 40 | 35 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | [8 empty] | Normal case: C1 EOR - Lean Gas
S-02115 | HV-2031 | S | 0.022 | cP |  |  | 18.02 |  |  |  | inch | [8 empty] | 0 | 44 | 0 | 345 | 17.3 |  | 0 |  | 4000 | 44 |  | 345 | 17.3 |  | 9.2813 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure by EPC & silencer vendor
S-02115 | HV-2076 | S | 0.022 | cP |  |  | 18.02 |  |  | 8 | inch | [8 empty] | 50000 | 44 | 42.3 | 345 | 17.3 |  | 343.7324 | 25.7279 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: Start-up
S-02115 | HV-2097 | S | 0.022 | cP |  |  | 18.02 |  |  | 2 | inch | [8 empty] | 3000 | 42.1 | 5 | 343 | 16.2 |  | 7.3502 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure by EPC & silencer vendor
S-02115 | HV-2098 | S | 0.022 | cP |  |  | 18.02 |  |  | 12 | inch | [8 empty] | 32826 | 42.1 | 42.1 | 343 | 16.2 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | [8 empty] | Normal case: C3 EOR - Rich Gas
S-02115 | HV-2334 | L | 0.089 | cP |  |  | 18.02 | 104 | bar a | 1 | inch | [8 empty] | 0 | 103 |  | 313 | 684 |  |  |  | 50000 | 103 | 2 | 313 | 684 | 39.8 | 15.9 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.77 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-2335 | L | 0.089 | cP |  |  | 18.02 | 104 | bar a | 1 | inch | [8 empty] | 0 | 103 |  | 313 | 684 |  |  |  | 50000 | 103 | 2 | 313 | 684 | 39.8 | 15.9 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.77 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-2371 | L | 0.1 | cP |  |  | 18.02 | 60.4 | bar a | 4 | inch | [8 empty] | 79000 | 103 | 2 | 276 | 764 | 30.4 | 15.7 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.81 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: Start-up
S-02115 | HV-2385 | L | 0.089 | cP |  |  | 18.02 | 104 | bar a | 1 | inch | [8 empty] | 3837 | 103 | 2 | 313 | 684 | 39.8 | 1.25 |  | 7700 | 103 | 2 | 313 | 684 | 39.8 | 2.5 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.77 | 0.9 |  | 1 | 1 | 0.72 | 0.72 | Normal case: C3 EOR - Rich Gas
S-02115 | HV-2545 | G |  |  | 1 | 1.4 | 28.01 |  |  | 2 | inch | [8 empty] | 1000 | 6 | 2 | 40 |  |  | 11.2888 | 98.0011 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3010 | G | 0.016 | cP | 1.01 | 1.39 | 11.44 |  |  | 2 | inch | [8 empty] | 0 | 10 | 6 | 48 |  |  | 0 | 0 | 2200 | 10 | 6 | 48 |  |  | 11.4207 | 53.4351 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3011 | G |  |  | 1.01 | 1.39 | 11.14 |  |  |  | inch | [8 empty] | 0 | 24 | 0 | 48 |  |  | 0 |  | 8050 | 24 | 0 | 48 |  |  | 16.1245 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3013 | G | 0.03 | cP | 1.01 | 1.4 | 2.02 |  |  | 1 | inch | [8 empty] | 0 | 25 | 6 | 40 |  |  | 0 | 0 | 1600 | 25 | 6 | 40 |  |  | 1.2912 | 151.5753 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3016 | G | 0.019 | cP | 1 | 1.41 | 28.89 |  |  | 3 | inch | [8 empty] | 0 | 7.5 | 6 | 35 |  |  | 0 | 0 | 8000 | 7.5 | 6 | 35 |  |  | 107.9888 | 82.864 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0
S-02115 | HV-3054 | L | 0.11 | cP |  |  | 18.02 | 34.7 | bar a | 1 | inch | [8 empty] | 2815 | 33.7 | 8 | 242 | 811 | 15 | 1.76 |  | 3600 | 33.7 | 8 | 242 | 811 | 15 | 2.25 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.85 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | HV-3087 | L | 0.11 | cP |  |  | 18.02 | 34.7 | bar a | 1.5 | inch | [8 empty] | 0 | 33.7 | 2 | 242 | 811 |  |  |  | 50000 | 33.7 | 2 | 242 | 811 | 22.5 | 33.2 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.85 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3090 | L | 0.11 | cP |  |  | 18.02 | 34.7 | bar a | 1.5 | inch | [8 empty] | 0 | 33.7 | 2 | 242 | 811 |  |  |  | 50000 | 33.7 | 2 | 242 | 811 | 22.5 | 33.2 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.85 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3093 | L | 0.11 | cP |  |  | 18.02 | 34.7 | bar a | 1.5 | inch | [8 empty] | 0 | 33.7 | 2 | 242 | 811 |  |  |  | 50000 | 33.7 | 2 | 242 | 811 | 22.5 | 33.2 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.85 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-3166 | G | 0.016 | cP | 1.03 | 1.37 | 11.4 |  |  |  | inch | [8 empty] | 0 | 83.7 | 1.5 | 48 |  |  | 0 |  | 100000 | 83.7 | 1.5 | 48 |  |  | 60.8584 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | HV-5338 | G | [7 empty] | 3 | inch | [8 empty] | 0 | 2.6 | 1.5 | 101 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Manual vent for removal of inerts as required
S-02115 | HV-6069 | G | 0.019 | cP | 1 | 1.21 | 16.66 |  |  | 16 | inch | [8 empty] | 171646 | 43.3 | 43 | 265 |  |  | 2108.77 | 17.3931 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas - full bypass
S-02115 | LV-2016 | L | 0.11 | cP |  |  | 18.02 | 44.5 | bar a | 3 | inch | [8 empty] | 10050 | 43.5 | 2 | 257 | 789 | 25.7 | 5.36 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.83 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | LV-2372 | L | 0.23 | cP |  |  | 18.02 |  |  | 4 | inch | [8 empty] | 0 | 109 | 104 | 122 | 947 |  | 0 | 0 | 100000 | 109 | 104 | 122 | 947 |  | 53.2326 | 3.618 | 50000 | 109 | 10 | 122 | 947 |  | 5.9816 | 1.809 | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0.72 | Normal case: Start-up. The valve will experience high dp during start-up.
S-02115 | LV-2403 | L | 0.17 | cP |  |  | 18.02 |  |  | 2 | inch | [8 empty] | 24317 | 55 | 45 | 165 | 905 |  | 9.3632 | 3.6825 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | LV-2419 | L | 0.17 | cP |  |  | 18.02 |  |  | 4 | inch | [8 empty] | 27086 | 25.3 | 25.2 | 159 | 909 |  | 104.0639 | 1.0209 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | LV-2441 | L | 0.2 | cP |  |  | 18.02 |  |  | 4 | inch | [8 empty] | 90055 | 53 | 45 | 138 | 929 |  | 38.2642 | 3.3213 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | LV-2474 | L | 0.56 | cP |  |  | 18.02 |  |  | 3 | inch | [8 empty] | 68415 | 53 | 46 | 49 | 990 |  | 30.1039 | 4.2093 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | LV-3161/A | L | 0.39 | cP |  |  | 29.6 |  | bar a | 8 | inch | [8 empty] | 246704 | 83.7 | 32 | 48 | 757 | *) | 48.6 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas. *) 1624 Nm3/h of dissolved gas with MW 17.16 is released.
S-02115 | LV-3161/B | L | 0.39 | cP |  |  | 29.6 |  | bar a | 8 | inch | [8 empty] | 246704 | 83.7 | 32 | 48 | 757 | *) | 48.6 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas. *) 1624 Nm3/h of dissolved gas with MW 17.16 is released.
S-02115 | LV-3192 | L | 0.43 | cP |  |  | 29.6 |  | bar a | 8 | inch | [8 empty] | 240106 | 4 | 2 | 48 | 781 | *) | 239 | [17 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas. *) 829 Nm3/h of dissolved gas with MW 39.28 is released.
S-02115 | LV-5070 | L | 0.16 | cP |  |  | 18.02 | 3.4 | bar a | 3 | inch | [8 empty] | 34117 | 3.7 | 2.7 | 110 | 951 |  | 40.5245 | 2.1852 | [8 empty] | 34117 | 5.7 | 2.7 | 138 | 928 | 0.9 | 31.2 |  | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.93 | 0.9 |  | 1 | 1 | 0.72
S-02115 | LV-5501 | L | 0.62 | cP |  |  | 18.02 |  |  | 2 | inch | [8 empty] | 27742 | 50 | 46 | 43 | 991 |  | 16.1402 | 3.8366 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | LV-6021/A | L | 0.11 | cP |  |  | 18.02 |  |  | 6 | inch | [8 empty] | 260087 | 43.8 | 41.8 | 241 | 814 |  | 236.1178 | 4.8656 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | LV-6021/B | L | 0.11 | cP |  |  | 18.02 | 33.5 | bar a |  | inch | [8 empty] | 0 | 32.5 | 1 | 240 | 814 |  | 0 | 0 | 260087 | 32.5 | 1 | 240 | 814 | 23.7 | 166.2 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.85 | 0.9 |  | 1 | 1 | 0.72 |  | Max case: C1 EOR - Lean Gas, no condensate to D 3003
S-02115 | LV-6082 | L | 0.43 | cP | [5 empty] | 3 | inch | [8 empty] | 0 | 2.5 | 1.5 | 65 | 980 |  | 0 | 0 | 47200 | 2.5 | 1.5 | 65 | 980 |  | 55.2289 | 2.9337 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 |  | 0.9 |  | 1 | 1 | 0.72
S-02115 | LV-7251 | L | 0.159 | cP |  |  |  | 8.5 | bar a | 2 | inch | [8 empty] | 4927 | 7.5 | 0 | 173 | 894 | 13.9 | 7.5 |  | 9854 | 7.5 | 0 | 173 | 894 | 13.9 | 15 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 0.91 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-1006 | G | 0.013 | cP | 0.93 | 1.28 | 16.74 |  |  | 10 | inch | [8 empty] | 178361 | 51.9 | 50 | 40 |  |  | 594.3535 | 23.2291 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | PV-1011 | G | 0.013 | cP | 0.92 | 1.21 | 18.57 |  |  | 6 | inch | [8 empty] | 16337 | 50 | 4.5 | 40 |  |  | 20.9257 | 54.6883 | 31103 | 50 | 4.5 | 40 |  |  | 39.8392 | 104.1176 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas. Max case: C3 EOR - Lean Gas and no purge gas to fuel.
S-02115 | PV-1045 | G | 0.021 | cP | 1.01 | 1.19 | 16.54 |  |  |  | inch | 42500 | 25 | 0 | 365 |  |  | 151.9568 |  | 0 | 47.3 | 0 | 365 |  |  | 0 |  | 85000 | 47.3 | 1.5 | 365 |  |  | 163.6352 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. case is 50% of normal NG flow outlet HDS
S-02115 | PV-2015 | S | 0.019 | cP |  |  | 18.02 |  |  | 4 | inch | [8 empty] | 10500 | 44 | 43.5 | 272 | 21.4 |  | 118.1881 | 16.9999 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | PV-2073 | G | 0.019 | cP | 0.94 | 1.19 | 17.47 |  |  |  | inch | [8 empty] | 0 | 42.3 | 0 | 262 |  |  | 0 |  | 212000 | 42.3 | 1.5 | 262 |  |  | 413.3308 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. case is 50% of normal saturated NG outlet E 6001
S-02115 | PV-2361 | S | 0.027 | cP |  |  | 18.02 |  |  |  | inch | [8 empty] | 0 | 100 | 0 | 460 | 33.3 |  | 0 |  | 117000 | 100 | 0 | 460 | 33.3 |  | 130.6218 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. case is 30% of normal HHP Steam outlet E 2021
S-02115 | PV-2363 | S | 0.027 | cP |  |  | 18.02 |  |  | 24 | inch | [8 empty] | 389772 | 100 | 99.7 | 460 | 33.3 |  | 4523.377 | 11.1732 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | PV-2406 | G | 0.019 | cP | 0.99 | 1.32 | 13.17 |  |  |  | inch | [8 empty] | 0 | 25.8 | 0 | 165 |  |  | 0 | 0 | 375000 | 25.8 | 1.5 | 165 |  |  | 904.1206 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. case is 50% of normal process gas flow outlet D 2002
S-02115 | PV-2481 | G | 0.016 | cP | 1.01 | 1.39 | 11.44 |  |  |  | inch | [8 empty] | 0 | 24 | 0 | 48 |  |  | 0 |  | 552868 | 24 | 1.5 | 48 |  |  | 1122.229 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. is 100% vent of C3 EOR - Rich gas
S-02115 | PV-2536 | G |  |  | 1 | 1.37 | 10.66 |  |  |  | inch | [16 empty] | 66777 | 3.6 | 0 | 47 |  |  | 709.9767 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PCV-2551 | G |  |  | 0.99 | 1.3 | 16.74 |  |  | 1.5 | inch | [8 empty] | 0 | 4 | 2 | 35 |  |  | 0 | 0 | [8 empty] | 620 | 4 | 3 | 35 |  |  | 10.3241 | 44.8913 | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PDV-2575 | G |  |  | 1 | 1.41 | 28.01 |  |  | 8 | inch | [8 empty] | 0 | 6 | 5.5 | 70 |  |  | 0 |  | 40000 | 7 | 6 | 70 |  |  | 690.4885 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0.72
S-02115 | PV-2603 | G |  |  | 1.01 | 1.41 | 3.32 |  |  | 1.5 | inch | [8 empty] | 3380 | 25 | 24 | 40 |  |  | 10.4805 | 39.9007 | 5000 | 25 | 24 | 40 |  |  | 15.5037 | 59.0248 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 0.98 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-2608 | G |  |  | 1.03 | 1.37 | 11.6 |  |  | 1.5 | inch | [8 empty] | 5061 | 76.2 | 50.4 | 48 |  |  | 3.9197 | 29.8091 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | PCV-3008 | G | 0.016 | cP | 1.01 | 1.39 | 11.44 |  |  | 1.5 | inch | [8 empty] | 0 | 24 | 10 | 48 |  |  | 0 | 0 | 2200 | 24 | 10 | 48 |  |  | 4.5529 | 60.4926 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-3042 | S | 0.018 | cP |  |  | 18.02 |  |  | 24 | inch | [8 empty] | 278728 | 33.7 | 33.4 | 242 | 17.4 |  | 4486.666 | 15.3787 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | PV-3166 | G | 0.016 | cP | 1.03 | 1.37 | 11.4 |  |  |  | inch | [8 empty] | 0 | 83.7 | 1.5 | 48 |  |  | 0 |  | 100000 | 83.7 | 1.5 | 48 |  |  | 60.8584 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. is vent of C3 EOR - Rich gas
S-02115 | PV-3194 | G | 0.016 | cP | 0.99 | 1.29 | 29.9 |  |  | 6 | inch | [8 empty] | 4946 | 4 | 3.6 | 48 |  |  | 166.6827 | 20.2925 | [16 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas
S-02115 | PCV-5009 | G |  | cP | 1 | 1.41 | 28.01 |  |  | 2 | inch | [8 empty] | 350 | 6 | 0 | 40 |  |  | 3.8681 | 57.3867 | 3220 | 6 | 0 | 40 |  |  | 35.5861 | 527.9575 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0.72 | Normal case is max. pump out. Max. case is normal case plus thermal inbreathing.
S-02115 | PV-5069 | S | 0.016 | cP | 1 | 1.23 | 8.02 |  |  | 10 | inch | [8 empty] | 34117 | 7 | 2.4 | 188 | 3.97 |  | 419.2688 | 110.6062 | [16 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-5091/A | G |  | cP | 1 | 1.41 | 28.01 |  |  | 1.5 | inch | [16 empty] | 1000 | 6 | 0.7 | 40 |  |  | 11.0516 | 172.3743 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-5091/B | G | 0.013 |  | 0.99 | 1.2 | 43.59 |  |  | 4 | inch | [8 empty] | 586 | 0.4 | 0.2 | 48 |  |  | 66.0168 | 20.5724 | 1200 | 0.4 | 0.2 | 48 |  |  | 135.188 | 42.1278 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C3 EOR - Rich Gas.
S-02115 | PV-5109 | G | 0.013 | cP | 0.99 | 1.2 | 43.59 |  |  | 4 | inch | [8 empty] | 0 | 0.6 | 0.5 | 48 |  |  | 0 | 0 | 1200 | 0.7 | 0.5 | 48 |  |  | 121.0263 | 33.7746 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-5207/A | G |  | cP | 1 | 1.41 | 28.01 |  |  | 1.5 | inch | [16 empty] | 1000 | 6 | 0.1 | 40 |  |  | 11.0516 | 265.2985 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-5207/B | G |  | cP | 1 | 1.41 | 28.01 |  |  | 2 | inch | [16 empty] | 500 | 0.35 | 0 | 65 |  |  | 37.5309 | 88.5258 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PCV-5395 | G |  | cP | 1 | 1.41 | 28.01 |  |  | 1.5 | inch | [8 empty] | 310 | 6 | 0 | 40 |  |  | 3.426 | 90.3613 | 1430 | 6 | 0 | 40 |  |  | 15.8038 | 416.8277 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case is max. pump out. Max. case is normal case plus thermal inbreathing.
S-02115 | PCV-5412 | G |  | cP | 1 | 1.41 | 28.01 |  |  | 1.5 | inch | [8 empty] | 310 | 6 | 0 | 40 |  |  | 3.426 | 90.3613 | 1430 | 6 | 0 | 40 |  |  | 15.8038 | 416.8277 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case is max. pump out. Max. case is normal case plus thermal inbreathing.
S-02115 | PCV-5445 | G |  | cP | 1 | 1.41 | 28.01 |  |  | 1 | inch | [8 empty] | 5 | 6 | 0 | 40 |  |  | 0.055258 | 3.2792 | 19 | 6 | 0 | 40 |  |  | 0.20998 | 12.4611 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0.72 | Normal case is max. pump out. Max. case is normal case plus thermal inbreathing.
S-02115 | PV-6025 | S | 0.019 | cP |  |  | 18.02 |  |  | 20 | inch | [8 empty] | 260087 | 32.7 | 31.7 | 240 | 16.9 |  | 2349.729 | 21.7365 | 260087 | 32.7 | 32.2 | 240 | 16.9 |  | 3300.045 | 21.4093 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | PV-7002/A | S | 0.027 | cP | 0.89 | 1.18 | 18.02 |  |  |  | inch | [8 empty] | 500 | 98 | 44 | 454 | 33 |  | 0.61942 |  | 40000 | 98 | 44 | 454 | 33 |  | 49.5538 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-7002/B | S | 0.027 | cP | 0.89 | 1.18 | 18.02 |  |  |  | inch | [8 empty] | 0 | 98 | 44 | 454 | 33 |  | 0 |  | 389772 | 98 | 44 | 454 | 33 |  | 482.8669 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max. case: C3 EOR - Rich Gas
S-02115 | PV-7002/C | S | 0.027 | cP | 0.89 | 1.18 | 18.02 |  |  |  | inch | [8 empty] | 0 | 98 | 44 | 454 | 33 |  | 0 |  | 389772 | 98 | 44 | 454 | 33 |  | 482.8669 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Max case: C3 EOR - Rich Gas
S-02115 | PV-7004 | S | 0.022 | cP | 0.91 | 1.19 | 18.02 |  |  |  | inch | [16 empty] | 404583 | 44 |  | 345 | 17.3 |  | 1018.232 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 | 0.9 | 1 | 1 | 0.72 | 0.72 | Downstream pressure by EPC & silencer vendor
S-02115 | PV-7025/A | S | 0.027 | cP | 0.89 | 1.18 | 18.02 |  |  |  | inch | [8 empty] | 97820 | 98 | 44 | 454 | 33 |  | 121.1837 |  | 115000 | 98 | 44 | 454 | 33 |  | 142.4671 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C2 SOR - Lean Gas
S-02115 | PV-7025/B | S | 0.027 | cP | 0.89 | 1.18 | 18.02 |  |  |  | inch | [8 empty] | 97820 | 98 | 44 | 454 | 33 |  | 121.1837 |  | 115000 | 98 | 44 | 454 | 33 |  | 142.4671 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C2 SOR - Lean Gas
S-02115 | PV-7028 | S | 0.025 | cP | 0.94 | 1.23 | 18.02 |  |  | 20 | inch | [8 empty] | 0 | 43 | 43 | 410 | 14.8 |  |  |  | 200000 | 43 | 42.5 | 410 | 14.8 |  | 2709.312 | 18.7331 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-7031/A | S | 0.022 | cP | 0.91 | 1.19 | 18.02 |  |  |  | inch | [8 empty] | 0 | 44 | 34 | 345 | 17.3 |  | 0 |  | 260087 | 44 | 34 | 345 | 17.3 |  | 824.033 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 | 0.9 | 1 | 1 | 0.72 | 0.72
S-02115 | PV-7031/B | S | 0.022 | cP | 0.91 | 1.19 | 18.02 |  |  |  | inch | [8 empty] | 0 | 44 | 34 | 345 | 17.3 |  | 0 |  | 260087 | 44 | 34 | 345 | 17.3 |  | 824.033 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 | 0.9 | 1 | 1 | 0.72 | 0.72
S-02115 | PV-7031/C | S | 0.018 | cP | 0.84 | 1.12 | 18.02 |  |  |  | inch | [8 empty] | 24587 | 32.7 | 7 | 240 | 16.9 |  | 74.5691 |  | 50000 | 32.7 | 7 | 240 | 16.9 |  | 151.6434 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas
S-02115 | PV-7031/D | S | 0.018 | cP | 0.84 | 1.12 | 18.02 |  |  |  | inch | [8 empty] | 24587 | 32.7 | 7 | 240 | 16.9 |  | 74.5691 |  | 50000 | 32.7 | 7 | 240 | 16.9 |  | 151.6434 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | PV-7034 | S | 0.019 | cP | 0.82 | 1.11 | 18.02 |  |  |  | inch | [8 empty] | 0 | 32.7 |  | 240 | 20.5 |  | 0 |  | 281504 | 32.7 |  | 240 | 20.5 |  | 778.6676 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure by EPC & silencer vendor
S-02115 | PV-7051/A | S | 0.022 | cP | 0.91 | 1.19 | 18.02 |  |  |  | inch | [8 empty] | 0 | 44 | 7.5 | 345 | 17.3 |  | 0 |  | 130000 | 44 | 7.5 | 345 | 17.3 |  | 327.1768 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-7051/B | S | 0.022 | cP | 0.91 | 1.19 | 18.02 |  |  |  | inch | [8 empty] | 0 | 44 | 7.5 | 345 | 17.3 |  | 0 |  | 130000 | 44 | 7.5 | 345 | 17.3 |  | 327.1768 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-7056 | S | 0.016 | cP | 0.95 | 1.23 | 18.02 |  |  |  | inch | [8 empty] | 0 | 7 |  | 188 | 3.97 |  | 0 |  | 196600 | 7 |  | 188 | 3.97 |  | 2407.924 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure by EPC & silencer vendor
S-02115 | PV-7094 | S | 0.016 | cP | 0.95 | 1.23 | 18.02 |  |  | 12 | inch | [8 empty] | 0 | 7 | 1 | 188 | 3.97 |  | 0 | 0 | 49000 | 7 | 1 | 188 | 3.97 |  | 600.1438 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | PV-7101 | S |  |  |  |  | 18.02 | [20 empty] | 83000 | 2 | 0 | 120 | 1.66 |  | 2408.838 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 | 0.9 | 1 | 1 | 0.72 | 0
S-02115 | TV-2220 | G | 0.013 | cP | 0.93 | 1.28 | 16.74 |  |  | 6 | inch | [16 empty] | 50000 | 50 | 49.8 | 40 |  |  | 515.448 | 18.1595 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38
S-02115 | TV-2457 | G | 0.019 | cP | 1 | 1.36 | 12.32 |  |  | 16 | inch | [16 empty] | 160000 | 24.8 | 24.7 | 138 |  |  | 3341.692 | 21.2025 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38
S-02115 | TV-3113 | G | 0.017 | cP | 1.04 | 1.37 | 11.41 |  |  | 10 | inch | [16 empty] | 185000 | 90 | 89.8 | 748 |  |  | 2247.004 | 44.134 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Max case: C3 EOR - Rich Gas, 25 % bypass
S-02115 | TV-3116 | G | 0.017 | cP | 1.04 | 1.37 | 11.41 |  |  | 10 | inch | [16 empty] | 185000 | 90 | 89.8 | 748 |  |  | 2247.004 | 44.134 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Max case: C3 EOR - Rich Gas, 25 % bypass
S-02115 | TV-3118 | G | 0.017 | cP | 1.04 | 1.37 | 11.41 |  |  | 10 | inch | [16 empty] | 185000 | 90 | 89.8 | 748 |  |  | 2247.004 | 44.134 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Max case: C3 EOR - Rich Gas, 25 % bypass
S-02115 | TV-5064 | G | 0.019 | cP | 0.99 | 1.32 | 13.17 |  |  | 16 | inch | [16 empty] | 180000 | 25.3 | 25.2 | 159 |  |  | 3920.708 | [9 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Max case: C3 EOR - Rich Gas, 25 % bypass
S-02115 | TV-5277 | G | 0.019 | cP | 0.99 | 1.32 | 13.17 |  |  | 18 | inch | [16 empty] | 188000 | 25.8 | 25.7 | 165 |  |  | 4091.238 | 20.1917 | [8 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Max case: C3 EOR - Rich Gas, 25 % bypass
S-02115 | TV-7002 | L | 0.23 | cP | [5 empty] | 1 | inch | [8 empty] | 19 | 120 | 44 | 122 | 947 |  | 0.0025942 | 0.010999 | 3000 | 120 | 44 | 122 | 947 |  | 0.40962 | 1.7366 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure depends on design of PV-7002/A
S-02115 | TV-7003 | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 120 | 44 | 122 | 947 |  | 0 | 0 | 29000 | 120 | 44 | 122 | 947 |  | 3.9596 | 7.4612 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure depends on design of PV-7002/B
S-02115 | TV-7004 | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 120 | 44 | 122 | 947 |  | 0 | 0 | 29000 | 120 | 44 | 122 | 947 |  | 3.9596 | 7.4612 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure depends on design of PV-7002/C
S-02115 | TV-7025/A | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 50 | 43 | 122 | 945 |  | 0 | 0 | 13000 | 50 | 42.5 | 122 | 945 |  | 5.6563 | 3.3517 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure is steam pressure. The stated Cv is the combination of valve and nozzle TZ-7025.
S-02115 | TV-7025/B | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 50 | 43 | 122 | 945 |  | 0 | 0 | 13000 | 50 | 42.5 | 122 | 945 |  | 5.6563 | 3.3517 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure is steam pressure. The stated Cv is the combination of valve and nozzle TZ-7025.
S-02115 | TV-7026 | L | 0.23 | cP | [5 empty] | 1 | inch | [8 empty] | 836 | 120 | 43 | 122 | 947 |  | 0.1134 | 0.48395 | 1500 | 120 | 43 | 122 | 947 |  | 0.20347 | 0.86832 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure depends on design of PV-7025/A
S-02115 | TV-7027 | L | 0.23 | cP | [5 empty] | 1 | inch | [8 empty] | 836 | 120 | 43 | 122 | 947 |  | 0.1134 | 0.48395 | 1500 | 120 | 43 | 122 | 947 |  | 0.20347 | 0.86832 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure depends on design of PV-7025/B
S-02115 | TV-7032 | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 50 | 33.7 | 122 | 945 |  | 0 | 0 | 26100 | 50 | 33.7 | 122 | 945 |  | 7.7031 | 6.7293 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 | 0.9 | 1 | 1 | 0.72 | 0.72 | Downstream pressure depends on design of PV-7031/B
S-02115 | TV-7033 | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 50 | 33.7 | 122 | 945 |  | 0 | 0 | 26100 | 50 | 33.7 | 122 | 945 |  | 7.7031 | 6.7293 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Downstream pressure depends on design of PV-7031/A
S-02115 | TV-7052 | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 50 | 7 | 122 | 945 |  | 0 | 0 | 14500 | 50 | 7 | 122 | 945 |  | 2.6348 | 3.7385 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 | 0.9 | 1 | 1 | 0.72 | 0.72
S-02115 | TV-7053 | L | 0.23 | cP | [5 empty] | 1.5 | inch | [8 empty] | 0 | 50 | 7 | 122 | 945 |  | 0 | 0 | 14500 | 50 | 7 | 122 | 945 |  | 2.6348 | 3.7385 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | TV-7071/A | L | 0.23 | cP | [5 empty] | 1 | inch | [8 empty] | 857 | 50 | 44 | 122 | 945 |  | 0.41689 |  | 1000 | 50 | 44 | 122 | 945 |  | 0.48646 | [9 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | TV-7071/B | L | 0.23 | cP | [5 empty] | 1 | inch | [8 empty] | 857 | 50 | 44 | 122 | 945 |  | 0.41689 | 0.49715 | 1000 | 50 | 44 | 122 | 945 |  | 0.48646 | 0.58011 | [8 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | USV-1001 | L |  | cP | [5 empty] | 2 | inch | [8 empty] | 0 | 52 | 52 | 40 | [20 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15
S-02115 | USV-2010 | G | 0.022 | cP | 0.98 | 1.39 | 32.01 |  |  | 12 | inch | [8 empty] | 65769 | 35 | 35 | 35 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-2021 | S | 0.019 | cP |  |  | 18.02 |  |  | 6 | inch | [8 empty] | 10500 | 44 | 44 | 272 | 21.4 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-2038 | S | 0.022 | cP |  |  | 18.02 |  |  | 4 | inch | [8 empty] | 4588 | 44 | 44 | 345 | 17.3 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-2043 | G | 0.03 | cP | 1 | 1.36 | 32.01 |  |  | 2 | inch | [8 empty] | 0 | 34 | 0 | 230 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | USV-2045 | G | 0.03 | cP | 1 | 1.36 | 32.01 |  |  | 16 | inch | [8 empty] | 65769 | 34 | 34 | 230 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USY-2045 | G | 0.03 | cP | 1 | 1.36 | 32.01 |  |  | 3 | inch | [8 empty] | 0 | 34 | 0 | 230 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72 | 0.72
S-02115 | USV-2048 | G | 0.03 | cP | 1 | 1.36 | 32.01 |  |  | 16 | inch | [8 empty] | 65769 | 34 | 34 | 230 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-2049 | G | 0.03 | cP | 1 | 1.36 | 32.01 |  |  | 3 | inch | [8 empty] | 0 | 34 | 0 | 230 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | USV-2092 | G | 0.019 | cP | 0.94 | 1.19 | 17.47 |  |  | 24 | inch | [8 empty] | 423949 | 42.1 | 42.1 | 262 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-2093 | G | 0.019 | cP | 0.94 | 1.19 | 17.47 |  |  | 24 | inch | [8 empty] | 423949 | 42.1 | 42.1 | 262 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-2094 | G | 0.019 | cP | 0.94 | 1.19 | 17.47 |  |  | 1 | inch | [8 empty] | 0 | 41.1 | 0 | 262 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.9 |  | 1 | 1 | 0.72
S-02115 | UV-2125 | G | 0.017 | cP | 1 | 1.27 | 28.99 |  |  | 24 | inch | [8 empty] | 8508 | 0 | 0 | 45 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38
S-02115 | UV-2233 | L | 0.23 | cP |  |  | 18.02 |  |  | 3 | inch | [8 empty] | 0 | 52 | 52 | 49 | 944 |  |  |  | 17000 | 52 | 52 | 49 | 944 | [11 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15
S-02115 | USV-2381 | L | 0.089 | cP |  |  | 18.02 | 104 | bar a | 2 | inch | [8 empty] | 3837 | 103 | 103 | 313 | 684 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-2482 | G | 0.016 | cP | 1.01 | 1.39 | 11.44 |  |  | 12 | inch | [8 empty] | 0 | 24 | 0 | 48 |  |  | 0 |  | 269605 | 24 | 24 | 48 | [12 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38
S-02115 | USV-2541 | G |  |  | 1 | 1.37 | 13.9 |  |  | 28 | inch | [8 empty] | 80880 | 2 | 2 | 45 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-2542 | G |  |  | 1 | 1.37 | 13.9 |  |  | 28 | inch | [8 empty] | 80880 | 2 | 2 | 45 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-2543 | G |  |  | 1 | 1.37 | 11.9 |  |  | 2 | inch | [8 empty] | 0 | 2 | 0 | 45 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 | 0.15
S-02115 | USV-2544 | G |  |  | 1 | 1.37 | 13.03 |  |  | 24 | inch | [8 empty] | 67806 | 2 | 2 | 47 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-2545 | G |  |  | 1 | 1.37 | 11.9 |  |  | 2 | inch | [8 empty] | 0 | 2 | 0 | 45 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 | 0.15
S-02115 | USV-2547 | G |  |  | 0.95 | 1.24 | 16.74 |  |  | 2 | inch | [8 empty] | HOLD | 4 | 4 | 35 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 | 0.15
S-02115 | USV-2548 | G |  |  | 0.95 | 1.24 | 16.74 |  |  | 2 | inch | [8 empty] | HOLD | 4 | 4 | 35 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15
S-02115 | USV-2549 | G |  |  | 0.95 | 1.34 | 16.74 |  |  | 1.5 | inch | [8 empty] | 0 | 4 | 0 | 35 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15
S-02115 | USV-3018 | G |  | cP | [5 empty] | 3 | inch | [8 empty] | 0 | 6 | 6 | 48 | [20 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15
S-02115 | USV-3052 | L | 0.11 | cP |  |  | 18.02 | 34.7 | bar a | 1 | inch | [8 empty] | 2815 | 33.7 | 33.7 | 242 | 811 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 |  | Normal case: C4 SOR - Rich Gas.
S-02115 | USV-3172 | L | 0.39 | cP |  |  | 29.6 |  |  | 10 | inch | [8 empty] | 246704 | 83.7 | 83.7 | 48 | 757 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 1 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | UV-5021 | G | 0.017 | cP | 1 | 1.27 | 28.99 |  |  | 24 | inch | [8 empty] | 0 | 0 | 0 | 45 |  |  |  |  | 8508 | 0 | 0 | 45 | [12 empty] | Nm3/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38
S-02115 | USV-5302 | S | 0.016 | cP |  |  | 18.02 |  |  | 32 | inch | [8 empty] | 196357 | 7 | 7 | 188 | 3.97 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C4 SOR - Lean Gas.
S-02115 | USV-5391 | L | 0.4 | cP |  |  | 32.04 |  |  | 10 | inch | [8 empty] | 208338 | 1.1 | 1.1 | 48 | 766 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-5392 | L | 0.4 | cP |  |  | 32.04 |  |  | 10 | inch | [8 empty] | 208338 | 3 | 3 | 48 | 766 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-5393 | L | 0.4 | cP |  |  | 32.04 |  |  | 3 | inch | [8 empty] | 0 | 1 | 1 | 48 | 766 |  |  |  | *) | 1 | 1 | 48 | 766 | [11 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 |  | Max. case is minimum flow for P 5008 A/B. *) Flow by pump vendor.
S-02115 | USV-5420 | L | 0.4 | cP |  |  | 32.04 |  |  | 10 | inch | [8 empty] | 208338 | 1.1 | 1.1 | 48 | 766 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | USV-5421 | L | 0.4 | cP |  |  | 32.04 |  |  | 3 | inch | [8 empty] | 0 | 1 | 1 | 48 | 766 |  |  |  | *) | 1 | 1 | 48 | 766 | [11 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15 | 0.15 | Max. case is minimum flow for P 5008 A/B. *) Flow by pump vendor.
S-02115 | USV-5422 | L | 0.4 | cP |  |  | 32.04 |  |  | 10 | inch | [8 empty] | 208338 | 1.1 | 1.1 | 48 | 766 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C3 EOR - Rich Gas
S-02115 | UV-6035 | L | 0.24 | cP |  |  | 18.02 |  |  | 8 | inch | [8 empty] | 209041 | 44 | 44 | 119 | 945 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.68 |  | 1 | 0.7 | 0.38 |  | Normal case: C1 EOR - Lean Gas
S-02115 | USV-6081 | L | 0.12 | cP |  |  | 18.02 |  |  | 2 | inch | [8 empty] | 6179 | 1 | 1 | 78 | 975 | [19 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15
S-02115 | USV-6082 | L | 0.12 | cP |  |  | 18.02 |  |  | 4 | inch | [8 empty] | 0 | 43 | 0 | 225 | 834 |  |  |  | 54000 | 43 | 0 | 225 | 834 | [11 empty] | kg/h | bar g | bar g | kg/m3 | m/s | °C | 1 | 1 | 0.55 |  | 1 | 1 | 0.15

## Safety Valve Calc._d
Job No. | Tag No. | Fluid | Covering Code | Viscosity | Viscosity Unit | Compressibility | Cp/Cv | Mole Weight | Flash | Density | Density Unit | Super heat corr. | Capacity | Capacity Unit | Source of Overpressure | MAWP | Set Pressure | Accumulation (% MAWP) | Relief (% above S.P.) | Blow Down | Sup. back Pressure | Build-up (% of S.P.) | Alfa (AD-Merkblatt) | Relief Temperature | Relief Temperature Unit | Calc. Orifice | Calc. Orifice Unit
S-02115 | PSV-1008 | G | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.28 | 16.74 |  |  |  |  | 1) | Nm3/h | Inadvertent opening of PV-1006 | 55 | 55 | 10 | 10 | 2011-07-05 | <1.5 | <7.2 |  | 40 | °C
S-02115 | PSV-1009 | G | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.28 | 16.74 |  |  |  |  | 1) | Nm3/h | Inadvertent opening of PV-1006 | 55 | 55 | 10 | 10 | 2011-07-05 | <1.5 | <7.2 |  | 40 | °C
S-02115 | PSV-1013 | G | API 520, ASME Section VIII Division I |  |  | 0.99 | 1.3 | 16.74 |  |  |  |  | 37000 | Nm3/h | Inadvertent opening of PV-1011 Cv=44 | 7 | 7 | 10 | 10 | 2011-07-05 | <1.5 | <8.6 |  | 35 | °C | 52.721 | cm²
S-02115 | PSV-1014 | G | API 520, ASME Section VIII Division I |  |  | 0.99 | 1.3 | 16.74 |  |  |  |  | 37000 | Nm3/h | Inadvertent opening of PV-1011 Cv=44 | 7 | 7 | 10 | 10 | 2011-07-05 | <1.5 | <8.6 |  | 35 | °C | 52.721 | cm²
S-02115 | PSV-1015 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.26 | 16.74 |  |  |  |  | 1) |  | Fire - unwetted surface | 60 | 60 | 21 | 21 | 2011-07-05 | <1.5 | <18.5 |  |  | °C | 0.2 | cm²
S-02115 | PSV-1031 | G | API 520, ASME Section VIII Division I |  |  | 1.01 | 1.18 | 16.54 |  |  |  |  | 1) |  | Fire - unwetted surface | 55 | 55 | 21 | 21 | 2011-07-05 | <1.5 | <18.2 |  |  | °C | 0.45 | cm²
S-02115 | PSV-1038 | G | API 520, ASME Section VIII Division I |  |  | 1.01 | 1.18 | 16.54 |  |  |  |  | 1) |  | Fire - unwetted surface | 55 | 55 | 21 | 21 | 2011-07-05 | <1.5 | <18.2 |  |  | °C | 0.45 | cm²
S-02115 | PSV-1043 | G | API 520, ASME Section VIII Division I |  |  | 1.01 | 1.18 | 16.54 |  |  |  |  | 1) |  | Fire - unwetted surface | 55 | 55 | 21 | 21 | 2011-07-05 | <1.5 | <18.2 |  |  | °C | 0.45 | cm²
S-02115 | PSV-2019 | S | API 520, ASME Section VIII Division I |  |  | 0.78 | 1.09 | 18.02 |  | 31.38 | kg/m3 | 1 | 450 | kg/h | Fire - wetted surface | 52 | 52 | 21 | 21 | 2011-07-05 | 0 | <21 |  | 290 | °C | 0.13746 | cm²
S-02115 | PSV-2078 | G | API 520, ASME Section VIII Division I |  |  | 1.02 | 1.39 | 9.37 |  |  |  |  | 1) | Nm3/h | Inadvertent opening of FV-2079 | 52 | 52 | 10 | 10 | 2011-07-05 | <1.5 | <7.1 |  | 48 | °C
S-02115 | PSV-2121 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.72 | kg/m3 |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 194 | °C | 1) | cm²
S-02115 | PSV-2122 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.72 | kg/m3 |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 194 | °C | 1) | cm²
S-02115 | PSV-2171 | S | API 520, ASME Section VIII Division I |  |  | 0.94 | 1.21 | 18.02 |  |  |  |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 204 | °C | 1) | cm²
S-02115 | PSV-2172 | S | API 520, ASME Section VIII Division I |  |  | 0.94 | 1.21 | 18.02 |  |  |  |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 204 | °C | 1) | cm²
S-02115 | PSV-2354 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 29 | 16 | 16 | 2011-07-05 | <1.5 | <10.8 |  | 360 | °C | 65.771 | cm²
S-02115 | PSV-2355 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 29 | 16 | 16 | 2011-07-05 | <1.5 | <10.8 |  | 360 | °C | 65.771 | cm²
S-02115 | PSV-2356 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 30.4 | 16 | 10.5 | 2011-07-05 | <1.5 | <5.5 |  | 360 | °C | 65.862 | cm²
S-02115 | PSV-2357 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 30.4 | 16 | 10.5 | 2011-07-05 | <1.5 | <5.5 |  | 360 | °C | 65.862 | cm²
S-02115 | PSV-2358 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 30.4 | 16 | 10.5 | 2011-07-05 | <1.5 | <5.5 |  | 360 | °C | 65.862 | cm²
S-02115 | PSV-2359 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 30.4 | 16 | 10.5 | 2011-07-05 | <1.5 | <5.5 |  | 360 | °C | 65.862 | cm²
S-02115 | PSV-2360 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.33 | 13.14 |  |  |  |  | 145000 | Nm3/h | Blocked outlet | 29 | 29 | 16 | 16 | 2011-07-05 | <1.5 | <10.8 |  | 360 | °C | 65.771 | cm²
S-02115 | PSV-2376 | S | ASME Section I |  |  | 0.62 | 1.04 | 18.02 |  | 69.8 | kg/m3 | 1 | 107500 | kg/h | Blocked outlet | 112 | 112 | 6 | 6 | 2011-04-02 | 0 | <6 |  | 324 | °C | 19.483 | cm²
S-02115 | PSV-2377 | S | ASME Section I |  |  | 0.62 | 1.04 | 18.02 |  | 69.8 | kg/m3 | 1 | 107500 | kg/h | Blocked outlet | 112 | 115.2 | 6 | 3 | 2011-04-02 | 0 | <3 |  | 324 | °C | 19.493 | cm²
S-02115 | PSV-2378 | S | ASME Section I |  |  | 0.62 | 1.04 | 18.02 |  | 69.8 | kg/m3 | 1 | 107500 | kg/h | Blocked outlet | 112 | 115.2 | 6 | 3 | 2011-04-02 | 0 | <3 |  | 324 | °C | 19.493 | cm²
S-02115 | PSV-2379 | S | ASME Section I |  |  | 0.62 | 1.04 | 18.02 |  | 69.8 | kg/m3 | 1 | 107500 | kg/h | Blocked outlet | 112 | 115.2 | 6 | 3 | 2011-04-02 | 0 | <3 |  | 324 | °C | 19.493 | cm²
S-02115 | PSV-2380 | S | ASME Section I |  |  | 0.62 | 1.04 | 18.02 |  | 69.8 | kg/m3 | 1 | 107500 | kg/h | Blocked outlet | 112 | 112 | 6 | 6 | 2011-04-02 | 0 | <6 |  | 324 | °C | 19.483 | cm²
S-02115 | PSV-2458 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.36 | 12.06 |  |  |  |  | 13200 | Nm3/h | Tube rupture E 2025 | 14 | 14 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 138 | °C | 9.6813 | cm²
S-02115 | PSV-2494 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.39 | 11.24 |  |  |  |  | 6000 | Nm3/h | Tube rupture E 2027 | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 56.4 | °C | 6.6859 | cm²
S-02115 | PSV-2546 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.4 | 28.01 |  |  |  |  | 1350 | Nm3/h | Inadvertent opening of HV-2545 Cv=15 | 7 | 7 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 40 | °C | 2.4545 | cm²
S-02115 | PSV-2555 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.4 | 28.01 |  |  |  |  | 1350 | Nm3/h | Inadvertent opening of HV-2545 Cv=15 | 7 | 7 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 40 | °C | 2.4545 | cm²
S-02115 | PSV-2581 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.41 | 28.01 |  |  |  |  | 31210 | Nm3/h | Blocked outlet | 10.5 | 10.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 40 | °C | 39.251 | cm²
S-02115 | PSV-2604 | G | API 520, ASME Section VIII Division I |  |  | 1.02 | 1.39 | 9.37 |  |  |  |  | 9500 | Nm3/h | Inadvertent opening of PV-2608 Cv=5.5 | 60 | 60 | 10 | 10 | 2011-07-05 | 1.5 | <7.5 |  | 48 | °C | 1.332 | cm²
S-02115 | PSV-2605 | G | API 520, ASME Section VIII Division I |  |  | 1.02 | 1.39 | 9.37 |  |  |  |  | 9500 | Nm3/h | Inadvertent opening of PV-2608 Cv=5.5 | 60 | 60 | 10 | 10 | 2011-07-05 | 1.5 | <7.5 |  | 48 | °C | 1.332 | cm²
S-02115 | PSV-3021 | G | API 520, ASME Section VIII Division I | [9 empty] | 1) |  | Fire - unwetted surface | 99 | 99 | 21 | 21 | 2011-07-05 | <1.5 | <19.4 |  |  | °C | 1.113 | cm²
S-02115 | PSV-3047 | S | ASME Section I |  |  | 0.8 | 1.1 | 18.02 |  | 24.67 | kg/m3 | 1 | 155000 | kg/h | Blocked outlet | 45 | 45 | 6 | 6 | 2011-04-02 | 0 | <6 |  | 262 | °C | 69.048 | cm²
S-02115 | PSV-3048 | S | ASME Section I |  |  | 0.8 | 1.1 | 18.02 |  | 24.67 | kg/m3 | 1 | 155000 | kg/h | Blocked outlet | 45 | 46.3 | 6 | 3 | 2011-04-02 | 0 | <3 |  | 262 | °C | 69.048 | cm²
S-02115 | PSV-3057 | S | ASME Section I |  |  | 0.8 | 1.1 | 18.02 |  | 24.67 | kg/m3 | 1 | 155000 | kg/h | Blocked outlet | 45 | 45 | 6 | 6 | 2011-04-02 | 0 | <6 |  | 262 | °C | 69.048 | cm²
S-02115 | PSV-3143 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.37 | 10.07 |  |  |  |  | 43700 | Nm3/h | Tube rupture E 3003 1 | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 41.8 | °C | 45.298 | cm²
S-02115 | PSV-3146 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.37 | 10.07 |  |  |  |  | 43700 | Nm3/h | Tube rupture E 3003 1 | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 41.8 | °C | 45.298 | cm²
S-02115 | PSV-3149 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.37 | 10.07 |  |  |  |  | 43700 | Nm3/h | Tube rupture E 3003 1 | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 41.8 | °C | 45.298 | cm²
S-02115 | PSV-3163 | G | API 520, ASME Section VIII Division I | [9 empty] | 1) |  | Fire - unwetted surface | 99 | 99 | 21 | 21 | 2011-07-05 | <1.5 | <19.4 |  |  | °C | 6.34 | cm²
S-02115 | PSV-3173 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.38 | 9.37 |  |  |  |  | 100000 | Nm3/h | Inadvertent opening of FV-3169 Cv=49.3 | 7 | 7 | 10 | 10 | 2011-07-05 | <1.5 | <8.5 |  | 40 | °C | 105.71 | cm²
S-02115 | PSV-3174 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.38 | 9.37 |  |  |  |  | 100000 | Nm3/h | Inadvertent opening of FV-3169 Cv=49.3 | 7 | 7 | 10 | 10 | 2011-07-05 | <1.5 | <8.5 |  | 40 | °C | 105.71 | cm²
S-02115 | PSV-3196 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.38 | 9.37 |  |  |  |  | 80000 | Nm3/h | Inadvertent opening of LV-3161 A/B | 7 | 7 | 16 | 16 | 2011-07-05 | <1.5 | <15.5 |  | 48 | °C | 81.708 | cm²
S-02115 | PSV-3197 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.38 | 9.37 |  |  |  |  | 80000 | Nm3/h | Inadvertent opening of LV-3161 A/B | 7 | 7.35 | 16 | 10.5 | 2011-07-05 | <1.5 | <9.5 |  | 48 | °C | 81.692 | cm²
S-02115 | PSV-3206 | G | API 520, ASME Section VIII Division I |  |  | 1 | 1.38 | 9.37 |  |  |  |  | 80000 | Nm3/h | Inadvertent opening of LV-3161 A/B | 7 | 7 | 16 | 16 | 2011-07-05 | <1.5 | <15.5 |  | 48 | °C | 81.708 | cm²
S-02115 | PSV-5006 | G | API 2000, API 650 |  |  | 1 | 1.25 | 25.95 |  |  |  |  | 35000 | Nm3/h | Inadvertent opening of LV-3192 Cv=313 | 0.02 | [8 empty] | °C
S-02115 | PSV-5007 | G | API 2000 | [11 empty] | In & Out-breathing | [9 empty] | °C
S-02115 | PSV-5058 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.18 | 29.92 |  |  |  |  | 29670 | Nm3/h | Reflux failure | 3.5 | 3.5 | 16 | 16 | 2011-07-05 | 1.5 | <7 |  | 116 | °C | 122.7 | cm²
S-02115 | PSV-5059 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.18 | 29.92 |  |  |  |  | 29670 | Nm3/h | Reflux failure | 3.5 | 3.67 | 16 | 10.5 | 2011-07-05 | 1.5 | <7 |  | 116 | °C | 122.8 | cm²
S-02115 | PSV-5060 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.18 | 29.92 |  |  |  |  | 29670 | Nm3/h | Reflux failure | 3.5 | 3.5 | 16 | 16 | 2011-07-05 | <1.5 | <7 |  | 116 | °C | 112.8 | cm²
S-02115 | PSV-5061 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.18 | 29.92 |  |  |  |  | 29670 | Nm3/h | Reflux failure | 3.5 | 3.5 | 16 | 16 | 2011-07-05 | 1.5 | <7 |  | 116 | °C | 122.7 | cm²
S-02115 | PSV-5073 | S | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.19 | 18.02 |  | 6.38 | kg/m3 | 1 | 600 | kg/h | Fire - wetted surface | 9.5 | 9.5 | 21 | 21 | 2011-07-05 | 0 | <21 |  | 190 | °C | 0.93684 | cm²
S-02115 | PSV-5085 | L | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 6125 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.68 | cm²
S-02115 | PSV-5108 | L | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 112 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.01 | cm²
S-02115 | PSV-5179 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.18 | 29.08 |  |  |  |  | 4000 | Nm3/h | Fire - wetted surface | 3.5 | 3.5 | 21 | 21 | 2011-07-05 | <1.5 | <7 |  | 121 | °C | 15.871 | cm²
S-02115 | PSV-5180 | G | API 520, ASME Section VIII Division I |  |  | 0.95 | 1.18 | 29.08 |  |  |  |  | 4000 | Nm3/h | Fire - wetted surface | 3.5 | 3.5 | 21 | 21 | 2011-07-05 | <1.5 | <7 |  | 121 | °C | 15.871 | cm²
S-02115 | PSV-5220 | G | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 600 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | <20 | 0 | <10 |  | 48 | °C | 0.07 | cm²
S-02115 | PSV-5236 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-5239 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-5250 | G | API 520, ASME Section VIII Division I |  |  | 0.94 | 1.18 | 27.1 |  |  |  |  | 41403 | Nm3/h | Reflux failure | 6 | 6 | 16 | 16 | 2011-07-05 | 1.5 | <12 |  | 141 | °C | 95.775 | cm²
S-02115 | PSV-5251 | G | API 520, ASME Section VIII Division I |  |  | 0.94 | 1.18 | 27.1 |  |  |  |  | 41403 | Nm3/h | Reflux failure | 6 | 6.3 | 16 | 10.5 | 2011-07-05 | 1.5 | <11 |  | 141 | °C | 95.757 | cm²
S-02115 | PSV-5261 | G | API 520, ASME Section VIII Division I |  |  | 0.94 | 1.18 | 27.1 |  |  |  |  | 41403 | Nm3/h | Reflux failure | 6 | 6 | 16 | 16 | 2011-07-05 | 1.5 | <12 |  | 141 | °C | 95.775 | cm²
S-02115 | PSV-5308 | L | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 1300 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.14 | cm²
S-02115 | PSV-5339 | L | API 520, ASME Section VIII Division I | [6 empty] | 989.3 | kg/m3 |  | 1400 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 |  | 0 | <10 |  | 48 | °C | 0.16 | cm²
S-02115 | PSV-5370 | L | API 520, ASME Section VIII Division I | [6 empty] | 989.3 | kg/m3 |  | 60 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.01 | cm²
S-02115 | PSV-5384 | G | API 520, ASME Section VIII Division I |  |  | 0.8 | 1.1 | 32 |  |  |  |  | 4120 | Nm3/h | Fire - wetted surface | 19 | 19 | 21 | 21 | 2011-07-05 | <1.5 | <13 |  | 175 | °C | 3.3768 | cm²
S-02115 | PSV-5386 | G | API 520, ASME Section VIII Division I |  |  | 0.8 | 1.1 | 32 |  |  |  |  | 4120 | Nm3/h | Fire - wetted surface | 19 | 19 | 21 | 21 | 2011-07-05 | <1.5 | <13 |  | 175 | °C | 3.3768 | cm²
S-02115 | PSV-5400 | G | API 2000, API 650 |  |  | 0.98 | 1.2 | 32 |  |  |  |  | 12000 | Nm3/h | Fire - wetted surface | 0.02 | [8 empty] | °C
S-02115 | PSV-5401 | G | API 2000, API 650 | [11 empty] | In & Out-breathing | [9 empty] | °C
S-02115 | PSV-5405 | L | API 520, ASME Section VIII Division I | 0.4 | cP |  |  |  |  | 766 | kg/m3 |  | 1) | kg/h | Blocked outlet | 52 | 52 | 10 | 10 |  |  |  |  | 48 | °C
S-02115 | PSV-5417 | G | API 2000, API 650 |  |  | 0.98 | 1.2 | 32 |  |  |  |  | 12000 | Nm3/h | Fire - wetted surface | [9 empty] | °C
S-02115 | PSV-5418 | G | API 2000 | [11 empty] | In & Out-breathing | [9 empty] | °C
S-02115 | PSV-5444 | G | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 60 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.01 | cm²
S-02115 | PSV-5450 | G | API 2000, API 650 |  |  | 0.98 | 1.21 | 30.2 |  |  |  |  | 8000 | Nm3/h | Fire - wetted surface | [9 empty] | °C
S-02115 | PSV-5451 | G | API 2000 | [11 empty] | In & Out-breathing | [9 empty] | °C
S-02115 | PSV-5461 | L | API 520, ASME Section VIII Division I | 0.46 | cP |  |  |  |  | 813 | kg/m3 |  | 1) | kg/h | Blocked outlet | 60 | 60 | 10 | 10 | <20 |  |  |  |  | °C | 1) | cm²
S-02115 | PSV-5462 | L | API 520, ASME Section VIII Division I | 0.46 | cP |  |  |  |  | 813 | kg/m3 |  | 1) | kg/h | Blocked outlet | 60 | 60 | 10 | 10 | <20 |  |  |  | 50 | °C | 1) | cm²
S-02115 | PSV-5501 | L | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 225 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.02 | cm²
S-02115 | PSV-5505 | L | API 520, ASME Section VIII Division I | 0.61 | cP |  |  |  |  | 991 | kg/m3 |  | 30000 | kg/h | Tube rupture E 5014 | 7.5 | 7.5 | 10 | 10 | <20 | 0 | <10 |  | 44 | °C | 3.36 | cm²
S-02115 | PSV-5512 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-5514 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-6021 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 946 | kg/m3 |  | 1) | kg/h | Inadvertent opening of FV-6031 or FV-5367 | 71 | 71 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 121 | °C | 1) | cm²
S-02115 | PSV-6022 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 946 | kg/m3 |  | 1) | kg/h | Inadvertent opening of FV-6031 or FV-5367 | 71 | 71 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 121 | °C | 1) | cm²
S-02115 | PSV-6027 | S | API 520, ASME Section VIII Division I |  |  | 0.78 | 1.09 | 18.02 |  |  |  | 1 | 2560 | kg/h | Fire - wetted surface | 45 | 45 | 21 | 21 | 2011-07-05 | 0 | <21 |  | 270 | °C | 0.90145 | cm²
S-02115 | PSV-6053 | S | API 520, ASME Section VIII Division I |  |  | 0.75 | 1.08 | 18.02 |  | 35.1 | kg/m3 | 1 | 3800 | kg/h | Fire - wetted surface | 55 | 55 | 21 | 21 | 2011-07-05 | 0 | <21 |  | 283 | °C | 1.0984 | cm²
S-02115 | PSV-6056 | L | API 520, ASME Section VIII Division I | 0.46 | cP |  |  |  |  | 813 | kg/m3 |  | 1) | kg/h | Blocked outlet | 55 | 55 | 10 | 10 | 2011-07-05 | <1.5 | <7.2 |  | 50 | °C
S-02115 | PSV-6085 | L | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989 | kg/m3 |  | 705 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.08 | cm²
S-02115 | PSV-7010 | S | API 520, ASME Section VIII Division I |  |  | 0.87 | 1.16 | 18.02 |  | 24.62 | kg/m3 | 0.88 | 254500 | kg/h | Inadvertent opening of PV-7002 A & B or C | 52 | 52 | 16 | 16 | 2011-07-05 | 0 | <16 |  | 345 | °C | 92.091 | cm²
S-02115 | PSV-7011 | S | API 520, ASME Section VIII Division I |  |  | 0.87 | 1.16 | 18.02 |  | 24.62 | kg/m3 | 0.88 | 254500 | kg/h | Inadvertent opening of PV-7002 A & B or C | 52 | 54.6 | 16 | 10.5 | 2011-07-05 | 0 | <10.5 |  | 345 | °C | 92.071 | cm²
S-02115 | PSV-7012 | S | API 520, ASME Section VIII Division I |  |  | 0.87 | 1.16 | 18.02 |  | 23.98 | kg/m3 | 0.88 | 254500 | kg/h | Inadvertent opening of PV-7002 A & B or C | 52 | 52 | 16 | 16 | 2011-07-05 | 0 | <16 |  | 345 | °C | 92.091 | cm²
S-02115 | PSV-7013 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 947 | kg/m3 |  |  | kg/h | Hydraulic expansion | 170 | 170 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7014 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 947 | kg/m3 |  |  | kg/h | Hydraulic expansion | 170 | 170 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7015 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 947 | kg/m3 |  |  | kg/h | Hydraulic expansion | 170 | 170 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7016 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 947 | kg/m3 |  |  | kg/h | Hydraulic expansion | 170 | 170 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7017 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 947 | kg/m3 |  |  | kg/h | Hydraulic expansion | 170 | 170 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7023 | S | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.21 | 18.02 |  | 20.01 | kg/m3 | 0.83 | 267300 | kg/h | Inadvertent opening of PV-7025 A & B | 52 | 52 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 410 | °C | 108.04 | cm²
S-02115 | PSV-7024 | S | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.21 | 18.02 |  | 20.01 | kg/m3 | 0.83 | 267300 | kg/h | Inadvertent opening of PV-7025 A & B | 52 | 52 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 410 | °C | 108.04 | cm²
S-02115 | PSV-7032 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 945 | kg/m3 |  |  | kg/h | Hydraulic expansion | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7033 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 945 | kg/m3 |  |  | kg/h | Hydraulic expansion | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7036 | S | API 520, ASME Section VIII Division I |  |  | 0.8 | 1.1 | 18.02 |  | 25.58 | kg/m3 | 1 | 1) | kg/h | Inadvertent opening of PV-7031 A & B | 45 | 45 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 265 | °C | 0.71 | cm²
S-02115 | PSV-7037 | S | API 520, ASME Section VIII Division I |  |  | 0.8 | 1.1 | 18.02 |  | 25.58 | kg/m3 | 1 | 1) | kg/h | Inadvertent opening of PV-7031 A & B | 45 | 45 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 265 | °C | 0.71 | cm²
S-02115 | PSV-7052 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 945 | kg/m3 |  |  | kg/h | Hydraulic expansion | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7053 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 945 | kg/m3 |  |  | kg/h | Hydraulic expansion | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C
S-02115 | PSV-7057 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.93 | kg/m3 | 0.99 | 80063 | kg/h | Inadvertent opening of PV-7051 A & B | 9.5 | 9.5 | 16 | 16 | 2011-07-05 | 0 | <16 |  | 200 | °C | 131.25 | cm²
S-02115 | PSV-7058 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.93 | kg/m3 | 0.99 | 80063 | kg/h | Inadvertent opening of PV-7051 A & B | 9.5 | 9.9 | 16 | 10.5 | 2011-07-05 | 0 | <10.5 |  | 200 | °C | 132.14 | cm²
S-02115 | PSV-7059 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.93 | kg/m3 | 0.99 | 80063 | kg/h | Inadvertent opening of PV-7051 A & B | 9.5 | 9.9 | 16 | 10.5 | 2011-07-05 | 0 | <10.5 |  | 200 | °C | 132.14 | cm²
S-02115 | PSV-7060 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.93 | kg/m3 | 0.99 | 80063 | kg/h | Inadvertent opening of PV-7051 A & B | 9.5 | 9.9 | 16 | 10.5 | 2011-07-05 | 0 | <10.5 |  | 200 | °C | 132.14 | cm²
S-02115 | PSV-7061 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.93 | kg/m3 | 0.99 | 80063 | kg/h | Inadvertent opening of PV-7051 A & B | 9.5 | 9.5 | 16 | 16 | 2011-07-05 | 0 | <16 |  | 200 | °C | 131.25 | cm²
S-02115 | PSV-7072 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 945.7 | kg/m3 |  |  |  | Hydraulic expansion | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  |  | °C
S-02115 | PSV-7073 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 945.7 | kg/m3 |  |  |  | Hydraulic expansion | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  |  | °C
S-02115 | PSV-7095 | S | API 520, ASME Section VIII Division I |  | cP | 0.96 | 1.23 | 18.02 |  | 2.67 | kg/m3 | 1 | 32000 | kg/h | Loss of DMW cooling | 3.5 | 3.5 | 16 | 16 | 2011-07-05 | 0 | <16 |  | 152 | °C | 123.19 | cm²
S-02115 | PSV-7096 | S | API 520, ASME Section VIII Division I |  | cP | 0.96 | 1.23 | 18.02 |  | 2.67 | kg/m3 | 1 | 32000 | kg/h | Loss of DMW cooling | 3.5 | 3.67 | 16 | 10.5 | 2011-07-05 | 0 | <10.5 |  | 152 | °C | 123.3 | cm²
S-02115 | PSV-7097 | S | API 520, ASME Section VIII Division I |  | cP | 0.96 | 1.23 | 18.02 |  | 2.67 | kg/m3 | 1 | 32000 | kg/h | Loss of DMW cooling | 3.5 | 3.5 | 16 | 16 | 2011-07-05 | 0 | <16 |  | 152 | °C | 123.19 | cm²
S-02115 | PSV-7104 | L | API 520, ASME Section VIII Division I | 0.43 | cP |  |  |  |  | 980 | kg/m3 |  | 1) | kg/h | Blocked outlet | 71 | 71 | 10 | 10 |  |  |  |  | 65 | °C
S-02115 | PSV-7107 | L | API 520, ASME Section VIII Division I | 0.43 | cP |  |  |  |  | 980 | kg/m3 |  | 1) | kg/h | Blocked outlet | 71 | 71 | 10 | 10 |  |  |  |  | 65 | °C
S-02115 | PSV-7130 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 943 | kg/m3 |  | 1) | kg/h | Blocked outlet, reverse flow through pump | 4.5 | 4.5 | 10 | 10 | <20 | 1 |  |  | 120 | °C | 1) | cm²
S-02115 | PSV-7131 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 943 | kg/m3 |  | 1) | kg/h | Blocked outlet, reverse flow through pump | 4.5 | 4.5 | 10 | 10 | <20 | 1 |  |  | 120 | °C | 1) | cm²
S-02115 | PSV-7132 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.77 | kg/m3 |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 191 | °C | 1) | cm²
S-02115 | PSV-7134 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.77 | kg/m3 |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 191 | °C | 1) | cm²
S-02115 | PSV-7135 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 943 | kg/m3 |  | 1) | kg/h | Blocked outlet, reverse flow through pump | 4.5 | 4.5 | 10 | 10 | <20 | 1 |  |  | 120 | °C | 1) | cm²
S-02115 | PSV-7136 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.77 | kg/m3 |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 191 | °C | 1) | cm²
S-02115 | PSV-7137 | S | API 520, ASME Section VIII Division I |  |  | 0.93 | 1.2 | 18.02 |  | 5.77 | kg/m3 |  | 1) | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 191 | °C | 1) | cm²
S-02115 | PSV-7142 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 946 | kg/m3 |  | 255000 | kg/h | Inadvertent opening of FV-7141 Cv=52 | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C | 8.53 | cm²
S-02115 | PSV-7143 | L | API 520, ASME Section VIII Division I | 0.23 | cP |  |  |  |  | 946 | kg/m3 |  | 255000 | kg/h | Inadvertent opening of FV-7141 Cv=52 | 80 | 80 | 10 | 10 | <20 | 0 | <10 |  | 122 | °C | 8.53 | cm²
S-02115 | PSV-7165 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 114 | 114 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7168 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 114 | 114 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7171 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 47 | 47 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7174 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 47 | 47 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7195 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7198 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7215 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7218 | L | API 520, ASME Section VIII Division I | [7 empty] | kg/m3 |  | 1) | kg/h | Blocked outlet | 7 | 7 | 10 | 10 | [5 empty] | °C | 1) | cm²
S-02115 | PSV-7253 | S | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.19 | 18.02 |  | 5.86 | kg/m3 | 1 | 3700 | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 186 | °C | 6.3039 | cm²
S-02115 | PSV-7254 | S | API 520, ASME Section VIII Division I |  |  | 0.92 | 1.19 | 18.02 |  | 5.86 | kg/m3 | 1 | 3700 | kg/h | Blocked outlet | 9.5 | 9.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 186 | °C | 6.3039 | cm²
S-02115 | PSV-7256 | L | API 520, ASME Section VIII Division I | 0.57 | cP |  |  |  |  | 989.3 | kg/m3 |  | 190 | kg/h | Hydraulic expansion | 7.5 | 7.5 | 10 | 10 | 2011-07-05 | 0 | <10 |  | 48 | °C | 0.02 | cm²

## Component Properties
Job No. | Specified | Total | J-No. | Component | Property 1 | Property 2 | Property 3 | Property 4 | Property 5 | Property 6 | Property 7 | Property 8 | Property 9 | Property 10 | Property 11 | Property 12 | Property 13 | Property 14 | Property 15 | Property 16 | Property 17 | Property 18 | Property 19 | Property 20 | Property 21 | Property 22 | Property 23 | Property 24 | Property 25 | Property 26 | Property 27 | Property 28 | Property 29 | Property 30
S-02115 |  | 53 | 201 | Orifice Plate Assembly | Sizing Flow | Minimum Flow | Normal Flow | Maximum Flow | Special Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Sizing dP | Sizing Pipe ID, app. | Sizing d/D Ratio, app. | Material, Orifice Plate | Pressure Tappings | Nos. of Tappings | Flange: Size, Rating, Type | Material, Assemblies | Meter Run
S-02115 |  | 4 | 201.1 | ISA 1932 Flow Nozzle | Sizing Flow | Minimum Flow | Normal Flow | Maximum Flow | Special Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Sizing dP | Sizing Pipe ID | Sizing d/D Ratio | Material, Nozzle | Pressure Tappings | Nos. of Tappings | Flange: Size, Rating, Type
S-02115 |  | 1 | 201.2 | Venturi | Sizing Flow | Normal Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight |  | Sizing Pipe ID | Sizing d/D Ratio | Material | Pressure Tappings | Nos. of Tappings | Flange: Size, Rating, Type | Minimum Flow | Maximum Flow | Special Flow
S-02115 |  | 26 | 202 | Thermocouple | IEC Type | Immersion Length | Duplex with
S-02115 |  | 34 | 203 | Thermocouple Assembly | IEC Type | HTAS Spec. No.
S-02115 |  | 167 | 204 | Resistance Temperature Sensor | Type IEC 60751, Class A
S-02115 |  | 1 | 206 | Pitot Tube | Sizing Flow | Normal Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Sizing dP | Sizing Pipe ID | Material | Flange: Size, Rating, Type | Minimum Flow | Maximum Flow | Special Flow
S-02115 |  | 13 | 209 | Gas Analyzer | Range | Measured Component(s) | Measuring Principle | Accuracy | Process Connection | Number of Streams | Gas Composition: | Case/Stream No. | Ar | C2H6 | C3H8 | C4H10 | C5H12 | CH4 | CO | CO2 | H2 | N2 | NH3 | O2 | H2O | Ar | CH3OH | CH3OCH3 | HCOOCH3 | Local sample system common for | .............................. |  | Moleweight
S-02115 |  | 3 | 210 | pH Transmitter | Range | Temperature Compensation | Signal
S-02115 |  | 3 | 211 | Conductivity Transmitter | Range | Compensation | Signal | Local sample system common for
S-02115 |  | 4 | 212.1 | Flow Transmitter, Mass Coriolis | Sizing Flow | Minimum Flow | Normal Flow | Maximum Flow | Special Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Meter size | Material | Flange: Size, Rating, Type | Signal | Max. Allowable Pressure Drop
S-02115 |  | 2 | 212.5 | Flow Transmitter, Vortex | Sizing Flow | Minimum Flow | Normal Flow | Maximum Flow | Special Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Meter size | Material | Flange: Size, Rating, Type | Double Vortex Meter | Signal
S-02115 |  | 71 | 213 | Flow Transmitter, d/P | Range | Option | Accessories | Process Connection
S-02115 |  | 58 | 214 | Level Transmitter, d/P | Range | Option | C-C Distance | Accessories | Upper Density | Lower Density | Nozzles: Size, Rating, Type | Remote Diaphragm Seals
S-02115 |  | 12 | 214.2 | Level Transmitter, Radar Type | Range | Nozzles: Size, Rating, Type | Mounting | Accessories
S-02115 |  | 122 | 215 | Pressure Transmitter | Range | Process Connection | Option | Accessories
S-02115 |  | 23 | 216 | Diff. Press. Transmitter | Range | Process Connection | Option | Location LP side | Accessories | Remote Diaphragm Seals
S-02115 |  | 227 | 218 | Temperature Transmitter | Range | Input IEC Type | Mounting | Accessories | Output
S-02115 |  | 496 | 227.01 | Analog Input | Signal | Square Root Extraction | P&T Compensation | MW Compensation | Signal to
S-02115 |  | 176 | 227.02 | Digital Input | Group No. | Signal
S-02115 |  | 150 | 227.03 | Analog Output | Signal | Signal to
S-02115 |  | 81 | 227.04 | Digital Output | Group No. | Signal
S-02115 |  | 378 | 227.1 | Analog Indicator | Range | Signal to | Signal Conditioning
S-02115 |  | 83 | 227.11 | Communication Link | Input from
S-02115 |  | 130 | 227.2 | Controller | Range | Signal Conditioning | Signal to | Remote Set Point to | Remote Set Point from | PV from | Interlock
S-02115 |  | 434 | 227.3 | Alarm | Type | Alarm Signal to
S-02115 |  | 14 | 227.35 | Interlock Circuit | Group No. | Two out of Three Voting
S-02115 |  | 209 | 227.4 | Digital Indicator | Type
S-02115 |  | 14 | 227.55 | Totalizer | Type | Input from | Output to
S-02115 |  | 86 | 227.6 | Calculation | Calculation Type | Input from |  |  |  | Output to | Equation | Normalized equation | .. | Tuneable constants | .. | Output to | .. | Equation | ..
S-02115 |  | 34 | 227.7 | Manual Loader | Range | Signal Conditioning | Signal to | Remote Set Point to
S-02115 |  | 63 | 227.71 | Hand Switch | Type | Interlock
S-02115 |  | 31 | 227.76 | Auto/manual station | Range | Interlock
S-02115 |  | 10 | 227.85 | Selector switch | Input from | Output to | Connected to
S-02115 |  | 179 | 243 | Control Valve | See Tag No. | Valve to be specified | Damper to be specified
S-02115 |  | 179 | 243.1 | Valve Body/Bonnet | Type | Size | Rating | Connection Type | Body Material | Pipe Inlet/Outlet
S-02115 |  | 3 | 243.11 | Spray Nozzle | Type | GAS/STEAM LINE | Pipe Size/Material | Pressure Operating/Design | Temperature In Operat./Design | Temperature Out Oper./Design | Operating Density | LIQUID LINE | Pipe Size/Material | Pressure Operating/Design | Temperature Operating/Design | Flow Operating/Max. | Flow Control
S-02115 |  | 179 | 243.2 | Trim | Cv Required | Type | Characteristic | Material | Leakage Class
S-02115 |  | 179 | 243.3 | Actuator | Type | Modulating or ON/OFF | Failure Position | dP for Sizing | Hand Wheel | Stroking Time
S-02115 |  | 121 | 243.4 | Positioner | Type | Option
S-02115 |  | 75 | 243.6 | Solenoid Valve | Type | Tag No. | Accessories
S-02115 |  | 103 | 243.7 | Limit Switch | Open Tag No. | Closed Tag No.
S-02115 |  | 4 | 243.8 | Position transmitter | Signal | Tag No.
S-02115 |  | 44 | 243.99 | Remark:
S-02115 |  | 6 | 248.01 | Speed Controller | Range
S-02115 |  | 7 | 256 | Rotameter, SS tube | Range | Sizing Flow | Minimum Flow | Normal Flow | Maximum Flow | Special Flow | Fluid Phase | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Material | Flange: Size, Rating, Type | Metering Valve
S-02115 |  | 47 | 259 | Level Gauge | Type | C-C Distance | Visible Length Approx. | Nozzles: Size, Rating, Type | Body Material | Accessories | Upper Density | Lower Density
S-02115 |  | 215 | 260 | Pressure Gauge | Range | Type | Process Connection | Siphon | Overrange Protection | Diaphragm Seal | Pulsation Dampener | Accessories
S-02115 |  | 1 | 261 | D/P Indicator | Range | Type | Process Connection | C-C Distance | Accessories
S-02115 |  | 53 | 262 | Thermometer, Bimetal | Range | Specified by
S-02115 |  | 7 | 263 | Receiver Indicator, Local | Scale | Signal
S-02115 |  | 3 | 276 | Manual Oper. Switch | Type | Specified by
S-02115 |  | 66 | 281 | Safety Interlock Circuit | Group No. | Description | Signal (I/O ?)
S-02115 |  | 135 | 281.01 | Analog Input | Signal | Square Root Extraction | P&T Compensation | Signal Conditioning
S-02115 |  | 94 | 281.02 | Digital Input | Signal | Signal Repeated to
S-02115 |  | 96 | 281.04 | Digital Output | ESD No. | Signal
S-02115 |  | 75 | 281.09 | Repeater Isolator | Repeat Signal to
S-02115 |  | 45 | 281.6 | Calculation | Calculation Type | Input from | .... | Output to | .. | Equation | ..
S-02115 |  | 1 | 281.7 | Manual Input | Range | Type
S-02115 |  | 258 | 284 | Thermowell | Immersion Length | Insertion Length | Well Material | Type | Fluid Velocity | Supplied by
S-02115 |  | 4 | 287 | Restriction Orifice | Sizing Flow | Fluid Phase | Type | Sizing Pressure | Sizing Temperature | Sizing Density | Sizing Viscosity | Sizing Compressibility | Sizing Cp/Cv Ratio | Sizing Moleweight | Sizing dP | Sizing Pipe ID | Sizing d/D Ratio | Material, Orifice Plate | Flange: Size, Rating, Type | Sizing by Pump Vendor
S-02115 |  | 136 | 288.1 | Body | Type | Code | Bonnet Type | Body & Bonnet Material | Inlet Size, Rating, Connection | Outlet Size, Rating,Connection
S-02115 |  | 136 | 288.2 | Internals | Selected Orifice | Nozzle/Seat Material | Hard facing on Nozzle/seat | Balanced Bellows
S-02115 |  | 111 | 288.99 | Remark:
S-02115 |  | 71 | 298 | Sample Point | AP type (ref. S2 diagram) | Sample Cooler | Instrument Supply