Material of Construction

Recommended Material for Piping and Heat Exchanger

| Utility | Material |
| --- | --- |
| Boiler Blow Down | A106 Gr.B/A672 Gr.B60 |
| Boiler Feed Water | A106 Gr.B/A672 Gr.B60 |
| Cooling Water | A106 Gr.B/A672 Gr.B60 |
| LPS/LPC | A106 Gr.B/A672 Gr.B60 |
| MPS/MPC | A106 Gr.B/A672 Gr.B60 |
| Nitrogen | A106 Gr.B/A672 Gr.B60 |
| Plant Air | A106 Gr.B/A672 Gr.B60 |
| Service Water | A106 Gr.B/A672 Gr.B60 |
| Fire Foam | A106 Gr.B/A672 Gr.B60 |
| Fire Water (AG) | A106 Gr.B/A672 Gr.B60 |
| Demineralized Water | A312 TP304 |
| Instrument Air | A312 TP304 |
| Fire Water (after filter) | A53 Gr. B/GALV |
| Potable Water (AG) | A53 Gr. B/GALV. |
| Potable Water (UG | A53 Gr. B/GALV. PE Coated Externally |

| Chemicals | Material |
| --- | --- |
| Oxygen Scavenger | A312 TP304L |
| NAOH Solution | A312 TP304L |
| Phosphate Solution | A312 TP304L |
| Crossion Inhibitor (AG) | A312 TP316L |
| H2SO4 | A312 TP316L |
| HCL Solution (2~40%) (AG) | CPVC |
| NaClO Solution (10%) (AG) | CPVC |
| Lube Oil | A312 TP304 |

| Process Fluids | Material |
| --- | --- |
| Fuel Gas | A106 Gr. B/A672 Gr.B60 |
| Natural Gas | A106 Gr.B/A672 Gr.B60 |
| Methanol Mixtures | A106 Gr.B/A672 Gr.B60 |
| Process Oxygen | B165 N04400 /A312 TP304L |
| Process Condensate | A312 TP304L |
| Ammonia Water | A312 TP304L |
| Turbine Condensate | A312 TP304 |
| Hydrogen Gas | A106 Gr.B/A672 Gr.B60/ A312 TP304 |
| Syngas (H2+CO+CO2) | A312 TP304 |
| Reformed Gas (H2+CO+CO2) | A312 TP321H/ A312 TP304L |

| Component of Channel Side | CS | SS |
| --- | --- | --- |
| Head | SA-516 70N | SA-240 304L |
| Shell | SA-516 70N | SA-240 304L |
| Channel Flange | SA-266 2N | SA-965 F304L/SA-182 F304 |
| Pass Partition | SA-516 70N |  |
| Nozzle | SA-105N | SA-182 F304L |
| Flange | SA-105N | SA-312 TP304L |
| Component of Heat Transfer |  |  |
| Tie Rod | SA-36 | SA-479 304 |
| Spacer | SA-179 | SA-213 TP304/SA-789/SA-312 |
| Baffle | SA-516 70N | SA-240 304 |
| Support Plate | SA-516 70N | SA-240 304L |
| Partition Plate | SA-516 70N | SA-240 304L |
| Impingement Plate | SA-516 70N | SA-240 304 |
| Tubesheet | SA-266 2N | SA-182 F304/SA-965 |
| Roller | SA-36 |  |
| Bonnet Flange Gasket | SS304+Flexible Gasket |  |
| Body Flange Gasket | SS304+Flexible Gasket |  |
| Hex Bolt | SA-193 B7 | SA-193 B7/A2-70 |
| Hex Nut | SA-194 Gr 2H | SA-194 Gr 2H/A2-70 |
| Body Flange | SA-266 2N | SA-965 F304/F304L |
| Shell Side Shell | SA-516 70N | SA-240 304/ SA-387 |
| Saddle Support | SA-516 70N/70 |  |
| Forged Nozzle | SA-105N |  |
| Flange | SA-105N |  |
| Tubes/U-Tubes | SA-179 | SA-213 TP304/SA-789 |
| Sealing Strip | SA-516 70N | SA-240 304L |
| Suitable Fluid | Natural Gas Cooling Water Methanol | Demineralized Water Reformed Gas Process Condensate |

Valves

Body material selection is usually based on the pressure, temperature, corrosive properties, and

erosive properties of the flow media. Sometimes a compromise must be reached in selecting a

material. For instance, a material with good erosion resistance may not be satisfactory because

of poor corrosion resistance when handling a particular fluid. Some service conditions require

use of exotic alloys and metals to withstand particular corrosive properties of the flowing fluid.

These materials are much more expensive than common metals, so economy may also be a

factor in material selection. Fortunately, the majority of control valve applications handle

relatively non-corrosive fluids at reasonable pressures and temperatures.

Therefore, cast carbon steel is the most commonly used valve body material and can provide

satisfactory service at much lower cost than the exotic alloy materials. Specifications have been

developed for ordering highly corrosion-resistant, high-alloy castings. These specifications

represent solutions to problems encountered with some of those alloys. These problems

included unacceptable corrosion resistance compared to the wrought materials, weldability

issues, and unacceptable lead times. These alloys are also difficult to cast.

The specifications include a foundry qualification process, dedicated pattern equipment, pattern

alloy qualification, heat qualification, and detailed controls on raw material, visual inspection,

weld repairs, heat treatment, and nondestructive testing. Designations for these exotic and

common grades are included in Table 5.36 Designations for Common Valve Body Materials.

The following descriptions and tables provide basic information on various popular casting

grades used for control valve bodies. ASTM material designations are included. Use of proper

ASTM designations is considered good practice and is encouraged in specifying materials,

particularly for pressure containing parts. Additional engineering

data on these and other materials is included in Chapter 13.

Cast Carbon Steel (ASTM A216 Grade WCC)—WCC is the most popular cast steel material

used for valve bodies in moderate services such as air, saturated or superheated steam, non-

corrosive liquids and gases. WCC is not used above 425°C(800°F) as the carbon rich phase

might be converted to graphite. It is generally welded without post weld heat treatment unless

nominal thickness exceeds 1-1/4inches (32 mm). Major weld repairs always receive post weld

heat treatment.

Cast Chromium-Molybdenum Steel(ASTM A217 Grade WC9)—This is the standard cast Cr-

Mo grade. WC9 has replaced C5 as the standard because of superior casting and welding

properties.WC9 has successfully replaced C5 inmost applications, especially in steam and

boiler feedwater service. The chromium and molybdenum provide erosion-corrosion and creep

resistance, making it useful to 595°C (1100°F). WC9is generally heat treated after welding.

Major weld repairs always receive post weld heat treatment.

Cast Type 304L Stainless Steel (ASTMA351 Grade CF3)— This is a common material

offering for chemical service valves. Cast304L is often preferred for nitric acid and certain other

chemical service applications. Optimum corrosion resistance is retained even in the as-welded

condition when proper welding procedures are used. CF3 is not rated for pressure boundary

parts above 425°C (800°F).

Cast Type 316 Stainless Steel (ASTM A351 Grade CF8M)—This is the industry standard

stainless steel cast body material. The addition of molybdenum gives Type 316 greater

resistance to corrosion, pitting, creep, and oxidizing fluids compared to 304 or 304L. It has the

widest temperature range of any standard material: -254°C (-425°F ) to 816°C(1500°F). The

castings are heat treated to provide maximum corrosion resistance. At temperatures above

538°C (1000°F) the carbon content shall be 0.04% minimum.

Cast Type 317 Stainless Steel (ASTMA351 Grade CG8M)—S31700 is essentially S31600

with the nickel and molybdenum contents increased 1%each. This affords greater resistance to

pitting than is obtained with S31600.Like S31600, S31700 is completely austenitic and non-

magnetic. Because its strength is similar to that of S31600, it has the same pressure-

temperature ratings. CG8M is the casting version of S31700. It contains considerable amounts

of ferrite (15 to 35%), and is, therefore, partially to strongly magnetic. In general, Type S31700

has better corrosion resistance than S31600 in certain environments because of its higher

molybdenum content. It has good corrosion resistance in many applications such as digester

liquor, dry chlorine dioxide and many other pulp and paper environments. For CG8M, the

maximum temperature for pressure retaining

parts is 538°C (1000°F).

Designations for Common Valve Body Materials

| Fluid | Material |
| --- | --- |
| NG | SA216 WCB |
| Purge Gas | SA216 WCB |
| Syngas | SA216 WCB/A351 CF8 |
| Process Condensate | A351 CF8 |
| LPS | SA216 WCB |
| MPS | SA216 WCB |
| HPS | SA216 WCB /SA217 WC6 |
| HHPS | SA217 WC6 |
| LPC | SA217 WC6/WC9 |
| MPC | SA216 WCB |
| HPC | SA217 WC9 |
| BFW | SA216 WCB/ SA217 WC6 |
| WMW | A351 CF8 |
| Nitrogen | SA216 WCB |
| Crude Methanol | SA216 WCB |
| Flashed Methanol | A351 CF8 |
| Refined Methanol | SA216 WCB |
| Process Gas | SA216 WCB/ A351 CF8 |
| Oxygen | Monel |

Refractories:

Standard bricks for furnace hot face

Standard firebricks for radiant floor (top layer only)

Standard bricks for sidewalls and floors

Ceramic fibre lining for furnace side and end walls, arch and flue gas

duct

Peephole blocks

Block Insulation

Air setting mortar for bricks

Loose fibre

Castable for upper part of convection sections and nosing

10. Castable for lower part of convection sections

11. Castable for cold collector